## RO D01-Report
date | Feed psi | Conc Press Stage 1 | Feed Press Stage 2 | Stage 2-3 Press | Conc psi | Perm Press Stage 1 | Perm psi | Perm Flow | Stage 2 Flow | Stage 3 Flow | Conc flow | Perm EC | Perm EC Stage 1 | Perm EC Stage 2 | Perm EC Stage 3 | Conc EC | KVA | IBP amps | IBP KVA | Temp (C.) | TCF Water | Calc Perm EC | Feed Flow | Stage 1 Flow | Stage 1-2 Feed Flow | Stage 2-3 Feed Flow | 1st Pass dp | 2nd Pass dp | 3rd Pass dp | Stage 1 Flux | Stage 2 Flux | Stage 3 Flux | Stage 1-2 EC | Stage 2-3 EC | Calc Conc EC | Stage 1 AFBC | Stage 2 AFBC | Stage 3 AFBC | Stage 1 SF | Stage 2 SF | Stage 3 SF | Stage 1 NdeltaP | Stage 2 NdeltaP | Stage 3 NdeltaP | Stage 1 NPC | Stage 2 NPC | Stage 3 NPC | Stage 1 Net Driving Press | Stage 2 Net Driving Press | Stage 3 Net Driving Press | Stage 1 Percent Removal | Stage 2 Percent Removal | Stage 3 Percent Removal | Stage 1 Norm Removal | Stage 2 Norm Removal | Stage 3 Norm Removal | Stage 1 Norm Pressure | Stage 2 Norm Pressure | Stage 3 Norm Pressure | Calc Conc Corr factor | Calc 2-3 Cond | Calc Conc Cond | Stage 1 Bucket Flow | Stage 2 Bucket Flow | Stage 3 Bucket Flow | Stage 1 Flow EST | Stage 2 Flow EST | Stage 3 Flow EST | Total | Membrane psi | stage 1 bucket EC | stage 2 bucket EC | stage 3 bucket EC | combined bucket EC | Unit Feed to Permeate Removal | Area Weighted Specific Flux | Flow Weighted Specific Flux | Unit DP | Unit NDeltaP | Net Drv Psi | NPC | Unit Feed to Permeate Removal | Unit AFBC | Unit AFBC Removal | Unit Norm % Removal | Unit Recovery | ERD Boost Pressure | IBP Tot. KVA | Unit AFBC Norm Percent Removal | TCF Salt | Flow Weighted Average Feed Pressure
2022-06-15 | 170.9483 | 152.9046 | 152.9046 | 141.7205 | 129.77 | 14.0871 | 14.0871 | 3470.1054 | 1055.2367 | 304.3952 | 612.2675 | 28.5687 | 17.3896 | 39.7478 | 111.7906 | 10020.1463 | 350.9301 |  |  | 27.9368 | 0.90583 | 32.4694 | 4082.3729 | 2110.4735 | 1971.8995 | 916.6628 | 18.0437 | 11.1841 | 12.2078 | 13.9152 | 11.3061 | 6.5228 | 3490.0174 | 7461.872 | 11116.0417 | 2379.9447 | 4982.3962 | 9047.4868 | 0.092665 | 0.094381 | 0.076754 | 17.6683 | 10.3608 | 11.5441 | 15.8416 | 39.0653 | 133.7946 | 136.0266 | 108.5122 | 76.9797 | 99.27% | 99.2% | 98.76% | 99.33% | 99.22% | 98.52% | 129.4991 | 127.1447 | 156.3427 |  |  |  | 32 | 26 | 15 | 2496 | 1248 | 360 | 4104 | 115.6603 | 14 | 32 | 90 | 23 | 98.31% | 0.090668 | 0.091791 | 41.4356 | 39.5731 | 123.8058 | 26.3105 | 98.31% | 3756.2056 | 99.24% | 99.17% | 85% |  |  | 99.31% | 0.90583
2022-06-14 | 169.8967 | 151.8266 | 151.8266 | 140.6023 | 128.3962 | 14.0576 | 14.0576 | 3471.3118 | 1055.6036 | 304.501 | 612.651 | 27.5064 | 16.743 | 38.2698 | 107.6338 | 9629.6619 | 348.8627 |  |  | 27.7665 | 0.911 | 31.2621 | 4083.9628 | 2111.2072 | 1972.7556 | 917.152 | 18.0702 | 11.2242 | 12.229 | 13.92 | 11.31 | 6.525 | 3375.6007 | 7216.7289 | 10750.1058 | 2301.9466 | 4818.9036 | 8749.9695 | 0.093672 | 0.095178 | 0.076968 | 17.6835 | 10.3907 | 11.5543 | 15.8648 | 39.124 | 134.0054 | 135.378 | 108.2537 | 77.23 | 99.27% | 99.21% | 98.77% | 99.31% | 99.19% | 98.47% | 128.1068 | 126.0792 | 155.9081 |  |  |  | 32 | 26 | 15 | 2496 | 1248 | 360 | 4104 | 114.354 | 14 | 32 | 90 | 23 | 98.32% | 0.091481 | 0.092665 | 41.5234 | 39.6284 | 123.5073 | 26.3501 | 98.32% | 3632.9531 | 99.24% | 99.14% | 85% |  |  | 99.31% | 0.911
2022-06-13 | 168.5283 | 150.3354 | 150.3354 | 139.0468 | 126.5712 | 14.0222 | 14.0222 | 3471.9651 | 1055.8023 | 304.5583 | 612.3845 | 26.0249 | 15.8413 | 36.2086 | 101.8367 | 9131.7491 | 345.129 |  |  | 27.532 | 0.91816 | 29.5783 | 4084.3496 | 2111.6045 | 1972.7451 | 916.9428 | 18.1929 | 11.2886 | 12.3367 | 13.9227 | 11.3122 | 6.5263 | 3217.9322 | 6881.4877 | 10253.2245 | 2194.2564 | 4594.358 | 8344.453 | 0.095031 | 0.096279 | 0.077245 | 17.8019 | 10.4514 | 11.6614 | 15.8739 | 39.1388 | 134.0207 | 134.5176 | 107.8781 | 77.5737 | 99.28% | 99.21% | 98.78% | 99.28% | 99.15% | 98.39% | 126.2752 | 124.6376 | 155.3504 |  |  |  | 32 | 26 | 15 | 2496 | 1248 | 360 | 4104 | 112.6496 | 14 | 32 | 90 | 23 | 98.33% | 0.092584 | 0.09385 | 41.8181 | 39.9148 | 123.1248 | 26.3605 | 98.33% | 3463.6028 | 99.25% | 99.09% | 85.01% |  |  | 99.31% | 0.91816
2022-06-12 | 168.6586 | 150.4859 | 150.4859 | 139.1838 | 126.959 | 14.0372 | 14.0372 | 3472.4757 | 1055.9575 | 304.6031 | 613.5503 | 26.019 | 15.8377 | 36.2003 | 101.8135 | 9311.1333 | 346.1973 |  |  | 27.6548 | 0.9144 | 29.5716 | 4086.0259 | 2111.915 | 1974.1109 | 918.1534 | 18.1727 | 11.3021 | 12.3003 | 13.9247 | 11.3138 | 6.5272 | 3274.446 | 6998.7146 | 10422.7499 | 2233.0263 | 4673.9858 | 8484.6486 | 0.094703 | 0.096139 | 0.077392 | 17.7687 | 10.45 | 11.6 | 15.5331 | 38.3113 | 131.2554 | 134.4491 | 107.6088 | 77.12 | 99.29% | 99.23% | 98.8% | 99.3% | 99.18% | 98.45% | 126.7116 | 124.8196 | 155.0545 |  |  |  | 32 | 26 | 15 | 2496 | 1248 | 360 | 4104 | 112.8909 | 14 | 32 | 90 | 23 | 98.36% | 0.092393 | 0.093621 | 41.7751 | 39.8187 | 122.8905 | 25.8027 | 98.36% | 3523.6943 | 99.26% | 99.13% | 84.98% |  |  | 99.32% | 0.9144
2022-06-11 | 169.358 | 151.5116 | 151.5116 | 140.3417 | 128.0638 | 14.3192 | 14.3192 | 3457.6358 | 1051.4448 | 303.3014 | 609.895 | 26.6533 | 16.2238 | 37.0829 | 104.2956 | 9644.6563 | 346.8428 |  |  | 27.6884 | 0.91338 | 30.2925 | 4067.5307 | 2102.8896 | 1964.6411 | 913.1964 | 17.8464 | 11.1699 | 12.1298 | 13.8652 | 11.2655 | 6.4993 | 3373.0162 | 7213.9752 | 10749.626 | 2299.8636 | 4816.0232 | 8748.007 | 0.094019 | 0.095528 | 0.077432 | 17.5712 | 10.4055 | 11.5363 | 15.3661 | 37.8825 | 129.7046 | 134.6974 | 107.7127 | 76.6649 | 99.29% | 99.23% | 98.81% | 99.33% | 99.21% | 98.52% | 127.6336 | 125.6173 | 154.9749 |  |  |  | 32 | 26 | 15 | 2496 | 1248 | 360 | 4104 | 113.7377 | 14 | 32 | 90 | 23 | 98.37% | 0.091848 | 0.093023 | 41.1461 | 39.5131 | 122.8198 | 25.5149 | 98.37% | 3630.6382 | 99.27% | 99.16% | 85.01% |  |  | 99.33% | 0.91338
2022-06-10 | 170.3191 | 152.3904 | 152.3904 | 141.1794 | 128.958 | 14.4118 | 14.4118 | 3460.8275 | 1050.5688 | 304.3783 | 610.7791 | 26.7916 | 16.2594 | 37.0326 | 103.9389 | 9772.9853 | 349.1033 |  |  | 27.6032 | 0.91598 | 30.2767 | 4071.6066 | 2105.8804 | 1965.7262 | 915.1574 | 17.9288 | 11.2109 | 12.2391 | 13.8849 | 11.2561 | 6.5224 | 3416.6239 | 7296.2769 | 10880.5375 | 2328.9462 | 4875.0845 | 8850.9521 | 0.093946 | 0.095305 | 0.077668 | 17.6297 | 10.4272 | 11.6078 | 15.2726 | 37.4482 | 128.5768 | 135.3795 | 108.1828 | 76.9218 | 99.3% | 99.24% | 98.83% | 99.34% | 99.23% | 98.55% | 127.7333 | 125.9115 | 154.5032 |  |  |  | 32.0208 | 25.9583 | 15.0417 | 2497.625 | 1246 | 361 | 4104.625 | 114.5648 | 13.9583 | 31.7917 | 89.2292 | 23 | 98.38% | 0.091776 | 0.092927 | 41.3788 | 39.6646 | 123.3612 | 25.4303 | 98.38% | 3675.4596 | 99.27% | 99.18% | 85% |  |  | 99.33% | 0.91598
2022-06-09 | 170.4778 | 152.4023 | 152.4023 | 141.2006 | 129.0542 | 14.1407 | 14.1407 | 3471.5206 | 967.3903 | 342.6174 | 612.2464 | 26.9532 | 14.0625 | 25.7813 | 62.1095 | 9913.9973 | 350.1796 |  |  | 27.6248 | 0.91532 | 22.0701 | 4083.767 | 2161.5128 | 1922.2542 | 954.8638 | 18.0755 | 11.2017 | 12.2378 | 14.2517 | 10.3649 | 7.3418 | 3545.9511 | 7112.3006 | 11057.6373 | 2382.1402 | 4921.9846 | 8796.663 | 0.096301 | 0.087698 | 0.086919 | 17.9131 | 10.4391 | 11.1522 | 13.2457 | 23.7605 | 86.9553 | 135.459 | 108.1797 | 77.314 | 99.41% | 99.48% | 99.29% | 99.44% | 99.52% | 99.01% | 124.6091 | 136.8329 | 138.059 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 114.8393 | 12 | 22 | 53 | 23 | 98.39% | 0.092047 | 0.092978 | 41.515 | 39.5043 | 123.5029 | 25.3168 | 98.39% | 3722.9787 | 99.28% | 99.4% | 85.01% |  |  | 99.34% | 0.91532
2022-06-08 | 171.121 | 153.1618 | 153.1618 | 142.1257 | 129.4865 | 13.3223 | 13.3223 | 3457.8718 | 963.5869 | 341.2704 | 610.9777 | 29.4327 | 15.3562 | 28.153 | 67.8232 | 10221.2864 | 347.4122 |  |  | 27.4513 | 0.92064 | 24.1004 | 4068.8495 | 2153.0145 | 1915.835 | 952.2481 | 17.9591 | 11.0361 | 12.2035 | 14.1957 | 10.3241 | 7.3129 | 3619.6969 | 7254.0069 | 11267.953 | 2432.5311 | 5022.4461 | 8968.2422 | 0.095582 | 0.086921 | 0.086336 | 17.8931 | 10.3333 | 11.1624 | 14.1909 | 25.4747 | 93.3115 | 136.7332 | 109.35 | 77.9817 | 99.37% | 99.44% | 99.24% | 99.42% | 99.49% | 98.96% | 125.5473 | 138.0558 | 138.9924 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 116.3495 | 12 | 22 | 53 | 23 | 98.28% | 0.091331 | 0.092256 | 41.1987 | 39.3888 | 124.575 | 27.141 | 98.28% | 3799.2829 | 99.23% | 99.37% | 84.98% |  |  | 99.29% | 0.92064
2022-06-07 | 170.8366 | 152.6994 | 152.6994 | 141.409 | 128.9511 | 14.0374 | 14.0374 | 3473.2217 | 967.8644 | 342.7853 | 613.0208 | 26.0639 | 13.5986 | 24.9307 | 60.0603 | 9531.4855 | 351.3452 |  |  | 27.4708 | 0.92004 | 21.3419 | 4086.2425 | 2162.572 | 1923.6705 | 955.8061 | 18.1372 | 11.2904 | 12.4251 | 14.2587 | 10.37 | 7.3454 | 3428.031 | 6874.0642 | 10684.2779 | 2303.0916 | 4757.7787 | 8500.9122 | 0.09626 | 0.087248 | 0.085612 | 17.9568 | 10.5088 | 11.3043 | 13.3232 | 23.904 | 87.5038 | 136.2832 | 109.3526 | 78.9384 | 99.41% | 99.48% | 99.29% | 99.42% | 99.5% | 98.97% | 124.6624 | 137.5387 | 140.1673 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 114.9013 | 12 | 22 | 53 | 23 | 98.39% | 0.091673 | 0.092698 | 41.8527 | 39.7699 | 124.6295 | 25.4694 | 98.39% | 3598.8125 | 99.28% | 99.37% | 85% |  |  | 99.33% | 0.92004
2022-06-06 | 169.723 | 151.5124 | 151.5124 | 140.0161 | 127.5823 | 14.046 | 14.046 | 3471.7681 | 967.4593 | 342.6418 | 611.7898 | 25.0466 | 13.0678 | 23.9576 | 57.716 | 9048.98 | 350.4702 |  |  | 27.3296 | 0.9244 | 20.5089 | 4083.5579 | 2161.6669 | 1921.891 | 954.4316 | 18.2106 | 11.4963 | 12.6841 | 14.2527 | 10.3656 | 7.3423 | 3271.9328 | 6564.2418 | 10208.317 | 2197.9272 | 4542.1073 | 8119.8272 | 0.097129 | 0.087805 | 0.085436 | 18.0496 | 10.7181 | 11.5687 | 13.4736 | 24.1655 | 88.4147 | 135.6474 | 109.1275 | 79.4426 | 99.41% | 99.47% | 99.29% | 99.39% | 99.47% | 98.91% | 123.5476 | 136.6658 | 140.4564 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 113.4964 | 12 | 22 | 53 | 23 | 98.38% | 0.092274 | 0.093377 | 42.391 | 40.3364 | 124.3562 | 25.7484 | 98.38% | 3435.6221 | 99.27% | 99.34% | 85.02% |  |  | 99.33% | 0.9244
2022-06-05 | 171.2876 | 153.1726 | 153.1726 | 141.7532 | 129.1706 | 14.142 | 14.142 | 3470.4803 | 967.1005 | 342.5147 | 614.3621 | 25.3937 | 13.2489 | 24.2896 | 58.5159 | 9406.4565 | 355.3091 |  |  | 27.2592 | 0.92658 | 20.7931 | 4084.8424 | 2160.8651 | 1923.9773 | 956.8768 | 18.115 | 11.4193 | 12.5049 | 14.2475 | 10.3618 | 7.3396 | 3390.6474 | 6792.9727 | 10547.5188 | 2278.5281 | 4704.0165 | 8396.6757 | 0.096529 | 0.087344 | 0.085405 | 17.9398 | 10.6212 | 11.3506 | 13.2034 | 23.7043 | 86.8572 | 136.7617 | 109.9222 | 79.6291 | 99.42% | 99.48% | 99.3% | 99.42% | 99.5% | 98.97% | 124.3149 | 137.3875 | 140.5063 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 115.0061 | 12 | 22 | 53 | 23 | 98.42% | 0.09181 | 0.092872 | 42.0392 | 39.9116 | 125.1757 | 25.2558 | 98.42% | 3558.2492 | 99.29% | 99.37% | 84.96% |  |  | 99.34% | 0.92658
2022-06-04 | 172.9681 | 154.7775 | 154.7775 | 143.4292 | 131.1282 | 14.3099 | 14.3099 | 3472.3548 | 967.6228 | 342.6997 | 612.965 | 26.211 | 13.6753 | 25.0714 | 60.3992 | 9902.0479 | 358.5392 |  |  | 27.1485 | 0.93003 | 21.4623 | 4085.3198 | 2162.0322 | 1923.2876 | 955.6648 | 18.1906 | 11.3483 | 12.4044 | 14.2552 | 10.3674 | 7.3436 | 3546.0547 | 7111.0954 | 11053.0362 | 2382.2548 | 4921.6958 | 8794.167 | 0.096266 | 0.087408 | 0.086125 | 18.0155 | 10.5656 | 11.2876 | 13.0904 | 23.4846 | 85.9648 | 137.72 | 110.3103 | 79.2999 | 99.43% | 99.49% | 99.31% | 99.45% | 99.52% | 99.02% | 124.6552 | 137.2879 | 139.3321 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 116.8199 | 12 | 22 | 53 | 23 | 98.44% | 0.091809 | 0.092796 | 41.9433 | 39.8687 | 125.7217 | 25.023 | 98.44% | 3722.7232 | 99.3% | 99.41% | 85% |  |  | 99.35% | 0.93003
2022-06-03 | 172.9399 | 154.8954 | 154.8954 | 143.5455 | 131.0515 | 14.3571 | 14.3571 | 3468.0002 | 966.4093 | 342.27 | 613.6447 | 26.3553 | 13.7506 | 25.2094 | 60.7317 | 9904.5329 | 359.8593 |  |  | 27.0519 | 0.93304 | 21.5805 | 4081.6449 | 2159.3209 | 1922.3241 | 955.9147 | 18.0445 | 11.35 | 12.382 | 14.2373 | 10.3544 | 7.3344 | 3562.427 | 7138.4784 | 11086.2026 | 2393.7909 | 4942.7502 | 8824.566 | 0.096498 | 0.087609 | 0.08649 | 17.8916 | 10.571 | 11.2571 | 13.1251 | 23.56 | 86.3113 | 137.6603 | 110.2756 | 79.1222 | 99.43% | 99.49% | 99.31% | 99.45% | 99.52% | 99.02% | 124.3543 | 136.9727 | 138.7443 |  |  |  | 33 | 24 | 17 | 2574 | 1152 | 408 | 4134 | 116.7235 | 12 | 22 | 53 | 23 | 98.44% | 0.092052 | 0.093033 | 41.7765 | 39.7198 | 125.5913 | 25.1025 | 98.44% | 3738.7733 | 99.3% | 99.41% | 84.97% |  |  | 99.34% | 0.93304
2022-06-02 | 172.554 | 154.5663 | 154.5663 | 143.2937 | 130.7752 | 14.2968 | 14.2968 | 3463.6196 | 1001.714 | 337.1107 | 612.4209 | 26.7464 | 12.8671 | 25.7575 | 62.9162 | 9908.7867 | 359.2834 |  |  | 27.0796 | 0.93218 | 21.4664 | 4076.0406 | 2124.795 | 1951.2455 | 949.5316 | 17.9877 | 11.2726 | 12.3827 | 14.0096 | 10.7326 | 7.2238 | 3498.8891 | 7162.8899 | 11071.1118 | 2372.2706 | 4900.7178 | 8835.1579 | 0.095001 | 0.090739 | 0.085372 | 17.7319 | 10.3768 | 11.3402 | 12.1837 | 25.1422 | 87.8808 | 137.4663 | 110.2584 | 78.8765 | 99.46% | 99.47% | 99.29% | 99.49% | 99.49% | 99.01% | 126.3143 | 132.2476 | 140.561 |  |  |  | 31.9882 | 24.5059 | 16.4941 | 2495.0824 | 1176.2824 | 395.8588 | 4067.2235 | 116.527 | 13.0118 | 26.0471 | 63.6235 | 27.0471 | 98.41% | 0.092097 | 0.092831 | 41.643 | 39.4489 | 125.3396 | 25.4616 | 98.41% | 3732.5496 | 99.28% | 99.41% | 84.98% |  |  | 99.33% | 0.93218
2022-06-01 | 172.528 | 154.4148 | 154.4148 | 143.032 | 130.479 | 14.1062 | 14.1062 | 3469.9343 | 1040.4601 | 332.9472 | 613.3087 | 26.5216 | 11.9775 | 25.666 | 63.3096 | 9645.5401 | 360.112 |  |  | 27.0938 | 0.93173 | 21.0074 | 4083.243 | 2096.527 | 1986.7159 | 946.2559 | 18.1132 | 11.3828 | 12.3908 | 13.8233 | 11.1478 | 7.1346 | 3380.5153 | 7069.3555 | 10872.7316 | 2312.6168 | 4779.4388 | 8699.8331 | 0.093424 | 0.093702 | 0.083652 | 17.6677 | 10.3062 | 11.3736 | 11.4737 | 26.6696 | 88.6543 | 137.862 | 110.8483 | 79.4667 | 99.48% | 99.46% | 99.27% | 99.5% | 99.44% | 98.98% | 128.447 | 128.0649 | 143.4519 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 116.4426 | 14 | 30 | 74 | 31 | 98.39% | 0.091949 | 0.09257 | 41.8868 | 39.3475 | 125.8519 | 25.7464 | 98.39% | 3665.1599 | 99.28% | 99.4% | 84.98% |  |  | 99.33% | 0.93173
2022-05-31 | 170.2147 | 152.0378 | 152.0378 | 140.3994 | 127.964 | 14.0823 | 14.0823 | 3465.0362 | 1038.9914 | 332.4772 | 611.517 | 25.948 | 11.7185 | 25.111 | 61.9404 | 8830.7157 | 353.398 |  |  | 26.8554 | 0.93922 | 20.5531 | 4076.5532 | 2093.5676 | 1982.9856 | 943.9942 | 18.1769 | 11.6384 | 12.5843 | 13.8037 | 11.1321 | 7.1245 | 3122.1677 | 6530.891 | 10048.0112 | 2135.8605 | 4414.7143 | 8038.4558 | 0.095033 | 0.094887 | 0.083417 | 17.7755 | 10.57 | 11.5965 | 12.2348 | 28.4353 | 94.494 | 136.4233 | 110.1883 | 80.2168 | 99.45% | 99.43% | 99.23% | 99.43% | 99.36% | 98.82% | 126.2719 | 126.4665 | 143.8552 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 113.8447 | 14 | 30 | 74 | 31 | 98.3% | 0.093128 | 0.093875 | 42.3996 | 39.942 | 125.1142 | 27.4503 | 98.3% | 3385.5409 | 99.23% | 99.31% | 85% |  |  | 99.28% | 0.93922
2022-05-30 | 171.5934 | 153.4438 | 153.4438 | 141.8402 | 129.1851 | 14.1479 | 14.1479 | 3471.6171 | 1040.9646 | 333.1087 | 614.3078 | 26.813 | 12.1091 | 25.9481 | 64.0053 | 9134.8672 | 356.2259 |  |  | 26.8262 | 0.94014 | 21.2383 | 4085.9249 | 2097.5437 | 1988.3812 | 947.4165 | 18.1496 | 11.6036 | 12.7548 | 13.83 | 11.1532 | 7.138 | 3216.0826 | 6721.2116 | 10331.0846 | 2200.6366 | 4545.6894 | 8269.0902 | 0.09461 | 0.094554 | 0.08353 | 17.6841 | 10.491 | 11.6835 | 12.3059 | 28.6188 | 95.1943 | 137.4281 | 110.8954 | 80.3394 | 99.45% | 99.43% | 99.23% | 99.44% | 99.37% | 98.85% | 126.8364 | 126.9123 | 143.6608 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 115.0243 | 14 | 30 | 74 | 31 | 98.29% | 0.092819 | 0.09353 | 42.5081 | 39.8586 | 125.7937 | 27.6267 | 98.29% | 3486.0812 | 99.23% | 99.32% | 84.97% |  |  | 99.28% | 0.94014
2022-05-29 | 173.3638 | 155.2228 | 155.2228 | 143.7097 | 131.2615 | 14.1464 | 14.1464 | 3472.1985 | 1027.3938 | 335.0482 | 612.495 | 27.9582 | 12.6263 | 27.0563 | 66.7389 | 9665.9019 | 360.1451 |  |  | 26.8802 | 0.93844 | 22.1176 | 4084.6936 | 2109.7565 | 1974.9371 | 947.5432 | 18.141 | 11.5131 | 12.5061 | 13.9105 | 11.0078 | 7.1796 | 3400.824 | 7058.9031 | 10883.7698 | 2318.6158 | 4792.3981 | 8697.0328 | 0.094174 | 0.092653 | 0.084023 | 17.74 | 10.4804 | 11.4742 | 12.2273 | 27.8853 | 94.7535 | 138.617 | 111.4932 | 80.1877 | 99.46% | 99.44% | 99.23% | 99.47% | 99.42% | 98.91% | 127.4237 | 129.5161 | 142.8181 |  |  |  | 31 | 24.5312 | 16 | 2418 | 1177.5 | 384 | 3979.5 | 117.095 | 14 | 30 | 74 | 31 | 98.31% | 0.092063 | 0.092744 | 42.1602 | 39.6946 | 126.568 | 27.3474 | 98.31% | 3666.0692 | 99.24% | 99.37% | 85.01% |  |  | 99.28% | 0.93844
2022-05-28 | 174.4787 | 156.4703 | 156.4703 | 145.1775 | 132.5078 | 14.3775 | 14.3775 | 3468.8197 | 1010.6425 | 336.8808 | 613.3855 | 28.1772 | 12.7252 | 27.2682 | 67.2617 | 9954.568 | 362.7299 |  |  | 26.7194 | 0.94352 | 22.2587 | 4082.2052 | 2121.2964 | 1960.9088 | 950.2663 | 18.0084 | 11.2928 | 12.4084 | 13.9866 | 10.8283 | 7.2189 | 3524.5566 | 7244.0489 | 11185.6518 | 2394.1374 | 4945.2855 | 8931.2281 | 0.09481 | 0.091338 | 0.084985 | 17.6826 | 10.3398 | 11.3451 | 12.0647 | 26.936 | 94.0067 | 139.1899 | 111.8563 | 80.1453 | 99.47% | 99.45% | 99.25% | 99.5% | 99.46% | 98.95% | 126.5688 | 131.3801 | 141.2012 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.1551 | 14 | 30 | 74 | 31 | 98.34% | 0.092127 | 0.092844 | 41.7096 | 39.3675 | 126.9267 | 26.9045 | 98.34% | 3772.2773 | 99.25% | 99.4% | 84.97% |  |  | 99.3% | 0.94352
2022-05-27 | 174.472 | 156.444 | 156.444 | 145.019 | 132.5752 | 14.4297 | 14.4297 | 3468.6237 | 1010.5854 | 336.8618 | 613.8218 | 28.6087 | 12.92 | 27.6858 | 68.2917 | 10084.6669 | 362.9071 |  |  | 26.8841 | 0.93831 | 22.5996 | 4082.4455 | 2121.1766 | 1961.2689 | 950.6836 | 18.028 | 11.425 | 12.2912 | 13.9858 | 10.8277 | 7.2185 | 3665.1796 | 7531.8689 | 11627.8363 | 2489.7033 | 5142.2309 | 9285.2521 | 0.094652 | 0.091753 | 0.086522 | 17.6992 | 10.4567 | 11.2288 | 11.7136 | 26.1544 | 91.2952 | 138.6444 | 110.7291 | 78.2826 | 99.48% | 99.46% | 99.26% | 99.53% | 99.49% | 99.02% | 126.7797 | 130.7855 | 138.6929 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.1796 | 14 | 30 | 74 | 31 | 98.38% | 0.092424 | 0.093018 | 41.7442 | 39.3846 | 125.9563 | 26.124 | 98.38% | 3922.4809 | 99.27% | 99.44% | 84.96% |  |  | 99.32% | 0.93831
2022-05-26 | 173.9133 | 155.9236 | 155.9236 | 144.5321 | 131.909 | 14.3744 | 14.3744 | 3470.7486 | 1011.2045 | 337.0682 | 613.4348 | 28.1055 | 12.6928 | 27.1989 | 67.0906 | 9888.3594 | 361.7337 |  |  | 26.9474 | 0.93632 | 22.2021 | 4084.1834 | 2122.476 | 1961.7074 | 950.503 | 17.9896 | 11.3915 | 12.5131 | 13.9943 | 10.8343 | 7.2229 | 3733.8567 | 7677.231 | 11858.8261 | 2535.8771 | 5239.857 | 9466.8899 | 0.095 | 0.092398 | 0.088005 | 17.652 | 10.4247 | 11.4377 | 11.2809 | 25.1775 | 87.8358 | 137.9281 | 109.7901 | 76.8471 | 99.5% | 99.48% | 99.29% | 99.56% | 99.52% | 99.07% | 126.3155 | 129.8727 | 136.3557 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 117.5492 | 14 | 30 | 74 | 31 | 98.44% | 0.093048 | 0.093563 | 41.8942 | 39.5143 | 124.9714 | 25.1492 | 98.44% | 3996.8012 | 99.3% | 99.47% | 84.98% |  |  | 99.34% | 0.93632
2022-05-25 | 174.5838 | 156.4524 | 156.4524 | 145.0627 | 132.5463 | 14.3579 | 14.3579 | 3470.5747 | 1011.1538 | 337.0513 | 613.0887 | 28.681 | 12.9527 | 27.7558 | 68.4644 | 9980.0723 | 362.4769 |  |  | 26.8554 | 0.93922 | 22.6567 | 4083.6634 | 2122.3697 | 1961.2937 | 950.1399 | 18.1313 | 11.3897 | 12.5463 | 13.9936 | 10.8338 | 7.2225 | 3761.3125 | 7734.6219 | 11949.164 | 2554.4735 | 5278.6689 | 9538.2842 | 0.094928 | 0.092381 | 0.087986 | 17.7951 | 10.4272 | 11.4759 | 11.4629 | 25.5818 | 89.2342 | 138.4526 | 110.1451 | 77.0975 | 99.49% | 99.47% | 99.28% | 99.55% | 99.52% | 99.06% | 126.4111 | 129.8972 | 136.3849 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.2022 | 14 | 30 | 74 | 31 | 98.42% | 0.093002 | 0.093512 | 42.0673 | 39.6982 | 125.4351 | 25.553 | 98.42% | 4026.4149 | 99.29% | 99.46% | 84.99% |  |  | 99.33% | 0.93922
2022-05-24 | 174.4177 | 156.3121 | 156.3121 | 144.8666 | 132.229 | 14.3461 | 14.3461 | 3470.5043 | 1011.1333 | 337.0444 | 613.095 | 28.1544 | 12.7149 | 27.2461 | 67.2072 | 9786.5387 | 360.7408 |  |  | 26.7182 | 0.94356 | 22.2407 | 4083.5993 | 2122.3266 | 1961.2727 | 950.1394 | 18.1055 | 11.4456 | 12.5529 | 13.9934 | 10.8336 | 7.2224 | 3703.4391 | 7615.6237 | 11765.3095 | 2515.1603 | 5197.4518 | 9391.5309 | 0.095328 | 0.092598 | 0.087841 | 17.7702 | 10.4784 | 11.4818 | 11.4809 | 25.6218 | 89.3737 | 138.5066 | 110.3922 | 77.5801 | 99.49% | 99.48% | 99.28% | 99.54% | 99.51% | 99.05% | 125.8812 | 129.5924 | 136.61 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 117.8635 | 14 | 30 | 74 | 31 | 98.42% | 0.093257 | 0.093806 | 42.104 | 39.7304 | 125.6455 | 25.5929 | 98.42% | 3964.4587 | 99.29% | 99.45% | 84.99% |  |  | 99.33% | 0.94356
2022-05-23 | 171.9621 | 153.822 | 153.822 | 142.2474 | 129.5411 | 14.1444 | 14.1444 | 3466.683 | 1010.0199 | 336.6733 | 611.7788 | 26.4446 | 11.9427 | 25.5915 | 63.1258 | 9152.4586 | 355.0514 |  |  | 26.5305 | 0.94953 | 20.89 | 4078.4618 | 2119.9898 | 1958.472 | 948.4521 | 18.1401 | 11.5746 | 12.5845 | 13.978 | 10.8216 | 7.2144 | 3490.7255 | 7180.7953 | 11097.7822 | 2370.456 | 4899.7049 | 8856.8717 | 0.096912 | 0.093823 | 0.088072 | 17.8392 | 10.6211 | 11.544 | 11.5017 | 25.6617 | 89.4788 | 136.9551 | 109.5197 | 77.7811 | 99.5% | 99.48% | 99.29% | 99.51% | 99.48% | 98.99% | 123.8241 | 127.8998 | 136.2521 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 115.4115 | 14 | 30 | 74 | 31 | 98.43% | 0.094509 | 0.095153 | 42.2992 | 40.0043 | 124.7126 | 25.6331 | 98.43% | 3737.2942 | 99.29% | 99.42% | 85% |  |  | 99.33% | 0.94953
2022-05-22 | 173.0163 | 154.891 | 154.891 | 143.3681 | 130.8129 | 14.391 | 14.391 | 3469.6252 | 1010.8771 | 336.959 | 612.5725 | 27.3251 | 12.3404 | 26.4437 | 65.2277 | 9548.0661 | 357.8791 |  |  | 26.7403 | 0.94286 | 21.5856 | 4082.1977 | 2121.789 | 1960.4087 | 949.5315 | 18.1254 | 11.5229 | 12.6001 | 13.9898 | 10.8308 | 7.2206 | 3617.8264 | 7441.2346 | 11498.5705 | 2456.851 | 5077.8014 | 9177.4653 | 0.096042 | 0.093275 | 0.088256 | 17.7997 | 10.5572 | 11.5375 | 11.3958 | 25.4278 | 88.6764 | 137.3401 | 109.4818 | 77.1383 | 99.5% | 99.48% | 99.29% | 99.54% | 99.5% | 99.03% | 124.9454 | 128.6515 | 135.9674 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 116.3838 | 14 | 30 | 74 | 31 | 98.43% | 0.093911 | 0.09448 | 42.2483 | 39.8944 | 124.7143 | 25.3994 | 98.43% | 3873.1511 | 99.29% | 99.44% | 84.99% |  |  | 99.34% | 0.94286
2022-05-21 | 174.9594 | 156.8512 | 156.8512 | 145.3258 | 132.7206 | 14.3682 | 14.3682 | 3470.8095 | 1011.2222 | 337.0741 | 614.1577 | 28.3183 | 12.7889 | 27.4048 | 67.5984 | 9992.335 | 362.9128 |  |  | 26.7228 | 0.94341 | 22.3702 | 4084.9673 | 2122.5133 | 1962.454 | 951.2318 | 18.1082 | 11.5254 | 12.5832 | 13.9946 | 10.8345 | 7.223 | 3771.2636 | 7751.2326 | 11968.3149 | 2561.5383 | 5291.4762 | 9556.3571 | 0.095125 | 0.092585 | 0.088255 | 17.7616 | 10.5391 | 11.4858 | 11.3379 | 25.3114 | 88.3377 | 138.7934 | 110.4 | 77.2112 | 99.5% | 99.48% | 99.29% | 99.56% | 99.52% | 99.08% | 126.1503 | 129.6101 | 135.9695 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.3723 | 14 | 30 | 74 | 31 | 98.44% | 0.093213 | 0.093718 | 42.2168 | 39.7866 | 125.7058 | 25.2826 | 98.44% | 4036.2219 | 99.3% | 99.47% | 84.97% |  |  | 99.34% | 0.94341
2022-05-20 | 173.9678 | 155.9629 | 155.9629 | 144.594 | 132.1057 | 14.1869 | 14.1869 | 3456.4201 | 1023.0817 | 331.8311 | 609.4537 | 27.55 | 12.1081 | 25.8268 | 64.0056 | 9980.8482 | 358.3694 |  |  | 26.5351 | 0.94939 | 21.1512 | 4065.8738 | 2101.5073 | 1964.3665 | 941.2848 | 18.005 | 11.3689 | 12.494 | 13.8561 | 10.9616 | 7.1107 | 3735.0971 | 7766.7002 | 11960.6095 | 2544.7427 | 5267.6172 | 9563.7149 | 0.095245 | 0.094708 | 0.088056 | 17.7359 | 10.4392 | 11.5664 | 10.766 | 24.3966 | 82.7994 | 138.1153 | 109.8826 | 76.6644 | 99.52% | 99.51% | 99.33% | 99.58% | 99.54% | 99.13% | 125.9906 | 126.7046 | 136.2763 |  |  |  | 30.8122 | 24.3756 | 15.8122 | 2403.3513 | 1170.0292 | 379.4927 | 3952.8732 | 117.8969 | 13.6244 | 29.061 | 72.0208 | 31 | 98.48% | 0.093923 | 0.094396 | 41.8679 | 39.7414 | 125.0586 | 24.7214 | 98.48% | 4024.5502 | 99.32% | 99.49% | 85.01% |  |  | 99.35% | 0.94939
2022-05-19 | 173.4268 | 155.3879 | 155.3879 | 143.9268 | 131.187 | 14.1444 | 14.1444 | 3469.3675 | 1096.6998 | 316.3557 | 612.6584 | 26.9991 | 10.4513 | 21.7735 | 55.7401 | 9728.6259 | 357.9193 |  |  | 26.7549 | 0.9424 | 18.16 | 4082.0259 | 2056.3121 | 2025.7138 | 929.0141 | 18.039 | 11.4611 | 12.4729 | 13.5581 | 11.7504 | 6.7791 | 3551.9272 | 7719.2685 | 11676.451 | 2455.7826 | 5107.0622 | 9426.459 | 0.092563 | 0.10059 | 0.083446 | 17.4322 | 10.2627 | 11.6489 | 9.353 | 22.5734 | 69.2315 | 138.0363 | 110.0865 | 76.5589 | 99.57% | 99.57% | 99.41% | 99.62% | 99.56% | 99.27% | 129.6409 | 119.2973 | 143.8052 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 117.0466 | 12 | 25 | 64 | 31 | 98.47% | 0.093673 | 0.094269 | 41.973 | 39.3438 | 125.1191 | 24.7226 | 98.47% | 3929.501 | 99.31% | 99.54% | 84.99% |  |  | 99.35% | 0.9424
2022-05-18 | 173.7661 | 155.7053 | 155.7053 | 144.1986 | 131.6912 | 14.1134 | 14.1134 | 3471.7383 | 1097.4492 | 316.5719 | 611.9505 | 27.6433 | 10.7006 | 22.293 | 57.0701 | 9898.769 | 359.603 |  |  | 26.7504 | 0.94254 | 18.5933 | 4083.6888 | 2057.7172 | 2025.9716 | 928.5224 | 18.0608 | 11.5067 | 12.5949 | 13.5674 | 11.7584 | 6.7837 | 3602.3187 | 7833.6614 | 11856.6177 | 2490.2758 | 5180.9235 | 9568.8311 | 0.092514 | 0.10071 | 0.083829 | 17.4451 | 10.3048 | 11.7765 | 9.4514 | 22.8015 | 69.8869 | 138.2244 | 110.0454 | 76.2727 | 99.57% | 99.57% | 99.4% | 99.62% | 99.56% | 99.27% | 129.7095 | 119.1535 | 143.1482 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 117.5691 | 12 | 25 | 64 | 31 | 98.46% | 0.093748 | 0.094313 | 42.1624 | 39.5264 | 125.099 | 24.9727 | 98.46% | 3986.2758 | 99.31% | 99.54% | 85.01% |  |  | 99.35% | 0.94254
2022-05-17 | 172.9561 | 154.8551 | 154.8551 | 143.2641 | 130.5789 | 14.1135 | 14.1135 | 3472.5086 | 1097.6927 | 316.6421 | 613.5256 | 26.737 | 10.3498 | 21.5621 | 55.1989 | 9554.9662 | 357.3137 |  |  | 26.7037 | 0.94402 | 17.9837 | 4086.0342 | 2058.1738 | 2027.8604 | 930.1677 | 18.101 | 11.591 | 12.5962 | 13.5704 | 11.761 | 6.7852 | 3495.9623 | 7596.1086 | 11487.9911 | 2417.2175 | 5026.152 | 9275.2477 | 0.092994 | 0.101 | 0.083503 | 17.4657 | 10.3617 | 11.7409 | 9.4347 | 22.7738 | 69.8601 | 137.7577 | 109.9231 | 76.7077 | 99.57% | 99.57% | 99.4% | 99.61% | 99.55% | 99.25% | 129.04 | 118.8079 | 143.7068 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 116.4333 | 12 | 25 | 64 | 31 | 98.46% | 0.094039 | 0.094661 | 42.2882 | 39.5684 | 124.9746 | 24.9418 | 98.46% | 3867.2786 | 99.31% | 99.53% | 84.98% |  |  | 99.35% | 0.94402
2022-05-16 | 171.1874 | 152.9811 | 152.9811 | 141.3332 | 128.5674 | 14.1182 | 14.1182 | 3474.1176 | 1098.2013 | 316.7888 | 614.9755 | 25.7185 | 9.9555 | 20.7407 | 53.0962 | 9150.4346 | 354.312 |  |  | 26.7345 | 0.94304 | 17.2986 | 4089.0931 | 2059.1274 | 2029.9656 | 931.7643 | 18.2062 | 11.6479 | 12.8372 | 13.5767 | 11.7664 | 6.7883 | 3366.9721 | 7310.9262 | 11049.611 | 2328.3981 | 4839.2859 | 8924.3613 | 0.093884 | 0.10185 | 0.083709 | 17.5451 | 10.393 | 11.9303 | 9.4161 | 22.7391 | 69.801 | 136.3739 | 108.9463 | 76.4758 | 99.57% | 99.57% | 99.41% | 99.6% | 99.53% | 99.22% | 127.8169 | 117.8196 | 143.3545 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 114.4327 | 12 | 25 | 64 | 31 | 98.47% | 0.094805 | 0.095475 | 42.6914 | 39.8684 | 123.9664 | 24.9034 | 98.47% | 3723.569 | 99.31% | 99.51% | 84.96% |  |  | 99.35% | 0.94304
2022-05-15 | 171.8457 | 153.809 | 153.809 | 142.2724 | 129.6174 | 14.1626 | 14.1626 | 3472.0862 | 1097.5592 | 316.6036 | 612.0141 | 26.4667 | 10.2452 | 21.3441 | 54.6409 | 9556.2678 | 354.395 |  |  | 26.8869 | 0.93822 | 17.8019 | 4084.1003 | 2057.9234 | 2026.1769 | 928.6177 | 18.0367 | 11.5367 | 12.8055 | 13.5687 | 11.7596 | 6.7844 | 3484.2684 | 7577.195 | 11468.7191 | 2408.6277 | 5011.2127 | 9255.6605 | 0.093146 | 0.10129 | 0.084 | 17.4192 | 10.33 | 11.9716 | 9.3139 | 22.4692 | 68.8665 | 136.6729 | 108.9288 | 75.7772 | 99.57% | 99.57% | 99.41% | 99.61% | 99.55% | 99.26% | 128.8301 | 118.4747 | 142.8577 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 115.4158 | 12 | 25 | 64 | 31 | 98.47% | 0.094288 | 0.094886 | 42.3788 | 39.7208 | 123.863 | 24.609 | 98.47% | 3855.6788 | 99.31% | 99.54% | 85.01% |  |  | 99.36% | 0.93822
2022-05-14 | 173.0312 | 155.0028 | 155.0028 | 143.511 | 130.9858 | 14.1871 | 14.1871 | 3464.7108 | 1095.2277 | 315.9311 | 612.1415 | 26.7977 | 10.3733 | 21.6111 | 55.3243 | 9866.604 | 356.2113 |  |  | 26.9652 | 0.93576 | 18.0246 | 4076.8523 | 2053.552 | 2023.3003 | 928.0726 | 18.0284 | 11.4919 | 12.5753 | 13.5399 | 11.7346 | 6.77 | 3590.355 | 7801.8652 | 11799.9161 | 2482.3815 | 5162.0503 | 9526.7688 | 0.092167 | 0.1004 | 0.083682 | 17.4545 | 10.3078 | 11.7612 | 9.1068 | 21.9807 | 67.4223 | 137.4699 | 109.3676 | 75.7041 | 99.58% | 99.58% | 99.42% | 99.63% | 99.57% | 99.29% | 130.199 | 119.5189 | 143.4001 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 116.7428 | 12 | 25 | 64 | 31 | 98.5% | 0.093445 | 0.093996 | 42.0955 | 39.5235 | 124.397 | 24.0736 | 98.5% | 3971.7954 | 99.33% | 99.56% | 84.98% |  |  | 99.37% | 0.93576
2022-05-13 | 174.4739 | 156.4414 | 156.4414 | 144.933 | 132.1646 | 14.4903 | 14.4903 | 3468.7587 | 1096.5073 | 316.3002 | 613.4025 | 26.3774 | 10.2106 | 21.2721 | 54.4565 | 9837.0461 | 361.0967 |  |  | 26.7235 | 0.94339 | 17.7418 | 4082.1613 | 2055.9512 | 2026.21 | 929.7027 | 18.0325 | 11.5085 | 12.6916 | 13.5557 | 11.7483 | 6.7779 | 3596.9808 | 7814.2329 | 11815.551 | 2487.0787 | 5170.9909 | 9540.7164 | 0.092279 | 0.10035 | 0.083445 | 17.4232 | 10.299 | 11.8366 | 9.0305 | 21.8 | 66.8858 | 138.583 | 110.4483 | 76.6272 | 99.59% | 99.59% | 99.43% | 99.64% | 99.58% | 99.3% | 130.0402 | 119.5844 | 143.8071 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 117.6403 | 12 | 25 | 64 | 31 | 98.53% | 0.093448 | 0.094024 | 42.2325 | 39.5588 | 125.4625 | 23.8757 | 98.53% | 3978.6775 | 99.34% | 99.56% | 84.97% |  |  | 99.38% | 0.94339
2022-05-12 | 174.9443 | 156.9091 | 156.9091 | 145.3749 | 132.5941 | 14.1161 | 14.1161 | 3457.0762 | 1092.8144 | 315.2349 | 610.9047 | 26.1779 | 10.1334 | 21.1112 | 54.0447 | 9745.4818 | 359.5751 |  |  | 26.3842 | 0.95423 | 17.6076 | 4067.9809 | 2049.0269 | 2018.954 | 926.1396 | 18.0352 | 11.5342 | 12.6956 | 13.5101 | 11.7087 | 6.755 | 3590.2442 | 7801.704 | 11799.5988 | 2482.2498 | 5161.914 | 9526.5443 | 0.092446 | 0.10036 | 0.083166 | 17.518 | 10.379 | 11.9104 | 9.0522 | 21.8483 | 67.0159 | 139.45 | 111.3219 | 77.5059 | 99.59% | 99.59% | 99.43% | 99.64% | 99.58% | 99.3% | 129.8049 | 119.5641 | 144.2903 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 118.521 | 12 | 25 | 64 | 31 | 98.54% | 0.093495 | 0.094103 | 42.265 | 39.8074 | 126.3417 | 23.9288 | 98.54% | 3971.6538 | 99.34% | 99.56% | 84.98% |  |  | 99.37% | 0.95423
2022-05-11 | 176.1962 | 158.0837 | 158.0837 | 146.4403 | 133.5619 | 14.1215 | 14.1215 | 3472.2006 | 1097.5953 | 316.614 | 613.1579 | 26.8617 | 10.3981 | 21.6627 | 55.4564 | 9826.5538 | 364.1398 |  |  | 26.0856 | 0.96388 | 18.0676 | 4085.3585 | 2057.9912 | 2027.3673 | 929.7719 | 18.1125 | 11.6434 | 12.6869 | 13.5692 | 11.7599 | 6.7846 | 3619.7665 | 7867.3263 | 11901.1122 | 2502.5874 | 5204.7839 | 9607.5256 | 0.093052 | 0.101 | 0.083712 | 17.4818 | 10.4132 | 11.8342 | 9.3472 | 22.5577 | 69.1783 | 140.5575 | 112.225 | 78.1193 | 99.58% | 99.58% | 99.42% | 99.63% | 99.57% | 99.28% | 128.9605 | 118.8064 | 143.3478 |  |  |  | 30 | 26 | 15 | 2340 | 1248 | 360 | 3948 | 119.4659 | 12 | 25 | 64 | 31 | 98.51% | 0.094102 | 0.094714 | 42.4427 | 39.7292 | 127.3435 | 24.7057 | 98.51% | 4004.6438 | 99.33% | 99.55% | 84.99% |  |  | 99.35% | 0.96388
2022-05-10 | 174.3182 | 156.2515 | 156.2515 | 144.6301 | 131.7337 | 14.1382 | 14.1382 | 3460.6352 | 1029.2416 | 342.5598 | 610.9988 | 26.5461 | 12.2275 | 25.474 | 65.2135 | 9539.2118 | 358.6697 |  |  | 26.0807 | 0.96404 | 21.4122 | 4071.634 | 2088.8338 | 1982.8002 | 953.5586 | 18.0667 | 11.6214 | 12.7533 | 13.7725 | 11.0276 | 7.3406 | 3593.4409 | 7444.5938 | 11581.8839 | 2459.2702 | 5059.6154 | 9210.4606 | 0.095581 | 0.095662 | 0.090358 | 17.6901 | 10.5041 | 11.6503 | 11.3548 | 25.5924 | 91.8255 | 138.9114 | 111.1318 | 78.3174 | 99.5% | 99.5% | 99.29% | 99.54% | 99.49% | 99% | 125.5479 | 125.4421 | 132.8049 |  |  |  | 30 | 24.0208 | 15.9896 | 2340 | 1153 | 383.75 | 3876.75 | 117.6521 | 12 | 25 | 64 | 26.0521 | 98.49% | 0.094771 | 0.095088 | 42.4413 | 39.8445 | 126.0549 | 24.9851 | 98.49% | 3900.9333 | 99.32% | 99.44% | 84.99% |  |  | 99.35% | 0.96404
2022-05-09 | 171.3589 | 153.1563 | 153.1563 | 141.3405 | 128.4356 | 14.0453 | 14.0453 | 3462.9899 | 1030.7603 | 343.5868 | 611.2146 | 24.9269 | 11.6445 | 24.2478 | 61.778 | 8833.0307 | 351.934 |  |  | 26.076 | 0.9642 | 20.37 | 4074.2045 | 2088.6429 | 1985.5616 | 954.8013 | 18.2026 | 11.8157 | 12.8568 | 13.7713 | 11.0439 | 7.3626 | 3345.6952 | 6931.3793 | 10793.0412 | 2290.7901 | 4710.7993 | 8579.0423 | 0.097051 | 0.097007 | 0.090714 | 17.7997 | 10.6579 | 11.7285 | 11.6095 | 26.2071 | 93.6854 | 136.8166 | 109.7704 | 78.2565 | 99.49% | 99.49% | 99.28% | 99.49% | 99.44% | 98.91% | 123.6461 | 123.7029 | 132.2838 |  |  |  | 29.9271 | 24 | 16 | 2334.3125 | 1152 | 384 | 3870.3125 | 114.4027 | 12.1458 | 25.2917 | 64.4375 | 26 | 98.48% | 0.096023 | 0.096409 | 42.8751 | 40.1861 | 124.6809 | 25.1987 | 98.48% | 3635.007 | 99.31% | 99.38% | 85% |  |  | 99.34% | 0.9642
2022-05-08 | 171.2273 | 153.1959 | 153.1959 | 141.3252 | 128.3318 | 14.0471 | 14.0471 | 3472.6578 | 1053.318 | 351.106 | 613.4411 | 24.5806 | 13.2357 | 27.4168 | 66.1786 | 9037.487 | 352.4804 |  |  | 26.3903 | 0.95403 | 22.8899 | 4086.0988 | 2068.2338 | 2017.8651 | 964.5471 | 18.0314 | 11.8707 | 12.8556 | 13.6367 | 11.2855 | 7.5237 | 3364.0567 | 7007.7803 | 10980.84 | 2320.9167 | 4748.0962 | 8698.8915 | 0.095222 | 0.098228 | 0.092477 | 17.441 | 10.4818 | 11.5942 | 12.7614 | 29.7261 | 100.0757 | 136.626 | 109.6101 | 77.6178 | 99.43% | 99.42% | 99.24% | 99.45% | 99.37% | 98.85% | 126.0211 | 122.1651 | 129.7626 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 114.3128 | 14 | 29 | 70 | 26 | 98.53% | 0.095745 | 0.095856 | 42.7576 | 39.5171 | 124.1606 | 24.2092 | 98.53% | 3701.9733 | 99.34% | 99.33% | 84.99% |  |  | 99.37% | 0.95403
2022-05-07 | 172.2138 | 154.1339 | 154.1339 | 142.5425 | 129.743 | 14.2631 | 14.2631 | 3470.7128 | 1052.728 | 350.9093 | 613.5144 | 26.0842 | 14.0453 | 29.0939 | 70.2267 | 9547.7549 | 355.5044 |  |  | 26.5709 | 0.94824 | 24.2901 | 4084.2272 | 2067.0754 | 2017.1518 | 964.4238 | 18.08 | 11.5913 | 12.6971 | 13.6291 | 11.2792 | 7.5195 | 3531.676 | 7354.9603 | 11521.5798 | 2436.76 | 4984.0839 | 9128.6526 | 0.094473 | 0.097854 | 0.0931 | 17.4992 | 10.2395 | 11.4518 | 12.8128 | 29.8519 | 100.5277 | 136.7971 | 109.3001 | 76.5875 | 99.42% | 99.42% | 99.23% | 99.47% | 99.4% | 98.9% | 127.0199 | 122.6315 | 128.8934 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.4332 | 14 | 29 | 70 | 26 | 98.51% | 0.095336 | 0.09536 | 42.3685 | 39.1905 | 123.9172 | 24.3115 | 98.51% | 3885.9974 | 99.33% | 99.36% | 84.98% |  |  | 99.36% | 0.94824
2022-05-06 | 171.9211 | 153.78 | 153.78 | 142.1021 | 129.371 | 14.2338 | 14.2338 | 3472.7187 | 1053.3365 | 351.1122 | 612.6063 | 25.9091 | 13.951 | 28.8986 | 69.7552 | 9510.2214 | 354.4269 |  |  | 26.5346 | 0.9494 | 24.127 | 4085.325 | 2068.27 | 2017.0549 | 963.7184 | 18.1411 | 11.6779 | 12.7153 | 13.6369 | 11.2857 | 7.5238 | 3509.023 | 7312.771 | 11464.0684 | 2420.7039 | 4953.5994 | 9079.4332 | 0.094792 | 0.098225 | 0.09343 | 17.554 | 10.3201 | 11.4858 | 12.8343 | 29.8877 | 100.575 | 136.583 | 109.0838 | 76.4544 | 99.42% | 99.42% | 99.23% | 99.47% | 99.4% | 98.89% | 126.5929 | 122.1686 | 128.4379 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.1535 | 14 | 29 | 70 | 26 | 98.51% | 0.095673 | 0.095696 | 42.5342 | 39.3599 | 123.7557 | 24.3408 | 98.51% | 3862.212 | 99.33% | 99.35% | 85% |  |  | 99.36% | 0.9494
2022-05-05 | 172.1406 | 154.058 | 154.058 | 142.4902 | 129.7615 | 14.1728 | 14.1728 | 3469.5105 | 1052.3634 | 350.7878 | 611.5914 | 26.5936 | 14.3196 | 29.662 | 71.598 | 9646.0913 | 354.1468 |  |  | 26.6158 | 0.94681 | 24.7644 | 4081.1019 | 2066.3593 | 2014.7426 | 962.3792 | 18.0826 | 11.5677 | 12.7173 | 13.6243 | 11.2753 | 7.5169 | 3543.1865 | 7385.2316 | 11580.0801 | 2444.2105 | 5002.2034 | 9170.2848 | 0.094312 | 0.097728 | 0.093083 | 17.5255 | 10.2416 | 11.5134 | 12.999 | 30.2683 | 101.8363 | 136.777 | 109.2386 | 76.4596 | 99.41% | 99.41% | 99.22% | 99.47% | 99.39% | 98.89% | 127.237 | 122.7901 | 128.9171 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.581 | 14 | 29 | 70 | 26 | 98.49% | 0.095208 | 0.095224 | 42.3676 | 39.2805 | 123.8469 | 24.6506 | 98.49% | 3900.14 | 99.32% | 99.35% | 85.01% |  |  | 99.35% | 0.94681
2022-05-04 | 172.1813 | 154.1326 | 154.1326 | 142.6234 | 130.0998 | 14.1072 | 14.1072 | 3459.2932 | 1049.2643 | 349.7548 | 609.737 | 26.5355 | 14.2884 | 29.5973 | 71.4419 | 9744.3826 | 352.57 |  |  | 26.4625 | 0.95171 | 24.7104 | 4069.0302 | 2060.2742 | 2008.7561 | 959.4918 | 18.0487 | 11.5092 | 12.8142 | 13.5842 | 11.2421 | 7.4947 | 3575.9183 | 7454.0422 | 11688.8182 | 2466.7074 | 5048.588 | 9256.0361 | 0.094514 | 0.098 | 0.093446 | 17.5707 | 10.2355 | 11.6538 | 12.8808 | 29.9911 | 100.8956 | 136.7877 | 109.1759 | 76.3315 | 99.42% | 99.41% | 99.23% | 99.48% | 99.41% | 98.91% | 126.966 | 122.4486 | 128.4169 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.9353 | 14 | 29 | 70 | 26 | 98.5% | 0.095458 | 0.095463 | 42.372 | 39.4599 | 123.7356 | 24.4249 | 98.5% | 3936.2779 | 99.33% | 99.36% | 85.02% |  |  | 99.36% | 0.95171
2022-05-03 | 172.4057 | 154.1779 | 154.1779 | 142.5418 | 129.7065 | 14.1851 | 14.1851 | 3468.5742 | 1052.0794 | 350.6931 | 612.1152 | 25.3665 | 13.6589 | 28.2934 | 68.2944 | 9427.2592 | 355.382 |  |  | 26.1923 | 0.96042 | 23.6218 | 4080.6894 | 2065.8017 | 2014.8877 | 962.8084 | 18.2278 | 11.6361 | 12.8713 | 13.6207 | 11.2723 | 7.5149 | 3479.8494 | 7251.4316 | 11366.7952 | 2400.5894 | 4912.2545 | 9002.8673 | 0.095366 | 0.098639 | 0.09341 | 17.6675 | 10.2991 | 11.6423 | 12.8025 | 29.8148 | 100.3383 | 137.1721 | 109.755 | 77.2662 | 99.43% | 99.42% | 99.24% | 99.47% | 99.39% | 98.89% | 125.8311 | 121.6559 | 128.4666 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.565 | 14 | 29 | 70 | 26 | 98.53% | 0.0961 | 0.096161 | 42.7352 | 39.6088 | 124.435 | 24.2815 | 98.53% | 3829.9503 | 99.34% | 99.35% | 85% |  |  | 99.36% | 0.96042
2022-05-02 | 170.3224 | 152.1552 | 152.1552 | 140.3255 | 127.3552 | 14.0483 | 14.0483 | 3466.1336 | 1051.3391 | 350.4464 | 611.9233 | 24.4808 | 13.1819 | 27.3055 | 65.9097 | 8821.9408 | 349.3742 |  |  | 26.1128 | 0.963 | 22.7969 | 4078.0569 | 2064.3481 | 2013.7088 | 962.3697 | 18.1672 | 11.8298 | 12.9854 | 13.6111 | 11.2643 | 7.5096 | 3285.2643 | 6844.4157 | 10726.4424 | 2266.5421 | 4637.1165 | 8496.6855 | 0.096433 | 0.099389 | 0.093146 | 17.6252 | 10.4791 | 11.7525 | 13.1121 | 30.5414 | 102.807 | 135.9237 | 109.1429 | 77.6381 | 99.42% | 99.41% | 99.22% | 99.42% | 99.34% | 98.79% | 124.4392 | 120.7381 | 128.8294 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 113.2936 | 14 | 29 | 70 | 26 | 98.5% | 0.096853 | 0.096997 | 42.9823 | 39.8568 | 123.7177 | 24.873 | 98.5% | 3615.4828 | 99.32% | 99.29% | 84.99% |  |  | 99.35% | 0.963
2022-05-01 | 170.768 | 152.6395 | 152.6395 | 140.8305 | 127.9588 | 14.122 | 14.122 | 3472.5502 | 1053.2854 | 351.0951 | 611.2515 | 25.1788 | 13.5578 | 28.084 | 67.789 | 9143.6372 | 351.2864 |  |  | 26.2257 | 0.95934 | 23.4469 | 4083.8017 | 2068.1697 | 2015.632 | 962.3466 | 18.1285 | 11.809 | 12.8488 | 13.6363 | 11.2852 | 7.5235 | 3379.6965 | 7048.0259 | 11057.3857 | 2331.106 | 4772.4517 | 8753.7891 | 0.096194 | 0.099423 | 0.093926 | 17.5546 | 10.4507 | 11.6366 | 13.0868 | 30.4616 | 102.4316 | 135.9941 | 108.8912 | 76.8427 | 99.42% | 99.41% | 99.23% | 99.44% | 99.36% | 98.83% | 124.748 | 120.696 | 127.7597 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 113.849 | 14 | 29 | 70 | 26 | 98.5% | 0.096865 | 0.096944 | 42.7863 | 39.6418 | 123.5022 | 24.8082 | 98.5% | 3720.9798 | 99.32% | 99.32% | 85.03% |  |  | 99.35% | 0.95934
2022-04-30 | 171.587 | 153.6096 | 153.6096 | 142.0382 | 129.1161 | 14.355 | 14.355 | 3462.8138 | 1050.3322 | 350.1107 | 611.6675 | 26.2052 | 14.1105 | 29.2288 | 70.5524 | 9602.5878 | 352.2517 |  |  | 26.2981 | 0.957 | 24.4028 | 4074.4813 | 2062.371 | 2012.1104 | 961.7782 | 17.9774 | 11.5713 | 12.7985 | 13.5981 | 11.2536 | 7.5024 | 3531.3529 | 7355.9285 | 11525.9855 | 2436.4103 | 4984.1165 | 9130.9133 | 0.095594 | 0.099082 | 0.09457 | 17.4634 | 10.2615 | 11.5927 | 12.9634 | 30.1981 | 101.6691 | 136.1318 | 108.6944 | 75.9203 | 99.42% | 99.41% | 99.23% | 99.47% | 99.39% | 98.89% | 125.5315 | 121.112 | 126.8905 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 114.7823 | 14 | 29 | 70 | 26 | 98.5% | 0.096546 | 0.096548 | 42.3473 | 39.3176 | 123.2029 | 24.5934 | 98.5% | 3886.0276 | 99.33% | 99.35% | 84.99% |  |  | 99.36% | 0.957
2022-04-29 | 172.054 | 153.9315 | 153.9315 | 142.3004 | 129.545 | 14.3578 | 14.3578 | 3472.2198 | 1053.1852 | 351.0617 | 612.862 | 27.3561 | 14.7302 | 30.5126 | 73.6512 | 9801.9474 | 354.0291 |  |  | 26.1784 | 0.96087 | 25.4746 | 4085.0819 | 2067.973 | 2017.1089 | 963.9237 | 18.1225 | 11.6311 | 12.8709 | 13.635 | 11.2841 | 7.5228 | 3594.3478 | 7488.2018 | 11735.4301 | 2479.8566 | 5073.3403 | 9295.9054 | 0.096116 | 0.099891 | 0.095799 | 17.5368 | 10.2774 | 11.6213 | 13.3857 | 31.1798 | 104.9568 | 136.3093 | 108.544 | 75.4536 | 99.41% | 99.4% | 99.21% | 99.46% | 99.39% | 98.87% | 124.8498 | 120.1309 | 125.2623 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 115.16 | 14 | 29 | 70 | 26 | 98.47% | 0.097273 | 0.097229 | 42.6245 | 39.4355 | 123.1745 | 25.3925 | 98.47% | 3955.6481 | 99.31% | 99.34% | 85% |  |  | 99.34% | 0.96087
2022-04-28 | 170.2666 | 152.5326 | 152.5326 | 141.0457 | 128.2823 | 14.2447 | 14.2447 | 3437.3601 | 1042.6116 | 347.5372 | 606.333 | 26.3241 | 14.1745 | 29.3615 | 70.8727 | 9677.7508 | 346.5096 |  |  | 26.0277 | 0.96577 | 24.5135 | 4043.6931 | 2047.2113 | 1996.4818 | 953.8702 | 17.734 | 11.4869 | 12.6186 | 13.4981 | 11.1708 | 7.4472 | 3557.0849 | 7413.0029 | 11621.3562 | 2453.8598 | 5021.4684 | 9203.9371 | 0.096595 | 0.10028 | 0.096213 | 17.4259 | 10.3088 | 11.5756 | 12.9522 | 30.1622 | 101.4975 | 134.9565 | 107.5839 | 74.754 | 99.42% | 99.42% | 99.23% | 99.47% | 99.4% | 98.9% | 124.2305 | 119.6654 | 124.7231 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 114.0981 | 14 | 29 | 70 | 26 | 98.51% | 0.097713 | 0.097674 | 41.8395 | 39.3102 | 121.9445 | 24.5643 | 98.51% | 3915.1328 | 99.33% | 99.36% | 85.01% |  |  | 99.36% | 0.96577
2022-04-27 | 170.4727 | 152.6466 | 152.6466 | 141.1205 | 128.4265 | 14.2529 | 14.2529 | 3442.7256 | 1044.239 | 348.0797 | 607.1998 | 26.9681 | 14.5213 | 30.0798 | 72.6064 | 9707.3999 | 346.6593 |  |  | 26.1324 | 0.96236 | 25.1132 | 4049.9254 | 2050.4068 | 1999.5185 | 955.2795 | 17.8261 | 11.5261 | 12.7306 | 13.5192 | 11.1883 | 7.4589 | 3572.0091 | 7443.7774 | 11669.3301 | 2464.2408 | 5042.4391 | 9242.0471 | 0.096331 | 0.1001 | 0.096127 | 17.4761 | 10.3206 | 11.6528 | 13.1871 | 30.7108 | 103.3473 | 135.0582 | 107.5689 | 74.6734 | 99.41% | 99.4% | 99.21% | 99.46% | 99.39% | 98.88% | 124.5699 | 119.8852 | 124.835 |  |  |  | 29 | 24 | 16 | 2262 | 1152 | 384 | 3798 | 114.1678 | 14 | 29 | 70 | 26 | 98.48% | 0.097503 | 0.097453 | 42.0828 | 39.4495 | 121.98 | 25.0108 | 98.48% | 3931.5294 | 99.31% | 99.35% | 85.01% |  |  | 99.35% | 0.96236
2022-04-26 | 169.4658 | 151.6221 | 151.6221 | 140.0267 | 127.2035 | 13.923 | 13.923 | 3448.1368 | 1044.2776 | 335.567 | 609.4204 | 26.9151 | 14.4928 | 30.0207 | 72.4639 | 9537.0555 | 344.9615 |  |  | 26.1947 | 0.96034 | 24.8371 | 4057.5572 | 2068.2922 | 1989.265 | 944.9874 | 17.8436 | 11.5955 | 12.8587 | 13.6371 | 11.1887 | 7.1907 | 3549.1254 | 7437.9836 | 11493.6825 | 2438.9759 | 5022.5775 | 9173.506 | 0.097371 | 0.10048 | 0.093083 | 17.5047 | 10.492 | 11.8619 | 13.3853 | 30.7082 | 99.9691 | 134.4986 | 106.9386 | 74.1869 | 99.41% | 99.4% | 99.21% | 99.45% | 99.39% | 98.91% | 123.2399 | 119.4293 | 128.917 |  |  |  | 30.3438 | 24.8958 | 16 | 2366.8125 | 1195 | 384 | 3945.8125 | 113.2957 | 14 | 29 | 70 | 26 | 98.46% | 0.097679 | 0.097895 | 42.2978 | 39.8585 | 121.5789 | 25.3005 | 98.46% | 3876.8201 | 99.31% | 99.34% | 84.98% |  |  | 99.34% | 0.96034
2022-04-25 | 167.7318 | 149.7587 | 149.7587 | 138.0087 | 124.8495 | 13.9426 | 13.9426 | 3455.553 | 1044.7021 | 321.4468 | 609.5744 | 25.9412 | 13.9683 | 28.9344 | 69.8417 | 8958.3672 | 340.7253 |  |  | 26.2093 | 0.95987 | 23.6905 | 4065.1274 | 2089.4042 | 1975.7232 | 931.0212 | 17.9731 | 11.75 | 12.9202 | 13.7763 | 11.1932 | 6.8881 | 3385.8066 | 7152.5645 | 10887.4961 | 2315.6141 | 4808.2545 | 8760.0247 | 0.099205 | 0.10132 | 0.089305 | 17.6578 | 10.783 | 12.0793 | 13.7202 | 30.9137 | 96.6064 | 133.2944 | 106.0445 | 74.0356 | 99.4% | 99.4% | 99.2% | 99.41% | 99.36% | 98.9% | 120.9619 | 118.4408 | 134.3715 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 111.0083 | 14 | 29 | 70 | 26 | 98.43% | 0.098296 | 0.098922 | 42.6433 | 40.5201 | 120.9933 | 25.8111 | 98.43% | 3668.6831 | 99.29% | 99.31% | 85% |  |  | 99.32% | 0.95987
2022-04-24 | 169.5565 | 151.3046 | 151.3046 | 139.4746 | 126.3733 | 14.2118 | 14.2118 | 3471.4779 | 1049.5166 | 322.9282 | 613.8651 | 26.8963 | 14.4826 | 29.9997 | 72.4132 | 9294.49 | 347.692 |  |  | 26.0969 | 0.96351 | 24.5627 | 4085.343 | 2099.0332 | 1986.3098 | 936.7932 | 18.2519 | 11.83 | 13.0411 | 13.8398 | 11.2448 | 6.9199 | 3493.1563 | 7373.0308 | 11213.5738 | 2389.5693 | 4958.844 | 9026.4778 | 0.099259 | 0.1017 | 0.090171 | 17.7954 | 10.7655 | 12.0738 | 13.9012 | 31.3403 | 98.0253 | 134.3433 | 106.5336 | 73.9418 | 99.39% | 99.4% | 99.2% | 99.42% | 99.37% | 98.91% | 120.8954 | 117.9932 | 133.0803 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 112.1692 | 14 | 29 | 70 | 26 | 98.42% | 0.098587 | 0.099152 | 43.123 | 40.6347 | 121.7344 | 26.1664 | 98.42% | 3783.7136 | 99.29% | 99.32% | 84.97% |  |  | 99.32% | 0.96351
2022-04-23 | 169.7184 | 151.5868 | 151.5868 | 139.9403 | 126.8884 | 14.4891 | 14.4891 | 3462.9306 | 1046.9325 | 322.1331 | 608.5085 | 31.0459 | 16.717 | 34.6281 | 83.5851 | 9771.1156 | 346.8995 |  |  | 25.6562 | 0.97798 | 28.3523 | 4071.4392 | 2093.865 | 1977.5741 | 930.6416 | 18.1317 | 11.6464 | 13.0629 | 13.8057 | 11.2171 | 6.9029 | 3551.4902 | 7507.8116 | 11438.0588 | 2428.9322 | 5045.088 | 9198.7804 | 0.10068 | 0.10328 | 0.092037 | 17.7776 | 10.6799 | 12.2299 | 15.9834 | 36.002 | 112.4188 | 134.1024 | 106.2221 | 73.3493 | 99.31% | 99.31% | 99.09% | 99.34% | 99.29% | 98.78% | 119.1871 | 116.1941 | 130.3822 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 112.4278 | 14 | 29 | 70 | 26 | 98.21% | 0.10013 | 0.10066 | 42.841 | 40.6874 | 121.2739 | 30.0578 | 98.21% | 3849.6163 | 99.19% | 99.23% | 85.05% |  |  | 99.21% | 0.97798
2022-04-22
2022-04-21
2022-04-20
2022-04-19
2022-04-18
2022-04-17
2022-04-16 | 173.8915 | 156.2301 | 156.2301 | 144.9037 | 132.105 | 13.7026 | 13.7026 | 3421.8284 | 1034.5062 | 318.3096 | 605.1944 | 27.3706 | 14.738 | 30.5287 | 73.6901 | 9749.0034 | 356.5675 |  |  | 25.6154 | 0.97716 | 24.9959 | 4027.0227 | 2069.0125 | 1958.0102 | 923.504 | 17.6614 | 11.3264 | 12.5603 | 13.6418 | 11.084 | 6.8209 | 3683.4902 | 7775.526 | 11826.4038 | 2519.5964 | 5229.2626 | 9519.4892 | 0.096016 | 0.097689 | 0.085921 | 17.5949 | 10.5311 | 11.8801 | 13.4117 | 30.2332 | 94.5549 | 138.8339 | 110.8706 | 77.5728 | 99.42% | 99.42% | 99.23% | 99.47% | 99.42% | 99.01% | 124.9797 | 122.8393 | 139.6636 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 118.3575 | 14 | 29 | 70 | 26 | 98.48% | 0.094936 | 0.095582 | 41.548 | 40.0061 | 125.7326 | 25.2427 | 98.48% | 3989.9507 | 99.31% | 99.38% | 84.97% |  |  | 99.34% | 0.97716
2022-04-15 | 176.8271 | 158.8298 | 158.8298 | 147.2471 | 134.2362 | 14.0893 | 14.0893 | 3460.8251 | 1046.296 | 321.9372 | 611.7396 | 28.4975 | 15.3448 | 31.7857 | 76.724 | 9908.1361 | 364.7076 |  |  | 25.519 | 0.98253 | 26.025 | 4072.5647 | 2092.5919 | 1979.9727 | 933.6768 | 17.9973 | 11.5827 | 12.7938 | 13.7973 | 11.2103 | 6.8987 | 3687.1811 | 7783.4869 | 11839.2878 | 2522.2317 | 5234.5525 | 9529.5261 | 0.096005 | 0.097529 | 0.08538 | 17.6304 | 10.5918 | 11.9051 | 14.1859 | 31.9795 | 100.0124 | 141.2048 | 112.9354 | 79.3884 | 99.39% | 99.39% | 99.19% | 99.44% | 99.39% | 98.95% | 124.9938 | 123.0398 | 140.5484 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 120.1846 | 14 | 29 | 70 | 26 | 98.42% | 0.094793 | 0.095477 | 42.3738 | 40.1273 | 128.045 | 26.7002 | 98.42% | 3994.077 | 99.29% | 99.34% | 84.98% |  |  | 99.3% | 0.98253
2022-04-14 | 177.2364 | 159.1716 | 159.1716 | 147.5671 | 134.5177 | 14.0868 | 14.0868 | 3469.801 | 1049.0096 | 322.7722 | 612.3107 | 28.2258 | 15.1985 | 31.4827 | 75.9927 | 9890.5538 | 365.6097 |  |  | 25.2928 | 0.9901 | 25.7769 | 4082.1118 | 2098.0192 | 1984.0925 | 935.0829 | 18.0648 | 11.6045 | 12.8306 | 13.8331 | 11.2394 | 6.9165 | 3651.7423 | 7713.0797 | 11738.8777 | 2497.626 | 5185.5389 | 9445.8269 | 0.096653 | 0.098035 | 0.085487 | 17.6368 | 10.5816 | 11.9166 | 14.3355 | 32.304 | 100.9678 | 141.7051 | 113.5122 | 80.1064 | 99.39% | 99.39% | 99.2% | 99.43% | 99.38% | 98.93% | 124.1558 | 122.4055 | 140.3715 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 120.4038 | 14 | 29 | 70 | 26 | 98.42% | 0.095309 | 0.096032 | 42.5 | 40.1349 | 128.6513 | 26.9717 | 98.42% | 3956.5951 | 99.29% | 99.33% | 85% |  |  | 99.29% | 0.9901
2022-04-13 | 176.2313 | 158.2518 | 158.2518 | 146.6407 | 133.9081 | 14.0175 | 14.0175 | 3437.2564 | 1039.1705 | 319.7448 | 606.4771 | 27.5238 | 14.8205 | 30.6997 | 74.1026 | 9778.9852 | 358.6815 |  |  | 25.2593 | 0.99123 | 25.1358 | 4043.7335 | 2078.3411 | 1965.3924 | 926.2219 | 17.9795 | 11.6112 | 12.7517 | 13.7033 | 11.134 | 6.8517 | 3563.6271 | 7527.3792 | 11456.8699 | 2437.3226 | 5060.5354 | 9218.64 | 0.096258 | 0.097425 | 0.084331 | 17.8042 | 10.7394 | 12.014 | 14.2065 | 32.0122 | 100.0503 | 141.1116 | 113.2796 | 80.5342 | 99.39% | 99.39% | 99.2% | 99.42% | 99.37% | 98.91% | 124.6648 | 123.1713 | 142.2957 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 119.9443 | 14 | 29 | 70 | 26 | 98.42% | 0.094723 | 0.095502 | 42.3424 | 40.5576 | 128.3305 | 26.7281 | 98.42% | 3861.2072 | 99.29% | 99.32% | 85% |  |  | 99.3% | 0.99123
2022-04-12 | 176.9476 | 158.7094 | 158.7094 | 146.878 | 133.828 | 14.1646 | 14.1646 | 3472.2377 | 1049.7463 | 322.9989 | 613.7568 | 26.5795 | 14.312 | 29.6463 | 71.5601 | 9503.1942 | 364.9686 |  |  | 25.6084 | 0.97956 | 24.2734 | 4085.9945 | 2099.4926 | 1986.5019 | 936.7556 | 18.2382 | 11.8314 | 12.957 | 13.8428 | 11.2473 | 6.9214 | 3357.244 | 7086.2137 | 10777.782 | 2296.6738 | 4765.9204 | 8675.4996 | 0.095323 | 0.095847 | 0.08152 | 17.7784 | 10.7659 | 11.9976 | 14.5344 | 32.7687 | 102.4907 | 142.2521 | 114.9477 | 83.1687 | 99.38% | 99.38% | 99.18% | 99.37% | 99.31% | 98.82% | 125.8878 | 125.1993 | 147.2023 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 119.6623 | 14 | 29 | 70 | 26 | 98.38% | 0.093282 | 0.094198 | 43.0266 | 40.5419 | 130.0811 | 27.3586 | 98.38% | 3636.5694 | 99.27% | 99.26% | 84.98% |  |  | 99.28% | 0.97956
2022-04-11 | 173.617 | 155.4745 | 155.4745 | 143.5623 | 130.4642 | 14.1389 | 14.1389 | 3472.2665 | 1049.755 | 323.0015 | 613.0653 | 25.432 | 13.6941 | 28.3664 | 68.4706 | 8919.7771 | 357.7594 |  |  | 25.7586 | 0.97459 | 23.2254 | 4085.3317 | 2099.51 | 1985.8218 | 936.0668 | 18.1425 | 11.9122 | 13.0673 | 13.8429 | 11.2474 | 6.9215 | 3453.9621 | 7295.607 | 11103.3192 | 2362.1873 | 4904.7675 | 8934.4983 | 0.097294 | 0.098756 | 0.085883 | 17.691 | 10.847 | 12.1159 | 13.4527 | 30.3121 | 94.7409 | 138.6644 | 110.9975 | 78.5442 | 99.42% | 99.42% | 99.23% | 99.43% | 99.38% | 98.94% | 123.3372 | 121.512 | 139.7248 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 116.2682 | 14 | 29 | 70 | 26 | 98.49% | 0.095936 | 0.096675 | 43.122 | 40.6539 | 126.1236 | 25.3094 | 98.49% | 3742.2521 | 99.32% | 99.34% | 84.99% |  |  | 99.34% | 0.97459
2022-04-10 | 173.8091 | 155.6838 | 155.6838 | 143.8899 | 130.8924 | 14.1906 | 14.1906 | 3471.2336 | 1049.4427 | 322.9055 | 613.9507 | 25.4175 | 13.6863 | 28.3503 | 68.4317 | 9200.2534 | 358.7967 |  |  | 26.1774 | 0.9609 | 23.2122 | 4085.1843 | 2098.8854 | 1986.2989 | 936.8561 | 18.1254 | 11.7938 | 12.9344 | 13.8388 | 11.244 | 6.9194 | 3618.1213 | 7639.2926 | 11621.1632 | 2474.571 | 5136.9789 | 9353.4368 | 0.096185 | 0.098174 | 0.086601 | 17.6728 | 10.7322 | 11.9733 | 12.6504 | 28.5105 | 89.1487 | 138.2514 | 110.0531 | 76.7755 | 99.45% | 99.45% | 99.27% | 99.49% | 99.44% | 99.05% | 124.7595 | 122.2314 | 138.566 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 116.6329 | 14 | 29 | 70 | 26 | 98.56% | 0.095288 | 0.095895 | 42.8536 | 40.3784 | 125.2685 | 23.8054 | 98.56% | 3919.3795 | 99.35% | 99.4% | 84.97% |  |  | 99.38% | 0.9609
2022-04-09 | 174.2068 | 156.2064 | 156.2064 | 144.5767 | 131.6742 | 14.3246 | 14.3246 | 3471.9978 | 1052.2547 | 327.5649 | 613.0066 | 26.9897 | 14.3506 | 29.162 | 69.1857 | 9694.1364 | 359.8712 |  |  | 26.4407 | 0.95241 | 24.0129 | 4085.0044 | 2092.1783 | 1992.8261 | 940.5714 | 18.0004 | 11.6297 | 12.8558 | 13.7946 | 11.2742 | 7.0192 | 3610.717 | 7617.5452 | 11651.0703 | 2474.3436 | 5124.6639 | 9350.3459 | 0.094804 | 0.097095 | 0.086378 | 17.5235 | 10.5275 | 11.8687 | 13.1064 | 29.2157 | 90.6538 | 138.5821 | 110.5894 | 77.3951 | 99.42% | 99.43% | 99.26% | 99.47% | 99.43% | 99.03% | 126.577 | 123.5908 | 138.9246 |  |  |  | 31.8125 | 26 | 16.1875 | 2481.375 | 1248 | 388.5 | 4117.875 | 117.3672 | 13.625 | 27.6875 | 65.6875 | 25.625 | 98.47% | 0.094189 | 0.094703 | 42.4859 | 39.9197 | 125.5775 | 25.016 | 98.47% | 3926.2883 | 99.31% | 99.39% | 84.99% |  |  | 99.35% | 0.95241
2022-04-08 | 174.1481 | 156.138 | 156.138 | 144.5465 | 131.6118 | 14.4745 | 14.4745 | 3471.7617 | 1063.5146 | 347.6875 | 613.071 | 27.2974 | 13.6487 | 25.0226 | 53.4574 | 9731.6518 | 360.8569 |  |  | 26.2311 | 0.95916 | 21.1196 | 4084.8327 | 2060.5596 | 2024.2731 | 960.7585 | 18.01 | 11.5915 | 12.8551 | 13.5861 | 11.3948 | 7.4504 | 3577.7339 | 7510.4187 | 11739.4424 | 2472.9279 | 5066.7594 | 9312.1846 | 0.094176 | 0.098767 | 0.092434 | 17.3984 | 10.2219 | 11.6397 | 12.371 | 25.8081 | 75.1818 | 138.3721 | 110.6591 | 77.311 | 99.45% | 99.51% | 99.43% | 99.5% | 99.49% | 99.19% | 127.4214 | 121.498 | 129.8219 |  |  |  | 31 | 26 | 17 | 2418 | 1248 | 408 | 4074 | 117.1479 | 12 | 22 | 47 | 24 | 98.47% | 0.095366 | 0.095408 | 42.4567 | 39.26 | 125.2292 | 25.3102 | 98.47% | 3952.4366 | 99.31% | 99.45% | 84.99% |  |  | 99.34% | 0.95916
2022-04-07 | 170.7539 | 153.4117 | 153.4117 | 142.1919 | 129.7624 | 13.8581 | 13.8581 | 3391.9084 | 1014.0234 | 334.6277 | 598.6966 | 27.9694 | 13.4468 | 25.8179 | 58.0903 | 9831.0789 | 342.0492 |  |  | 25.8582 | 0.97132 | 21.5495 | 3990.6049 | 2043.2572 | 1947.3477 | 933.3243 | 17.3422 | 11.2198 | 12.3803 | 13.472 | 10.8645 | 7.1706 | 3592.7428 | 7468.079 | 11609.7225 | 2462.095 | 5066.0759 | 9236.3109 | 0.096231 | 0.097045 | 0.09137 | 17.4828 | 10.4365 | 11.6718 | 12.2927 | 25.7144 | 80.2792 | 135.9815 | 108.7424 | 76.228 | 99.45% | 99.49% | 99.37% | 99.5% | 99.49% | 99.13% | 124.7003 | 123.654 | 131.3348 |  |  |  | 31 | 25 | 16.5 | 2418 | 1200 | 396 | 4014 | 115.9445 | 12.5 | 24 | 54 | 26 | 98.41% | 0.095714 | 0.095995 | 40.9423 | 39.5911 | 123.0917 | 25.9438 | 98.41% | 3908.8729 | 99.28% | 99.44% | 85% |  |  | 99.32% | 0.97132
2022-04-06 | 174.4121 | 156.2801 | 156.2801 | 144.5555 | 131.7471 | 13.992 | 13.992 | 3472.3452 | 1011.6696 | 337.2232 | 613.0693 | 26.213 | 12.1703 | 24.3407 | 57.1069 | 9710.405 | 361.8286 |  |  | 25.6084 | 0.97956 | 20.0803 | 4085.4145 | 2123.4524 | 1961.9621 | 950.2925 | 18.1319 | 11.7246 | 12.9481 | 14.0008 | 10.8393 | 7.2262 | 3400.8942 | 6995.5314 | 10812.062 | 2309.7727 | 4773.4729 | 8628.5878 | 0.098056 | 0.094229 | 0.087065 | 17.785 | 10.7292 | 11.8419 | 12.4296 | 25.8873 | 85.8565 | 139.8661 | 112.6802 | 81.3019 | 99.47% | 99.49% | 99.34% | 99.46% | 99.46% | 99% | 122.3797 | 127.3488 | 137.8286 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 117.7111 | 13 | 26 | 61 | 28 | 98.4% | 0.095073 | 0.095873 | 42.8047 | 40.3562 | 127.7661 | 26.9476 | 98.4% | 3641.2365 | 99.28% | 99.39% | 84.99% |  |  | 99.29% | 0.97956
2022-04-05 | 174.5923 | 156.4054 | 156.4054 | 144.5067 | 131.5535 | 13.9767 | 13.9767 | 3471.2991 | 1011.3648 | 337.1216 | 612.42 | 24.8283 | 11.5274 | 23.0548 | 54.0901 | 9459.0618 | 361.5111 |  |  | 25.2395 | 0.99189 | 19.0195 | 4083.7191 | 2122.8127 | 1960.9065 | 949.5416 | 18.187 | 11.8986 | 13.0258 | 13.9966 | 10.8361 | 7.224 | 3334.0019 | 6860.5196 | 10607.2855 | 2264.021 | 4680.3596 | 8463.4995 | 0.098981 | 0.094955 | 0.087377 | 17.8512 | 10.8986 | 11.9289 | 12.1584 | 25.3147 | 83.9256 | 140.2597 | 113.1929 | 82.0064 | 99.49% | 99.51% | 99.36% | 99.46% | 99.46% | 99.01% | 121.2348 | 126.3758 | 137.3358 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 117.6814 | 13 | 26 | 61 | 28 | 98.45% | 0.095836 | 0.096681 | 43.1114 | 40.6788 | 128.3174 | 26.3524 | 98.45% | 3570.0963 | 99.3% | 99.39% | 85% |  |  | 99.31% | 0.99189
2022-04-04 | 173.1592 | 155.0598 | 155.0598 | 143.0377 | 129.7855 | 13.9708 | 13.9708 | 3473.2523 | 1011.9339 | 337.3113 | 611.9761 | 23.9801 | 11.1336 | 22.2672 | 52.2424 | 8772.395 | 362.3697 |  |  | 25.2007 | 0.9932 | 18.3698 | 4085.2283 | 2124.0071 | 1961.2212 | 949.2873 | 18.0993 | 12.0221 | 13.2014 | 14.0044 | 10.8421 | 7.2281 | 3470.0293 | 7145.3203 | 11054.9101 | 2355.7645 | 4872.7876 | 8817.5397 | 0.10049 | 0.097166 | 0.091319 | 17.7572 | 11.0114 | 12.0979 | 11.307 | 23.5286 | 77.9504 | 138.4156 | 110.8254 | 78.6143 | 99.53% | 99.54% | 99.41% | 99.52% | 99.52% | 99.12% | 119.4162 | 123.5003 | 131.408 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 115.8099 | 13 | 26 | 61 | 28 | 98.57% | 0.097958 | 0.09863 | 43.3228 | 40.8664 | 125.9613 | 24.4946 | 98.57% | 3716.6477 | 99.35% | 99.45% | 85.02% |  |  | 99.36% | 0.9932
2022-04-03 | 173.9409 | 155.8276 | 155.8276 | 143.9209 | 130.7609 | 13.9675 | 13.9675 | 3468.8508 | 1010.6515 | 336.8838 | 613.3561 | 24.3894 | 11.3237 | 22.6473 | 53.1341 | 9148.7193 | 365.7447 |  |  | 25.1972 | 0.99332 | 18.6833 | 4082.2069 | 2121.3154 | 1960.8914 | 950.2399 | 18.1133 | 11.9067 | 13.1421 | 13.9867 | 10.8284 | 7.2189 | 3631.1306 | 7469.0237 | 11542.177 | 2465.7849 | 5096.6022 | 9211.9846 | 0.10021 | 0.097308 | 0.092431 | 17.7857 | 10.9022 | 12.0166 | 10.9743 | 22.8532 | 75.7994 | 138.6444 | 110.5369 | 77.5791 | 99.54% | 99.56% | 99.42% | 99.55% | 99.55% | 99.18% | 119.7508 | 123.3201 | 129.8263 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 116.7802 | 13 | 26 | 61 | 28 | 98.61% | 0.098036 | 0.098608 | 43.1622 | 40.7045 | 125.7602 | 23.7909 | 98.61% | 3887.4446 | 99.37% | 99.49% | 84.97% |  |  | 99.38% | 0.99332
2022-04-02 | 175.4312 | 157.3447 | 157.3447 | 145.5909 | 132.5708 | 13.9752 | 13.9752 | 3473.9555 | 1012.1388 | 337.3796 | 611.6179 | 25.1925 | 11.6965 | 23.393 | 54.8837 | 9652.1916 | 369.3523 |  |  | 25.3716 | 0.98746 | 19.2985 | 4085.5734 | 2124.4371 | 1961.1363 | 948.9975 | 18.0865 | 11.7538 | 13.1084 | 14.0073 | 10.8443 | 7.2296 | 3692.1023 | 7604.9081 | 11769.6393 | 2506.2877 | 5185.3258 | 9386.0445 | 0.09884 | 0.095881 | 0.090999 | 17.7434 | 10.7676 | 12.0201 | 11.1029 | 23.0987 | 76.5019 | 139.9398 | 111.6829 | 78.4499 | 99.53% | 99.55% | 99.42% | 99.56% | 99.55% | 99.18% | 121.4089 | 125.1545 | 131.8692 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.6136 | 13 | 26 | 61 | 28 | 98.58% | 0.096639 | 0.097216 | 42.9486 | 40.5312 | 126.8876 | 24.0474 | 98.58% | 3954.9672 | 99.36% | 99.5% | 85.03% |  |  | 99.37% | 0.98746
2022-04-01 | 175.4826 | 157.6494 | 157.6494 | 146.0057 | 132.6466 | 14.1913 | 14.1913 | 3467.4009 | 1010.2291 | 336.743 | 613.0229 | 26.0352 | 12.0878 | 24.1756 | 56.7196 | 9763.1638 | 367.6132 |  |  | 25.0417 | 0.99858 | 19.9441 | 4080.4238 | 2120.4288 | 1959.995 | 949.7659 | 17.8332 | 11.6437 | 12.9011 | 13.9808 | 10.8239 | 7.2159 | 3726.8401 | 7665.2207 | 11844.6893 | 2530.9405 | 5230.7368 | 9453.7146 | 0.099878 | 0.096848 | 0.092203 | 17.5223 | 10.6689 | 11.8054 | 11.4689 | 23.8856 | 79.2297 | 139.7804 | 111.6034 | 78.1498 | 99.52% | 99.54% | 99.4% | 99.55% | 99.54% | 99.16% | 120.1463 | 123.9059 | 130.1469 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.5293 | 13 | 26 | 61 | 28 | 98.55% | 0.09768 | 0.09825 | 42.3781 | 39.9966 | 126.6531 | 24.8651 | 98.55% | 3989.8455 | 99.35% | 99.48% | 84.98% |  |  | 99.35% | 0.99858
2022-03-31 | 175.8328 | 157.9776 | 157.9776 | 146.262 | 133.0094 | 14.1633 | 14.1633 | 3468.1007 | 1010.433 | 336.811 | 613.3561 | 26.0788 | 12.108 | 24.2161 | 56.8146 | 9799.9112 | 367.9472 |  |  | 25.0785 | 0.99733 | 19.9775 | 4081.4568 | 2120.8567 | 1960.6001 | 950.1671 | 17.8552 | 11.7157 | 12.9244 | 13.9837 | 10.8261 | 7.2174 | 3624.7516 | 7453.6571 | 11515.4703 | 2461.8312 | 5086.9739 | 9191.9361 | 0.099267 | 0.095854 | 0.090206 | 17.5367 | 10.7292 | 11.8183 | 11.7982 | 24.576 | 81.537 | 140.4933 | 112.6427 | 79.7968 | 99.51% | 99.52% | 99.38% | 99.52% | 99.52% | 99.11% | 120.8857 | 125.1909 | 133.029 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 118.8436 | 13 | 26 | 61 | 28 | 98.51% | 0.096725 | 0.097393 | 42.4952 | 40.0843 | 127.6593 | 25.5832 | 98.51% | 3880.2744 | 99.33% | 99.45% | 84.97% |  |  | 99.33% | 0.99733
2022-03-30 | 180.2608 | 161.9473 | 161.9473 | 149.0238 | 135.1723 | 14.7229 | 14.7229 | 3471.1622 | 970.6593 | 443.1271 | 613.0012 | 18.117 | 11.776 | 19.9287 | 45.2925 | 8761.4572 | 382.6551 |  |  | 24.8597 | 1.0048 | 18.3345 | 4084.1634 | 2057.3758 | 2026.7876 | 1056.1283 | 18.3135 | 12.9235 | 13.7092 | 13.5651 | 10.3999 | 9.4956 | 3324.3902 | 6361.4328 | 10927.2526 | 2299.2511 | 4518.9644 | 8236.6281 | 0.094037 | 0.088356 | 0.1104 | 17.6836 | 10.858 | 11.3653 | 12.0074 | 22.0342 | 96.1507 | 144.9438 | 118.2675 | 86.4185 | 99.49% | 99.56% | 99.45% | 99.48% | 99.51% | 98.83% | 127.61 | 135.8138 | 108.6911 |  |  |  | 30 | 23 | 21 | 2340 | 1104 | 504 | 3948 | 120.5124 | 13 | 22 | 50 | 20 | 98.91% | 0.094838 | 0.094538 | 44.9462 | 39.9069 | 132.1342 | 18.9073 | 98.91% | 3677.9242 | 99.51% | 99.39% | 84.99% |  |  | 99.51% | 1.0048
2022-03-29 | 174.6962 | 133.9827 | 152 | 139.9891 | 131.4605 | 13.9856 | 13.9856 | 3458.1516 | 1130 | 434 | 609.8834 | 23.9095 | 14 | 24 | 66 | 8911.4066 | 363.4406 |  |  | 24.8597 | 1.0048 | 23.7937 | 4068.0349 | 1894.1516 | 2173.8834 | 1043.8834 | 18.0173 | 12.0109 | 13.2295 | 12.4889 | 12.1071 | 9.3 | 3086.1081 | 6400.8291 | 10908.7661 | 2224.331 | 4347.4606 | 8257.9949 | 0.097049 | 0.1102 | 0.11568 | 16.8528 | 9.4636 | 11.1208 | 13.5851 | 32.1103 | 136.8694 | 129.3022 | 110.3916 | 80.7792 | 99.37% | 99.45% | 99.2% | 99.39% | 99.26% | 98.34% | 123.6488 | 108.8938 | 103.7349 |  |  |  | 31 | 24 | 16 |  |  |  |  | 117.481 | 13 | 26 | 61 | 28 | 98.56% | 0.10424 | 0.10368 | 43.2576 | 37.4372 | 127.7202 | 24.8765 | 98.56% | 3675.3219 | 99.35% | 99.18% | 85.01% | 18.0173 |  | 99.35% | 1.0048 | 149.2765
2022-03-28 | 174.3393 | 134.8875 | 153 | 141.0155 | 130.7747 | 14.0127 | 14.0127 | 3471.5113 | 1130 | 434 | 613.8288 | 23.7858 | 14 | 24 | 66 | 8757.9722 | 363.85 |  |  | 24.8027 | 1.0067 | 23.756 | 4085.3401 | 1907.5113 | 2177.8288 | 1047.8288 | 18.1125 | 11.9845 | 13.3067 | 12.577 | 12.1071 | 9.3 | 3027.2376 | 6265.9903 | 10649.6159 | 2179.0921 | 4260.7215 | 8073.8974 | 0.097567 | 0.10901 | 0.1144 | 16.8558 | 9.4082 | 11.1061 | 13.9921 | 32.8277 | 140.2625 | 129.7752 | 111.8115 | 81.8429 | 99.36% | 99.44% | 99.18% | 99.36% | 99.23% | 98.26% | 122.9928 | 110.0803 | 104.897 |  |  |  | 31.7292 | 24.7292 | 16 |  |  |  |  | 116.7385 | 13 | 26 | 61 | 28 | 98.53% | 0.10392 | 0.1034 | 43.4037 | 37.3701 | 127.7902 | 25.4575 | 98.53% | 3593.6307 | 99.34% | 99.14% | 84.97% | 18.1125 |  | 99.33% | 1.0067 | 149.7976
2022-03-27 | 174.143 | 136.1158 | 154 | 142.2031 | 131.3121 | 14.1712 | 14.1712 | 3460.2575 | 1130 | 434 | 610.6948 | 25.0918 | 14 | 24 | 66 | 9250.0553 | 361.7799 |  |  | 25.158 | 0.99464 | 23.7877 | 4070.9522 | 1896.2575 | 2174.6948 | 1044.6948 | 17.8842 | 11.7969 | 13.1061 | 12.5028 | 12.1071 | 9.3 | 3171.6145 | 6576.2495 | 11202.8624 | 2285.3967 | 4467.3396 | 8482.6327 | 0.095954 | 0.1078 | 0.1149 | 16.7134 | 9.288 | 11.0009 | 13.1032 | 30.9333 | 131.9001 | 129.6013 | 111.7137 | 80.5032 | 99.39% | 99.46% | 99.22% | 99.43% | 99.31% | 98.45% | 125.0593 | 111.3214 | 104.4346 |  |  |  | 32 | 25 | 16 |  |  |  |  | 117.086 | 13 | 26 | 61 | 28 | 98.52% | 0.10278 | 0.1022 | 42.7872 | 37.0023 | 126.4997 | 25.1745 | 98.52% | 3775.2269 | 99.34% | 99.23% | 85% | 17.8842 |  | 99.34% | 0.99464 | 150.5301
2022-03-26 | 174.6023 | 137.2005 | 155 | 143.314 | 131.9793 | 14.338 | 14.338 | 3454.7676 | 1130 | 434 | 610.6542 | 26.1543 | 14 | 24 | 66 | 9608.9723 | 361.5521 |  |  | 25.3196 | 0.9892 | 23.8033 | 4065.4218 | 1890.7676 | 2174.6542 | 1044.6542 | 17.7995 | 11.686 | 13.0256 | 12.4666 | 12.1071 | 9.3 | 3282.0642 | 6806.3046 | 11596.7278 | 2366.5516 | 4623.2232 | 8780.0543 | 0.095007 | 0.1071 | 0.11537 | 16.6565 | 9.201 | 10.9342 | 12.5482 | 29.7268 | 126.7348 | 129.8006 | 111.8229 | 79.7384 | 99.41% | 99.48% | 99.25% | 99.47% | 99.36% | 98.56% | 126.3065 | 112.0433 | 104.0114 |  |  |  | 32 | 25 | 16 |  |  |  |  | 117.6691 | 13 | 26 | 61 | 28 | 98.52% | 0.10214 | 0.10152 | 42.5112 | 36.7917 | 126.0504 | 25.1552 | 98.52% | 3910.36 | 99.33% | 99.29% | 84.98% | 17.7995 |  | 99.34% | 0.9892 | 151.4022
2022-03-25 | 174.242 | 138.1963 | 156 | 144.2943 | 131.8162 | 14.1034 | 14.1034 | 3449.3571 | 1130 | 434 | 609.81 | 26.3071 | 14 | 24 | 66 | 9723.0081 | 359.1438 |  |  | 25.4212 | 0.9858 | 23.8186 | 4059.1671 | 1885.3571 | 2173.81 | 1043.81 | 17.8037 | 11.7057 | 12.8648 | 12.4309 | 12.1071 | 9.3 | 3300.25 | 6847.0282 | 11673.0663 | 2381.1373 | 4649.7393 | 8834.9861 | 0.094062 | 0.1057 | 0.11445 | 16.689 | 9.2237 | 10.8157 | 12.3929 | 29.4556 | 125.5137 | 130.2801 | 112.9151 | 80.1069 | 99.41% | 99.48% | 99.25% | 99.48% | 99.37% | 98.58% | 127.5755 | 113.528 | 104.8528 |  |  |  | 32 | 25 | 16 |  |  |  |  | 117.7211 | 13 | 26 | 61 | 28 | 98.52% | 0.10105 | 0.10044 | 42.3742 | 36.7284 | 125.8029 | 25.0094 | 98.52% | 3936.3519 | 99.33% | 99.3% | 84.98% | 17.8037 |  | 99.35% | 0.9858 | 151.9446
2022-03-24 | 174.0493 | 139.3668 | 157 | 145.4402 | 131.9535 | 13.7747 | 13.7747 | 3441.4264 | 1130 | 434 | 607.3211 | 26.4586 | 14 | 24 | 66 | 9945.17 | 355.5036 |  |  | 25.5881 | 0.98024 | 23.8413 | 4048.7475 | 1877.4264 | 2171.3211 | 1041.3211 | 17.6332 | 11.5598 | 12.675 | 12.3786 | 12.1071 | 9.3 | 3348.7905 | 6956.7204 | 11880.9241 | 2417.9724 | 4720.81 | 8983.7139 | 0.092687 | 0.10414 | 0.11348 | 16.5806 | 9.13 | 10.7044 | 12.0842 | 28.8485 | 122.7395 | 130.9135 | 113.9613 | 80.3336 | 99.42% | 99.49% | 99.27% | 99.5% | 99.39% | 98.63% | 129.4676 | 115.2299 | 105.7459 |  |  |  | 30.0417 | 25 | 16 |  |  |  |  | 118.1943 | 13 | 26 | 61 | 28 | 98.53% | 0.099679 | 0.09907 | 41.868 | 36.415 | 125.6706 | 24.544 | 98.53% | 4002.1231 | 99.34% | 99.33% | 85% | 17.6332 |  | 99.36% | 0.98024 | 152.6347
2022-03-23 | 173.9779 | 140.1893 | 158 | 146.2177 | 131.3224 | 13.9999 | 13.9999 | 3456.2452 | 1130 | 434 | 610.2966 | 25.406 | 14 | 24 | 66 | 9556.0207 | 358.2567 |  |  | 25.6057 | 0.97965 | 23.7991 | 4066.5417 | 1892.2452 | 2174.2966 | 1044.2966 | 17.8107 | 11.7823 | 12.9403 | 12.4763 | 12.1071 | 9.3 | 3241.9371 | 6723.9641 | 11458.64 | 2337.1141 | 4566.96 | 8674.5971 | 0.092969 | 0.10279 | 0.11148 | 16.664 | 9.2799 | 10.8696 | 12.5935 | 29.8025 | 127.0372 | 131.4681 | 115.3941 | 81.7271 | 99.4% | 99.47% | 99.24% | 99.46% | 99.35% | 98.54% | 129.0751 | 116.7485 | 107.6447 |  |  |  | 30 | 25 | 16 |  |  |  |  | 117.3423 | 13 | 26 | 61 | 28 | 98.54% | 0.099072 | 0.098503 | 42.5334 | 36.8135 | 126.049 | 24.5134 | 98.54% | 3861.9462 | 99.34% | 99.28% | 84.99% | 17.8107 |  | 99.36% | 0.97965 | 153.1575
2022-03-22 | 174.2484 | 141.0319 | 159 | 147.0399 | 131.2335 | 14.0519 | 14.0519 | 3456.9314 | 1130 | 434 | 611.51 | 24.79 | 14 | 24 | 66 | 9283.8934 | 359.8515 |  |  | 25.2684 | 0.99092 | 23.7971 | 4068.4415 | 1892.9314 | 2175.51 | 1045.51 | 17.9681 | 11.9601 | 13.1485 | 12.4809 | 12.1071 | 9.3 | 3160.8783 | 6551.2547 | 11153.96 | 2278.9128 | 4451.4005 | 8448.2094 | 0.093507 | 0.10269 | 0.1108 | 16.7987 | 9.4093 | 11.0201 | 13.0684 | 30.928 | 131.9422 | 132.2636 | 116.831 | 83.1737 | 99.39% | 99.46% | 99.22% | 99.43% | 99.31% | 98.44% | 128.3326 | 116.8578 | 108.304 |  |  |  | 30 | 25 | 16 |  |  |  |  | 117.1723 | 13 | 26 | 61 | 28 | 98.54% | 0.099212 | 0.098679 | 43.0767 | 37.2282 | 126.7219 | 24.8316 | 98.54% | 3763.578 | 99.34% | 99.23% | 84.97% | 17.9681 |  | 99.35% | 0.99092 | 153.8069
2022-03-21 | 174.1816 | 141.8694 | 160 | 147.8662 | 130.5271 | 14.0479 | 14.0479 | 3470.1014 | 1130 | 434 | 613.5027 | 23.5983 | 14 | 24 | 66 | 8782.2183 | 361.2638 |  |  | 25.0128 | 0.99957 | 23.7599 | 4083.6041 | 1906.1014 | 2177.5027 | 1047.5027 | 18.1306 | 12.1338 | 13.3335 | 12.5677 | 12.1071 | 9.3 | 3012.0955 | 6235.5218 | 10599.9239 | 2168.5431 | 4239.6709 | 8035.3611 | 0.094308 | 0.10186 | 0.10898 | 16.881 | 9.5282 | 11.135 | 13.9497 | 32.7557 | 139.9311 | 133.2048 | 118.8069 | 85.302 | 99.35% | 99.43% | 99.18% | 99.36% | 99.23% | 98.26% | 127.2431 | 117.8067 | 110.1149 |  |  |  | 30 | 25 | 16 |  |  |  |  | 116.4541 | 13 | 26 | 61 | 28 | 98.54% | 0.099072 | 0.098602 | 43.5979 | 37.5443 | 127.65 | 25.1851 | 98.54% | 3576.7364 | 99.34% | 99.14% | 84.98% | 18.1306 |  | 99.34% | 0.99957 | 154.3379
2022-03-20 | 174.9073 | 142.8964 | 161 | 148.8121 | 131.3515 | 14.0363 | 14.0363 | 3473.3794 | 1130 | 434 | 614.0511 | 23.6721 | 14 | 24 | 66 | 8995.8957 | 363.2307 |  |  | 24.9043 | 1.0033 | 23.7507 | 4087.4305 | 1909.3794 | 2178.0511 | 1048.0511 | 18.1036 | 12.1879 | 13.3224 | 12.5893 | 12.1071 | 9.3 | 3079.2419 | 6373.3785 | 10831.3175 | 2215.9465 | 4333.8397 | 8211.9885 | 0.094358 | 0.1018 | 0.10936 | 16.8382 | 9.5659 | 11.1148 | 13.7253 | 32.1624 | 137.4276 | 133.8558 | 119.3206 | 85.3156 | 99.37% | 99.45% | 99.2% | 99.38% | 99.26% | 98.33% | 127.1753 | 117.8803 | 109.7269 |  |  |  | 30 | 25 | 16 |  |  |  |  | 117.3262 | 13 | 26 | 61 | 28 | 98.56% | 0.09914 | 0.098653 | 43.6139 | 37.5188 | 127.9188 | 24.8434 | 98.56% | 3654.1716 | 99.35% | 99.17% | 84.98% | 18.1036 |  | 99.35% | 1.0033 | 155.2503
2022-03-19 | 175.6522 | 153.9004 | 172 | 160.0118 | 132.4685 | 14.0323 | 14.0323 | 3473.3044 | 1130 | 434 | 612.0373 | 24.7983 | 14 | 24 | 66 | 9428.4424 | 364.1892 |  |  | 25.032 | 0.99891 | 23.7509 | 4085.3417 | 1909.3044 | 2176.0373 | 1046.0373 | 18.0996 | 11.9882 | 13.151 | 12.5888 | 12.1071 | 9.3 | 3213.3667 | 6658.7357 | 11333.6917 | 2311.733 | 4524.9284 | 8585.6858 | 0.090303 | 0.093412 | 0.10367 | 16.851 | 9.4268 | 11.0118 | 13.0991 | 30.6707 | 130.8764 | 139.2553 | 129.4689 | 89.6094 | 99.39% | 99.47% | 99.23% | 99.43% | 99.32% | 98.48% | 132.8863 | 128.4628 | 115.7508 |  |  |  | 30 | 25 | 16 |  |  |  |  | 118.4341 | 13 | 26 | 61 | 28 | 98.56% | 0.093437 | 0.092985 | 43.2388 | 37.2895 | 127.7919 | 24.8149 | 98.56% | 3815.7204 | 99.35% | 99.24% | 85.02% | 18.0996 |  | 99.35% | 0.99891 | 162.8602
2022-03-18 | 175.0129 | 154.9767 | 173 | 161.122 | 132.1246 | 13.9987 | 13.9987 | 3457.8235 | 1130 | 434 | 611.2202 | 25.198 | 14 | 24 | 66 | 9488.1738 | 360.193 |  |  | 25.1494 | 0.99493 | 23.7946 | 4069.0437 | 1893.8235 | 2175.2202 | 1045.2202 | 18.0233 | 11.878 | 13.1062 | 12.4867 | 12.1071 | 9.3 | 3232.9381 | 6702.1595 | 11414.1985 | 2330.3974 | 4553.345 | 8643.9533 | 0.089112 | 0.092365 | 0.10311 | 16.849 | 9.3473 | 10.9905 | 12.8375 | 30.3579 | 129.4762 | 139.4141 | 130.4156 | 89.7349 | 99.4% | 99.47% | 99.24% | 99.45% | 99.33% | 98.5% | 134.6619 | 129.9198 | 116.3766 |  |  |  | 30 | 25 | 16 |  |  |  |  | 118.1182 | 13 | 26 | 61 | 28 | 98.55% | 0.092393 | 0.091932 | 43.0075 | 37.1867 | 127.0428 | 24.7845 | 98.55% | 3849.276 | 99.35% | 99.26% | 84.98% | 18.0233 |  | 99.35% | 0.99493 | 163.3642
2022-03-17 | 176.1435 | 155.9831 | 174 | 161.9558 | 132.9897 | 14.0796 | 14.0796 | 3471.9424 | 1130 | 434 | 612.9081 | 25.4462 | 14 | 24 | 66 | 9530.0487 | 365.0685 |  |  | 25.1657 | 0.99438 | 23.7548 | 4084.8505 | 1907.9424 | 2176.9081 | 1046.9081 | 18.0169 | 12.0442 | 13.1827 | 12.5798 | 12.1071 | 9.3 | 3255.3338 | 6743.1349 | 11471.2117 | 2342.5282 | 4583.2579 | 8692.3902 | 0.089134 | 0.09183 | 0.10246 | 16.7725 | 9.4631 | 11.0209 | 12.8591 | 30.1431 | 128.6837 | 140.341 | 131.102 | 90.2612 | 99.4% | 99.48% | 99.24% | 99.45% | 99.34% | 98.52% | 134.6283 | 130.6756 | 117.1237 |  |  |  | 30 | 25 | 16 |  |  |  |  | 118.876 | 13 | 26 | 61 | 28 | 98.54% | 0.092128 | 0.091677 | 43.2438 | 37.2566 | 127.9358 | 25.0113 | 98.54% | 3865.556 | 99.34% | 99.27% | 85% | 18.0169 |  | 99.35% | 0.99438 | 164.3626
2022-03-16 | 176.5877 | 156.8885 | 175 | 162.9645 | 133.3988 | 14.0707 | 14.0707 | 3471.2512 | 1130 | 434 | 613.054 | 25.7979 | 14 | 24 | 66 | 9531.5071 | 365.6012 |  |  | 24.9847 | 1.0005 | 23.7567 | 4084.3052 | 1907.2512 | 2177.054 | 1047.054 | 18.1115 | 12.0355 | 13.2433 | 12.5753 | 12.1071 | 9.3 | 3256.002 | 6744.0383 | 11471.6294 | 2343.2652 | 4584.055 | 8693.1681 | 0.08922 | 0.091691 | 0.10228 | 16.8622 | 9.4551 | 11.0686 | 12.9297 | 30.3238 | 129.4662 | 141.021 | 132.1112 | 90.9751 | 99.4% | 99.48% | 99.24% | 99.45% | 99.34% | 98.51% | 134.4997 | 130.8739 | 117.3261 |  |  |  | 30 | 25 | 16 |  |  |  |  | 119.2857 | 13 | 26 | 61 | 28 | 98.52% | 0.0921 | 0.091657 | 43.3903 | 37.3859 | 128.3459 | 25.5013 | 98.52% | 3866.6209 | 99.33% | 99.26% | 84.99% | 18.1115 |  | 99.33% | 1.0005 | 165.1486
2022-03-15 | 176.0418 | 157.9188 | 176 | 163.9064 | 132.5688 | 14.0541 | 14.0541 | 3471.7759 | 1130 | 434 | 613.3859 | 24.5075 | 14 | 24 | 66 | 9229.6902 | 365.1234 |  |  | 24.7903 | 1.0072 | 23.7552 | 4085.1618 | 1907.7759 | 2177.3859 | 1047.3859 | 18.0812 | 12.0936 | 13.3143 | 12.5787 | 12.1071 | 9.3 | 3165.2709 | 6554.3141 | 11145.1081 | 2278.0321 | 4455.7796 | 8447.2977 | 0.089465 | 0.091176 | 0.10151 | 16.8291 | 9.4977 | 11.1213 | 13.3919 | 31.4039 | 134.1188 | 141.6061 | 133.7402 | 92.2771 | 99.39% | 99.46% | 99.22% | 99.41% | 99.3% | 98.41% | 134.1303 | 131.6142 | 118.2206 |  |  |  | 30 | 25.2083 | 16.2083 |  |  |  |  | 118.4912 | 12.7917 | 25.7917 | 60.375 | 27.375 | 98.55% | 0.091939 | 0.091527 | 43.4891 | 37.4482 | 128.4434 | 25.0948 | 98.55% | 3758.0573 | 99.35% | 99.21% | 84.99% | 18.0812 |  | 99.34% | 1.0072 | 165.605
2022-03-14 | 175.6774 | 158.7938 | 177 | 164.7968 | 131.9407 | 14.0527 | 14.0527 | 3471.5382 | 1130 | 434 | 612.9849 | 23.5793 | 14 | 24 | 66 | 8864.9906 | 364.1579 |  |  | 24.6036 | 1.0136 | 23.7559 | 4084.5231 | 1907.5382 | 2176.9849 | 1046.9849 | 18.2062 | 12.2032 | 13.3058 | 12.5772 | 12.1071 | 9.3 | 3057.917 | 6332.3922 | 10769.0663 | 2200.901 | 4304.7688 | 8161.7374 | 0.089619 | 0.090605 | 0.10045 | 16.9497 | 9.5874 | 11.1223 | 13.948 | 32.713 | 139.6975 | 142.2484 | 135.4419 | 93.8374 | 99.36% | 99.44% | 99.19% | 99.37% | 99.24% | 98.29% | 133.9007 | 132.4432 | 119.4569 |  |  |  | 30 | 26 | 17 |  |  |  |  | 117.8613 | 12 | 25 | 58 | 25 | 98.56% | 0.091668 | 0.091294 | 43.7152 | 37.6594 | 128.7866 | 25.1476 | 98.56% | 3630.9223 | 99.35% | 99.15% | 84.99% | 18.2062 |  | 99.34% | 1.0136 | 166.0692
2022-03-13 | 176.4637 | 159.89 | 178 | 165.8551 | 132.784 | 14.1464 | 14.1464 | 3470.2459 | 1130 | 434 | 611.7542 | 23.5989 | 14 | 24 | 66 | 9049.4499 | 364.9912 |  |  | 24.6077 | 1.0134 | 23.7595 | 4082.0001 | 1906.2459 | 2175.7542 | 1045.7542 | 18.11 | 12.1449 | 13.2717 | 12.5687 | 12.1071 | 9.3 | 3110.021 | 6444.6514 | 10969.8919 | 2238.3838 | 4379.4218 | 8309.8516 | 0.089132 | 0.090218 | 0.10032 | 16.8753 | 9.5525 | 11.1185 | 13.7032 | 32.1509 | 137.1882 | 142.9085 | 136.0041 | 93.9539 | 99.37% | 99.45% | 99.21% | 99.39% | 99.27% | 98.35% | 134.6322 | 133.0117 | 119.6221 |  |  |  | 30 | 26 | 17 |  |  |  |  | 118.6427 | 12 | 25 | 58 | 25 | 98.58% | 0.091269 | 0.090884 | 43.5266 | 37.5464 | 129.1424 | 24.7202 | 98.58% | 3694.8771 | 99.36% | 99.18% | 85.01% | 18.11 |  | 99.35% | 1.0134 | 167.0398
2022-03-12 | 177.5158 | 161.0852 | 179 | 167.1066 | 134.3184 | 14.2135 | 14.2135 | 3449.38 | 1130 | 434 | 610.1292 | 24.8029 | 14 | 24 | 66 | 9477.9181 | 365.0362 |  |  | 24.4551 | 1.0187 | 23.8186 | 4059.5092 | 1885.38 | 2174.1292 | 1044.1292 | 17.9148 | 11.8934 | 13.1297 | 12.4311 | 12.1071 | 9.3 | 3233.5602 | 6707.0796 | 11431.0441 | 2333.1975 | 4555.3056 | 8653.2208 | 0.088256 | 0.090569 | 0.10126 | 16.7904 | 9.3689 | 11.032 | 13.0703 | 31.0708 | 132.432 | 143.491 | 136.1832 | 93.5629 | 99.4% | 99.47% | 99.24% | 99.44% | 99.32% | 98.47% | 135.9675 | 132.4955 | 118.5058 |  |  |  | 30 | 26 | 17 |  |  |  |  | 120.1075 | 12 | 25 | 58 | 25 | 98.57% | 0.091077 | 0.09065 | 42.938 | 37.1914 | 129.3058 | 24.873 | 98.57% | 3856.3327 | 99.36% | 99.25% | 84.97% | 17.9148 |  | 99.35% | 1.0187 | 168.1912
2022-03-11 | 178.5391 | 161.9127 | 180 | 167.9121 | 135.1193 | 14.1911 | 14.1911 | 3470.4654 | 1130 | 434 | 611.3777 | 24.6977 | 14 | 24 | 66 | 9561.3819 | 369.2474 |  |  | 24.4753 | 1.018 | 23.7589 | 4081.8431 | 1906.4654 | 2175.3777 | 1045.3777 | 18.0873 | 12.0879 | 13.2377 | 12.5701 | 12.1071 | 9.3 | 3263.0438 | 6764.285 | 11519.2106 | 2348.1076 | 4595.6611 | 8723.805 | 0.088643 | 0.090029 | 0.10068 | 16.8564 | 9.511 | 11.0976 | 13.1235 | 30.7768 | 131.2702 | 144.3643 | 136.9067 | 94.0356 | 99.4% | 99.48% | 99.24% | 99.44% | 99.33% | 98.5% | 135.375 | 133.2909 | 119.1864 |  |  |  | 30 | 26 | 17 |  |  |  |  | 120.9285 | 12 | 25 | 58 | 25 | 98.59% | 0.091013 | 0.0906 | 43.4129 | 37.465 | 130.1074 | 24.7676 | 98.59% | 3877.2363 | 99.36% | 99.25% | 85.02% | 18.0873 |  | 99.35% | 1.018 | 169.1006
2022-03-10 | 178.0147 | 162.923 | 181 | 168.924 | 134.46 | 14.1906 | 14.1906 | 3471.2768 | 1130 | 434 | 614.3875 | 25.2223 | 14 | 24 | 66 | 9596.4019 | 368.6908 |  |  | 24.4112 | 1.0203 | 23.7566 | 4085.6644 | 1907.2768 | 2178.3875 | 1048.3875 | 18.077 | 12.076 | 13.3102 | 12.5755 | 12.1071 | 9.3 | 3270.2641 | 6769.236 | 11504.3651 | 2353.8684 | 4602.8356 | 8722.1487 | 0.088743 | 0.089591 | 0.1007 | 16.8192 | 9.4751 | 11.0978 | 13.1257 | 30.7961 | 131.5827 | 144.5789 | 137.8773 | 94.2207 | 99.41% | 99.48% | 99.24% | 99.44% | 99.33% | 98.49% | 135.2225 | 133.9425 | 119.1601 |  |  |  | 30 | 25.3125 | 17 |  |  |  |  | 120.289 | 12 | 24.3125 | 60.0625 | 25 | 98.56% | 0.090928 | 0.090514 | 43.4631 | 37.3921 | 129.5417 | 25.3227 | 98.56% | 3882.1725 | 99.35% | 99.25% | 84.96% | 18.077 |  | 99.34% | 1.0203 | 169.5839
2022-03-09 | 178.6293 | 163.8609 | 182 | 169.8821 | 135.1865 | 14.0227 | 14.0227 | 3469.9027 | 1130 | 434 | 612.6962 | 25.0558 | 14 | 24 | 66 | 9689.5887 | 368.9698 |  |  | 24.2787 | 1.0249 | 23.7605 | 4082.5989 | 1905.9027 | 2176.6962 | 1046.6962 | 18.1391 | 12.1179 | 13.2848 | 12.5664 | 12.1071 | 9.3 | 3296.8511 | 6830.1799 | 11621.5496 | 2372.9317 | 4642.0237 | 8805.3781 | 0.088561 | 0.089381 | 0.10053 | 16.8962 | 9.523 | 11.1105 | 13.0698 | 30.6746 | 130.9301 | 145.4277 | 138.8282 | 94.8146 | 99.41% | 99.48% | 99.25% | 99.45% | 99.34% | 98.51% | 135.4998 | 134.2574 | 119.3699 |  |  |  | 30 | 25 | 17 |  |  |  |  | 121.1617 | 12 | 24 | 61 | 25 | 98.58% | 0.090738 | 0.090325 | 43.5419 | 37.5298 | 130.0988 | 25.0387 | 98.58% | 3916.4204 | 99.36% | 99.26% | 84.99% | 18.1391 |  | 99.34% | 1.0249 | 170.4341
2022-03-08 | 178.1286 | 164.7827 | 183 | 170.7374 | 134.3537 | 14.0185 | 14.0185 | 3471.87 | 1130 | 434 | 612.9041 | 23.3025 | 14 | 24 | 66 | 9307.1461 | 368.816 |  |  | 24.1373 | 1.0299 | 23.755 | 4084.7741 | 1907.87 | 2176.9041 | 1046.9041 | 18.2173 | 12.2626 | 13.4863 | 12.5794 | 12.1071 | 9.3 | 3178.3957 | 6583.1651 | 11197.9971 | 2287.2997 | 4474.7559 | 8485.8047 | 0.08869 | 0.088684 | 0.099325 | 16.9593 | 9.6348 | 11.2748 | 13.6389 | 31.9755 | 136.5192 | 146.0707 | 140.5965 | 96.4281 | 99.39% | 99.46% | 99.22% | 99.4% | 99.29% | 98.39% | 135.303 | 135.3118 | 120.8158 |  |  |  | 30 | 25 | 17 |  |  |  |  | 120.3172 | 12 | 24 | 61 | 25 | 98.63% | 0.09039 | 0.090017 | 43.9661 | 37.8689 | 130.3502 | 24.2956 | 98.63% | 3774.0998 | 99.38% | 99.2% | 85% | 18.2173 |  | 99.36% | 1.0299 | 170.8536
2022-03-07 | 208.8319 | 159.1572 | 184 | 166.652 | 147.5329 | 14.7969 | 14.7969 | 3470.5167 | 1130 | 434 | 612.9226 | 21.2201 | 14 | 24 | 66 | 8592.054 | 434.5113 |  |  | 23.9684 | 1.0358 | 23.7588 | 4083.4393 | 1906.5167 | 2176.9226 | 1046.9226 | 24.8428 | 17.348 | 19.2189 | 12.5704 | 12.1071 | 9.3 | 2950.8051 | 6109.8638 | 10389.4206 | 2124.2534 | 4153.7675 | 7874.5064 | 0.082075 | 0.089655 | 0.093297 | 23.1347 | 13.6302 | 16.0668 | 14.7604 | 34.6461 | 147.9702 | 158.6464 | 139.8803 | 103.253 | 99.34% | 99.42% | 99.16% | 99.31% | 99.17% | 98.12% | 146.2082 | 133.8465 | 128.621 | [10 empty] | 132.6973 |  |  |  |  | 98.66% | 0.086296 | 0.085946 | 61.4097 | 52.8317 | 157.5338 | 23.9577 | 98.66% | 3504.1519 | 99.39% | 99.07% | 84.99% | 24.8428 |  | 99.37% | 1.0358 | 177.8078
2022-03-06 | 176.9886 | 158.7288 | 158.7288 | 146.3667 | 132.9918 | 13.9952 | 13.9952 | 3470.5011 | 1054.8636 | 358.6536 | 611.6246 | 21.7208 | 10.426 | 20.852 | 52.9988 | 8947.0239 | 365.529 |  |  | 23.8864 | 1.0387 | 17.9946 | 4082.1258 | 2056.984 | 2025.1418 | 970.2783 | 18.2597 | 12.3621 | 13.4515 | 13.5625 | 11.3021 | 7.6854 | 3292.9508 | 6850.2992 | 10836.2019 | 2276.628 | 4644.9486 | 8540.7144 | 0.098841 | 0.1017 | 0.0959 | 17.6476 | 10.8447 | 12.0866 | 11.0972 | 25.1994 | 90.7884 | 142.5325 | 115.4321 | 83.2455 | 99.54% | 99.55% | 99.38% | 99.51% | 99.46% | 98.94% | 121.4075 | 117.9885 | 125.1309 |  |  |  | 30 | 25 | 17 | 2340 | 1200 | 408 | 3948 | 119.003 | 12 | 24 | 61 | 25 | 98.67% | 0.099287 | 0.099407 | 44.0733 | 40.579 | 130.0193 | 23.6492 | 98.67% | 3643.8347 | 99.4% | 99.4% | 85.02% |  |  | 99.38% | 1.0387
2022-03-05 | 177.9046 | 159.7686 | 159.7686 | 147.5308 | 134.2505 | 13.991 | 13.991 | 3469.6608 | 1054.6081 | 358.5668 | 612.8905 | 22.5962 | 10.8462 | 21.6924 | 55.1348 | 9421.9168 | 367.8022 |  |  | 23.8996 | 1.0383 | 18.7199 | 4082.5513 | 2056.4859 | 2026.0654 | 971.4573 | 18.136 | 12.2378 | 13.4163 | 13.5592 | 11.2994 | 7.6836 | 3458.6697 | 7189.8316 | 11363.93 | 2391.6255 | 4877.1538 | 8960.6215 | 0.098489 | 0.10168 | 0.096849 | 17.5222 | 10.7244 | 12.0271 | 10.9817 | 24.9496 | 89.9592 | 142.9417 | 115.3814 | 82.3722 | 99.55% | 99.56% | 99.38% | 99.54% | 99.49% | 99% | 121.8406 | 118.0185 | 123.9042 |  |  |  | 30 | 25 | 17 | 2340 | 1200 | 408 | 3948 | 120.249 | 12 | 24 | 61 | 25 | 98.69% | 0.099248 | 0.099289 | 43.7901 | 40.2737 | 129.9139 | 23.4149 | 98.69% | 3825.968 | 99.41% | 99.44% | 84.99% |  |  | 99.39% | 1.0383
2022-03-04 | 176.2245 | 158.3218 | 158.3218 | 146.3785 | 132.7834 | 14.2047 | 14.2047 | 3465.5606 | 1053.3619 | 358.143 | 612.975 | 23.7003 | 11.3761 | 22.7523 | 57.8286 | 9451.5241 | 363.7284 |  |  | 24.3316 | 1.023 | 19.6345 | 4078.5356 | 2054.0557 | 2024.4799 | 971.118 | 17.9027 | 11.9432 | 13.1834 | 13.5432 | 11.286 | 7.6745 | 3473.5924 | 7216.6838 | 11399.3898 | 2402.4006 | 4896.9534 | 8991.5433 | 0.098186 | 0.10148 | 0.097281 | 17.3207 | 10.4763 | 11.8211 | 11.285 | 25.65 | 92.5409 | 141.1133 | 113.7745 | 80.7077 | 99.53% | 99.54% | 99.36% | 99.53% | 99.48% | 98.97% | 122.2175 | 118.2474 | 123.3539 |  |  |  | 30 | 25 | 17 | 2340 | 1200 | 408 | 3948 | 118.5922 | 12 | 24 | 61 | 25 | 98.63% | 0.099096 | 0.099094 | 43.0293 | 39.6181 | 128.1121 | 24.0718 | 98.63% | 3841.5682 | 99.38% | 99.42% | 84.97% |  |  | 99.37% | 1.023
2022-03-03 | 175.6852 | 157.8216 | 157.8216 | 145.7677 | 132.492 | 14.1642 | 14.1642 | 3462.2144 | 1052.3448 | 357.7972 | 611.5904 | 23.8715 | 11.4583 | 22.9167 | 58.2465 | 9559.5104 | 361.4912 |  |  | 24.4994 | 1.0172 | 19.7764 | 4073.8048 | 2052.0724 | 2021.7325 | 969.3877 | 17.8635 | 12.0539 | 13.1796 | 13.5301 | 11.2751 | 7.6671 | 3512.0173 | 7299.7042 | 11536.1561 | 2428.6933 | 4952.0748 | 9097.0324 | 0.097954 | 0.10151 | 0.097766 | 17.3145 | 10.5972 | 11.8527 | 11.1685 | 25.3774 | 91.5142 | 140.5031 | 112.9848 | 79.7718 | 99.53% | 99.54% | 99.36% | 99.54% | 99.49% | 98.99% | 122.5063 | 118.2153 | 122.7423 |  |  |  | 30 | 25 | 17 | 2340 | 1200 | 408 | 3948 | 118.3785 | 12 | 24 | 61 | 25 | 98.63% | 0.099062 | 0.099015 | 43.097 | 39.7644 | 127.3361 | 23.816 | 98.63% | 3884.8078 | 99.39% | 99.44% | 84.99% |  |  | 99.38% | 1.0172
2022-03-02 | 175.8858 | 157.9789 | 157.9789 | 146.0415 | 132.6678 | 14.0222 | 14.0222 | 3469.4944 | 1052.2418 | 364.2375 | 613.1392 | 23.9167 | 11.4419 | 22.9633 | 58.163 | 9659.246 | 363.2688 |  |  | 24.7069 | 1.01 | 19.8411 | 4082.6337 | 2053.0152 | 2029.6185 | 977.3768 | 17.9068 | 11.9374 | 13.2358 | 13.5364 | 11.274 | 7.8051 | 3538.3871 | 7323.0849 | 11638.8374 | 2449.2327 | 4979.8702 | 9150.0682 | 0.097157 | 0.10059 | 0.098699 | 17.2854 | 10.4117 | 11.7963 | 10.986 | 25.1062 | 91.8363 | 140.7212 | 113.2035 | 79.8729 | 99.53% | 99.54% | 99.36% | 99.55% | 99.5% | 99% | 123.5111 | 119.297 | 121.5822 |  |  |  | 29.9167 | 24.9167 | 17.25 | 2333.5 | 1196 | 414 | 3943.5 | 118.6412 | 12 | 24.0833 | 61 | 25.0833 | 98.64% | 0.098502 | 0.09836 | 43.08 | 39.4934 | 127.4703 | 23.5282 | 98.64% | 3920.2073 | 99.39% | 99.44% | 84.98% |  |  | 99.38% | 1.01
2022-03-01 | 175.4394 | 157.473 | 157.473 | 145.402 | 131.9667 | 14.0025 | 14.0025 | 3466.2611 | 1025.4578 | 427.2741 | 611.9962 | 23.0619 | 10.644 | 22.1749 | 54.1068 | 9284.2849 | 361.1357 |  |  | 24.5085 | 1.0169 | 19.4128 | 4078.2573 | 2013.5292 | 2064.7281 | 1039.2703 | 17.9664 | 12.0709 | 13.3379 | 13.276 | 10.987 | 9.1559 | 3357.3313 | 6648.1619 | 11251.8981 | 2347.3733 | 4633.7683 | 8549.9749 | 0.095902 | 0.097682 | 0.11326 | 17.2129 | 10.0386 | 11.2374 | 10.5293 | 25.5643 | 107.979 | 140.77 | 114.377 | 82.2025 | 99.55% | 99.52% | 99.37% | 99.55% | 99.45% | 98.74% | 125.1275 | 122.8481 | 105.9488 |  |  |  | 29 | 24 | 20 | 2262 | 1152 | 480 | 3894 | 117.9918 | 12 | 25 | 61 | 26 | 98.65% | 0.099249 | 0.098569 | 43.3753 | 38.4889 | 127.7641 | 23.6143 | 98.65% | 3788.3532 | 99.39% | 99.39% | 84.99% |  |  | 99.38% | 1.0169
2022-02-28 | 175.1769 | 157.1055 | 157.1055 | 144.8126 | 131.1729 | 14.0078 | 14.0078 | 3472.3433 | 1050.8097 | 379.6971 | 613.3265 | 21.8583 | 10.0885 | 21.0176 | 51.283 | 8771.7016 | 362.3533 |  |  | 24.2842 | 1.0247 | 17.9005 | 4085.6698 | 2041.8364 | 2043.8334 | 993.0237 | 18.0714 | 12.2928 | 13.3683 | 13.4627 | 11.2587 | 8.1364 | 3234.1418 | 6634.2441 | 10709.6125 | 2246.2374 | 4533.9204 | 8349.1145 | 0.097871 | 0.10086 | 0.10106 | 17.3706 | 10.564 | 11.7387 | 10.657 | 25.5711 | 93.8517 | 140.9526 | 114.3867 | 82.4958 | 99.55% | 99.54% | 99.39% | 99.53% | 99.44% | 98.88% | 122.6102 | 118.9796 | 118.7368 |  |  |  | 30.5417 | 25.5417 | 18.4583 | 2382.25 | 1226 | 443 | 4051.25 | 117.2081 | 12 | 25 | 61 | 26 | 98.65% | 0.099338 | 0.099124 | 43.7325 | 39.6733 | 128.5088 | 23.7368 | 98.65% | 3605.8853 | 99.39% | 99.39% | 84.99% |  |  | 99.38% | 1.0247
2022-02-27 | 176.891 | 158.8883 | 158.8883 | 146.6174 | 133.1314 | 13.9756 | 13.9756 | 3472.3189 | 1057.4558 | 366.0424 | 612.4213 | 22.1804 | 10.2371 | 21.3273 | 52.0386 | 9151.6081 | 365.5652 |  |  | 24.0858 | 1.0317 | 18.0211 | 4084.7402 | 2048.8206 | 2035.9195 | 978.4637 | 18.0027 | 12.2709 | 13.3794 | 13.5087 | 11.3299 | 7.8438 | 3365.6311 | 6979.9229 | 11120.6986 | 2332.7384 | 4741.0333 | 8731.1757 | 0.097937 | 0.10148 | 0.098084 | 17.3421 | 10.6633 | 11.9202 | 10.5198 | 25.1413 | 88.39 | 142.3016 | 115.1788 | 82.5032 | 99.56% | 99.55% | 99.4% | 99.55% | 99.47% | 98.99% | 122.5274 | 118.2454 | 122.3442 |  |  |  | 31 | 26 | 18 | 2418 | 1248 | 432 | 4098 | 119.1207 | 12 | 25 | 61 | 26 | 98.68% | 0.099096 | 0.099033 | 43.653 | 39.9256 | 129.4655 | 23.3766 | 98.68% | 3740.6635 | 99.41% | 99.43% | 85.01% |  |  | 99.39% | 1.0317
2022-02-26 | 178.4751 | 160.539 | 160.539 | 148.3621 | 134.6895 | 14.1564 | 14.1564 | 3469.3407 | 1056.5488 | 365.7284 | 613.0693 | 22.5343 | 10.4005 | 21.6676 | 52.869 | 9395.8113 | 369.2488 |  |  | 23.9436 | 1.0367 | 18.3087 | 4082.41 | 2047.0634 | 2035.3466 | 978.7978 | 17.9361 | 12.1769 | 13.4193 | 13.4971 | 11.3202 | 7.837 | 3447.7326 | 7145.9481 | 11377.3468 | 2389.9929 | 4855.4187 | 8936.0052 | 0.097542 | 0.10106 | 0.097943 | 17.2902 | 10.5829 | 11.9447 | 10.4735 | 25.0409 | 88.0944 | 143.4527 | 116.1254 | 82.9537 | 99.56% | 99.55% | 99.41% | 99.56% | 99.48% | 99.01% | 123.0244 | 118.7403 | 122.5201 |  |  |  | 31 | 26 | 18 | 2418 | 1248 | 432 | 4098 | 120.5707 | 12 | 25 | 61 | 26 | 98.69% | 0.098732 | 0.098656 | 43.5323 | 39.8178 | 130.3563 | 23.2835 | 98.69% | 3830.8735 | 99.41% | 99.45% | 84.98% |  |  | 99.39% | 1.0367
2022-02-25 | 175.8705 | 158.2598 | 158.2598 | 146.3054 | 133.2998 | 14.0895 | 14.0895 | 3411.6338 | 1022.8587 | 336.7436 | 601.1715 | 22.8936 | 10.5663 | 22.0131 | 53.712 | 9433.3641 | 355.5039 |  |  | 23.7173 | 1.0448 | 18.2569 | 4012.8054 | 2052.0315 | 1960.7739 | 937.9151 | 17.6107 | 11.9544 | 13.1323 | 13.5299 | 10.9592 | 7.2159 | 3528.7938 | 7353.171 | 11441.9314 | 2418.9909 | 4981.2706 | 9098.1914 | 0.1003 | 0.10097 | 0.093664 | 17.5949 | 11.0164 | 12.2956 | 10.6205 | 24.1937 | 81.5675 | 140.9335 | 113.3968 | 80.4907 | 99.56% | 99.56% | 99.41% | 99.56% | 99.51% | 99.1% | 119.6396 | 118.8438 | 128.1173 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 119.2451 | 12 | 25 | 61 | 26 | 98.68% | 0.099454 | 0.099847 | 42.6973 | 40.9068 | 127.9337 | 23.3474 | 98.68% | 3846.4678 | 99.4% | 99.47% | 85.02% |  |  | 99.39% | 1.0448
2022-02-24 | 175.3608 | 157.8167 | 157.8167 | 145.9866 | 132.8465 | 13.9548 | 13.9548 | 3410.2501 | 1022.4439 | 336.607 | 602.3012 | 23.053 | 10.6399 | 22.1664 | 54.0859 | 9397.3461 | 354.2439 |  |  | 23.6091 | 1.0487 | 18.384 | 4012.5513 | 2051.1992 | 1961.3521 | 938.9082 | 17.5441 | 11.8301 | 12.9791 | 13.5244 | 10.9548 | 7.213 | 3523.4046 | 7336.1516 | 11405.8672 | 2415.813 | 4971.9395 | 9073.6025 | 0.10087 | 0.10149 | 0.094122 | 17.5269 | 10.893 | 12.1271 | 10.744 | 24.4886 | 82.6306 | 140.6081 | 113.198 | 80.3642 | 99.56% | 99.55% | 99.4% | 99.56% | 99.51% | 99.09% | 118.9695 | 118.244 | 127.4938 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 118.8799 | 12 | 25 | 61 | 26 | 98.67% | 0.099985 | 0.10039 | 42.3533 | 40.547 | 127.687 | 23.6317 | 98.67% | 3839.3317 | 99.4% | 99.47% | 84.99% |  |  | 99.38% | 1.0487
2022-02-23 | 177.6487 | 159.7176 | 159.7176 | 147.5862 | 133.9948 | 14.0344 | 14.0344 | 3467.5572 | 1039.6254 | 342.2635 | 611.3332 | 23.0026 | 10.6166 | 22.1179 | 53.9677 | 9397.6865 | 366.2619 |  |  | 23.5773 | 1.0498 | 18.3438 | 4078.8904 | 2085.6683 | 1993.2221 | 953.5967 | 17.9311 | 12.1313 | 13.3372 | 13.7517 | 11.1388 | 7.3342 | 3521.8036 | 7337.2135 | 11414.8417 | 2414.3333 | 4970.989 | 9077.6147 | 0.10122 | 0.1018 | 0.094314 | 17.4807 | 10.9067 | 12.1795 | 10.9193 | 24.8777 | 83.8902 | 142.6301 | 114.8731 | 81.6378 | 99.56% | 99.56% | 99.41% | 99.55% | 99.5% | 99.08% | 118.5561 | 117.8816 | 127.2347 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 120.0124 | 12 | 25 | 61 | 26 | 98.67% | 0.1003 | 0.10071 | 43.3997 | 40.5669 | 129.6385 | 24.0074 | 98.67% | 3838.5527 | 99.4% | 99.46% | 85.01% |  |  | 99.37% | 1.0498
2022-02-22 | 175.7148 | 157.8221 | 157.8221 | 145.6313 | 132.148 | 13.996 | 13.996 | 3473.3021 | 1041.3478 | 342.8306 | 613.4719 | 22.8696 | 10.5552 | 21.99 | 53.6556 | 9227.1957 | 364.5461 |  |  | 23.8784 | 1.039 | 18.2377 | 4086.774 | 2089.1238 | 1997.6503 | 956.3025 | 17.8928 | 12.1907 | 13.3342 | 13.7744 | 11.1573 | 7.3464 | 3461.0468 | 7205.9438 | 11202.9044 | 2373.1107 | 4883.8347 | 8912.3645 | 0.10153 | 0.10221 | 0.094703 | 17.3904 | 10.9204 | 12.1204 | 10.9494 | 24.9578 | 84.218 | 140.9597 | 113.4215 | 80.6001 | 99.56% | 99.55% | 99.4% | 99.54% | 99.49% | 99.06% | 118.1881 | 117.4057 | 126.7114 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 118.1054 | 12 | 25 | 61 | 26 | 98.65% | 0.10066 | 0.10106 | 43.4177 | 40.4312 | 128.1426 | 24.0843 | 98.65% | 3771.317 | 99.39% | 99.45% | 84.99% |  |  | 99.37% | 1.039
2022-02-21 | 173.8193 | 155.8736 | 155.8736 | 143.6235 | 130.1524 | 14.122 | 14.122 | 3469.3768 | 1040.1709 | 342.4431 | 613.5896 | 22.7879 | 10.5175 | 21.9114 | 53.4639 | 8920.8816 | 360.55 |  |  | 24.0018 | 1.0346 | 18.1726 | 4082.9664 | 2086.7627 | 1996.2037 | 956.0327 | 17.9457 | 12.2502 | 13.4173 | 13.7589 | 11.1447 | 7.3381 | 3356.4899 | 6984.5367 | 10852.7543 | 2301.7977 | 4735.1883 | 8636.3389 | 0.10222 | 0.1029 | 0.09508 | 17.4644 | 10.9832 | 12.1977 | 11.1881 | 25.5122 | 86.1363 | 139.268 | 112.0602 | 79.8515 | 99.54% | 99.54% | 99.38% | 99.51% | 99.46% | 99% | 117.3973 | 116.6199 | 126.2092 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 116.0091 | 12 | 25 | 61 | 26 | 98.62% | 0.10129 | 0.10172 | 43.6131 | 40.6453 | 126.7608 | 24.6187 | 98.62% | 3656.6123 | 99.38% | 99.42% | 84.97% |  |  | 99.36% | 1.0346
2022-02-20 | 172.4796 | 154.9703 | 154.9703 | 143.1415 | 129.8688 | 14.233 | 14.233 | 3436.1929 | 1030.2219 | 339.1677 | 605.8616 | 23.7363 | 10.9552 | 22.8234 | 55.689 | 9292.9916 | 353.9041 |  |  | 24.3573 | 1.0221 | 18.9289 | 4042.0545 | 2066.8033 | 1975.2512 | 945.0293 | 17.5093 | 11.8288 | 13.0729 | 13.6273 | 11.0381 | 7.2679 | 3475.4335 | 7239.29 | 11260.7458 | 2382.7558 | 4905.1458 | 8955.8181 | 0.1012 | 0.10219 | 0.095521 | 17.3033 | 10.7799 | 12.1006 | 11.0154 | 25.1009 | 84.6576 | 137.6329 | 110.4113 | 77.7715 | 99.54% | 99.53% | 99.38% | 99.54% | 99.49% | 99.05% | 118.572 | 117.4324 | 125.6265 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 115.6825 | 12 | 25 | 61 | 26 | 98.61% | 0.10061 | 0.10094 | 42.411 | 40.1838 | 124.8195 | 24.2222 | 98.61% | 3787.7969 | 99.37% | 99.44% | 85.01% |  |  | 99.37% | 1.0221
2022-02-19 | 174.5988 | 156.9598 | 156.9598 | 144.9679 | 131.5782 | 14.3354 | 14.3354 | 3452.2035 | 1035.0221 | 340.748 | 610.1156 | 23.7664 | 10.9691 | 22.8523 | 55.7596 | 9512.0226 | 362.4328 |  |  | 24.3094 | 1.0238 | 18.9529 | 4062.3191 | 2076.4333 | 1985.8858 | 950.8636 | 17.639 | 11.9919 | 13.225 | 13.6908 | 11.0895 | 7.3017 | 3554.2551 | 7398.2133 | 11498.9553 | 2437.2009 | 5014.826 | 9149.1084 | 0.10061 | 0.10167 | 0.095267 | 17.298 | 10.8368 | 12.1228 | 10.851 | 24.7381 | 83.4974 | 139.3128 | 111.6686 | 78.4709 | 99.55% | 99.54% | 99.39% | 99.55% | 99.51% | 99.09% | 119.2671 | 118.0255 | 125.9621 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 117.3467 | 12 | 25 | 61 | 26 | 98.64% | 0.1001 | 0.1004 | 42.8559 | 40.2576 | 126.2168 | 23.872 | 98.64% | 3872.5069 | 99.39% | 99.46% | 84.98% |  |  | 99.38% | 1.0238
2022-02-18 | 176.1342 | 158.362 | 158.362 | 146.3343 | 133.0263 | 14.1278 | 14.1278 | 3469.5925 | 1040.2356 | 342.4644 | 611.3405 | 24.4279 | 11.2744 | 23.4884 | 57.3116 | 9753.895 | 369.502 |  |  | 24.2155 | 1.0271 | 19.4804 | 4080.933 | 2086.8925 | 1994.0405 | 953.8049 | 17.7721 | 12.0278 | 13.2057 | 13.7597 | 11.1454 | 7.3385 | 3628.6638 | 7560.5284 | 11763.7254 | 2487.5998 | 5122.0252 | 9354.4391 | 0.10042 | 0.10155 | 0.09533 | 17.3135 | 10.8079 | 12.0568 | 11.0174 | 25.1002 | 84.6314 | 140.7386 | 112.7276 | 79.0668 | 99.55% | 99.54% | 99.39% | 99.56% | 99.51% | 99.1% | 119.5001 | 118.1681 | 125.8782 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 118.9185 | 12 | 25 | 61 | 26 | 98.63% | 0.099966 | 0.10026 | 43.0056 | 40.1782 | 127.4231 | 24.2218 | 98.63% | 3955.2278 | 99.38% | 99.47% | 85.02% |  |  | 99.37% | 1.0271
2022-02-17 | 174.9079 | 157.4163 | 157.4163 | 145.5598 | 132.1532 | 14.0202 | 14.0202 | 3452.8879 | 1035.2273 | 340.8156 | 608.6299 | 24.2221 | 11.1794 | 23.2905 | 56.8288 | 9663.5946 | 366.0287 |  |  | 24.1488 | 1.0295 | 19.3163 | 4061.5177 | 2076.845 | 1984.6728 | 949.4455 | 17.4916 | 11.8565 | 13.181 | 13.6935 | 11.0917 | 7.3032 | 3592.2685 | 7483.7016 | 11642.5411 | 2462.7385 | 5070.3553 | 9258.7768 | 0.10078 | 0.10174 | 0.095378 | 17.162 | 10.7289 | 12.1163 | 11.0068 | 25.0785 | 84.5701 | 139.8841 | 112.2326 | 78.8266 | 99.55% | 99.54% | 99.39% | 99.55% | 99.51% | 99.09% | 119.077 | 117.9487 | 125.8153 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 118.0905 | 12 | 25 | 61 | 26 | 98.62% | 0.10022 | 0.10053 | 42.529 | 40.0071 | 126.6638 | 24.2008 | 98.62% | 3915.3405 | 99.38% | 99.46% | 85.01% |  |  | 99.37% | 1.0295
2022-02-16 | 175.7389 | 157.9896 | 157.9896 | 145.9105 | 132.5671 | 14.1093 | 14.1093 | 3469.2752 | 1040.1405 | 342.4331 | 612.7171 | 24.5174 | 11.3157 | 23.5744 | 57.5216 | 9790.2141 | 368.2297 |  |  | 24.0562 | 1.0327 | 19.5518 | 4081.9923 | 2086.7017 | 1995.2907 | 955.1502 | 17.7493 | 12.0791 | 13.2303 | 13.7585 | 11.1444 | 7.3379 | 3622.6071 | 7541.8857 | 11724.7197 | 2483.9782 | 5111.6825 | 9327.6883 | 0.10121 | 0.10239 | 0.096193 | 17.2814 | 10.8397 | 12.0479 | 11.1333 | 25.3788 | 85.6427 | 140.3916 | 112.4002 | 78.7786 | 99.54% | 99.54% | 99.38% | 99.55% | 99.5% | 99.08% | 118.5684 | 117.1952 | 124.7492 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 118.4959 | 12 | 25 | 61 | 26 | 98.62% | 0.10078 | 0.10107 | 43.0587 | 40.169 | 127.0804 | 24.4902 | 98.62% | 3947.3082 | 99.38% | 99.46% | 84.99% |  |  | 99.36% | 1.0327
2022-02-15 | 173.3333 | 155.7192 | 155.7192 | 143.7372 | 130.3497 | 14.0217 | 14.0217 | 3456.3393 | 1036.2621 | 341.1563 | 610.8731 | 24.0235 | 11.3052 | 23.5524 | 56.2903 | 9600.0918 | 361.3923 |  |  | 24.0877 | 1.0316 | 19.4173 | 4067.2124 | 2078.9209 | 1988.2915 | 952.0294 | 17.6142 | 11.9819 | 13.1307 | 13.7072 | 11.1028 | 7.3105 | 3553.0986 | 7394.9285 | 11493.3612 | 2436.5528 | 5012.9328 | 9144.866 | 0.10219 | 0.10341 | 0.097212 | 17.2424 | 10.8081 | 12.0142 | 11.285 | 25.7304 | 85.0745 | 138.3783 | 110.7596 | 77.5788 | 99.54% | 99.53% | 99.38% | 99.54% | 99.49% | 99.07% | 117.4318 | 116.0417 | 123.4419 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 116.396 | 12 | 25 | 59.75 | 25.5 | 98.62% | 0.10178 | 0.10206 | 42.7268 | 40.0647 | 125.3027 | 24.3516 | 98.62% | 3871.1307 | 99.38% | 99.45% | 84.98% |  |  | 99.36% | 1.0316
2022-02-14 | 170.8474 | 153.0998 | 153.0998 | 141.0359 | 127.5904 | 14.1898 | 14.1898 | 3469.4278 | 1040.1862 | 342.4481 | 612.9579 | 22.937 | 11.4685 | 23.8927 | 53.5196 | 8998.2282 | 357.6352 |  |  | 24.5528 | 1.0153 | 19.3441 | 4082.3857 | 2086.7934 | 1995.5923 | 955.4061 | 17.7476 | 12.0639 | 13.3301 | 13.7591 | 11.1449 | 7.3382 | 3354.9281 | 6981.5507 | 10852.1124 | 2300.8988 | 4733.0636 | 8634.1206 | 0.10247 | 0.1035 | 0.096487 | 17.2768 | 10.823 | 12.133 | 11.977 | 27.3127 | 84.6405 | 136.3367 | 109.3322 | 77.2203 | 99.5% | 99.5% | 99.38% | 99.48% | 99.42% | 99.02% | 117.1091 | 115.942 | 124.3686 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 113.3736 | 12 | 25 | 56 | 24 | 98.61% | 0.10184 | 0.10219 | 43.1416 | 40.2328 | 123.8395 | 24.3272 | 98.61% | 3655.2156 | 99.37% | 99.39% | 84.99% |  |  | 99.36% | 1.0153
2022-02-13 | 169.2226 | 151.8133 | 151.8133 | 139.9997 | 126.9573 | 14.3213 | 14.3213 | 3434.4431 | 1029.6973 | 338.995 | 605.7041 | 23.3621 | 11.6811 | 24.3355 | 54.5116 | 9201.1197 | 348.7279 |  |  | 24.7801 | 1.0075 | 19.7026 | 4040.1471 | 2065.7508 | 1974.3963 | 944.6991 | 17.4093 | 11.8136 | 13.0053 | 13.6203 | 11.0325 | 7.2642 | 3419.3059 | 7119.7349 | 11073.9355 | 2344.6864 | 4825.142 | 8807.6048 | 0.102 | 0.10332 | 0.097076 | 17.2163 | 10.7727 | 12.0437 | 11.7591 | 26.8046 | 83.0137 | 134.5317 | 107.5812 | 75.3917 | 99.5% | 99.5% | 99.38% | 99.5% | 99.44% | 99.06% | 117.6433 | 116.1433 | 123.614 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 112.5959 | 12 | 25 | 56 | 24 | 98.61% | 0.10164 | 0.10191 | 42.2283 | 40.0327 | 121.8831 | 23.8748 | 98.61% | 3726.2832 | 99.37% | 99.41% | 85.01% |  |  | 99.38% | 1.0075
2022-02-12 | 168.2974 | 151.2672 | 151.2672 | 139.7042 | 126.9949 | 14.0996 | 14.0996 | 3392.4517 | 1017.1076 | 334.8503 | 599.8407 | 24.423 | 12.2115 | 25.4406 | 56.9869 | 9626.4575 | 341.3684 |  |  | 24.7851 | 1.0073 | 20.5973 | 3992.2924 | 2040.4938 | 1951.7986 | 934.691 | 17.0302 | 11.563 | 12.7074 | 13.4538 | 10.8976 | 7.1754 | 3559.6612 | 7405.5129 | 11507.6951 | 2441.4987 | 5021.2759 | 9157.1747 | 0.10149 | 0.10317 | 0.098008 | 17.1417 | 10.7233 | 11.9508 | 11.6593 | 26.5934 | 82.4356 | 133.5362 | 106.4069 | 73.749 | 99.5% | 99.49% | 99.38% | 99.52% | 99.47% | 99.1% | 118.2386 | 116.3175 | 122.4384 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 112.9035 | 12 | 25 | 56 | 24 | 98.6% | 0.10147 | 0.10165 | 41.3006 | 39.8158 | 120.4977 | 23.6863 | 98.6% | 3877.8219 | 99.37% | 99.44% | 84.98% |  |  | 99.38% | 1.0073
2022-02-11 | 173.3119 | 155.7695 | 155.7695 | 143.9336 | 130.5863 | 14.2847 | 14.2847 | 3471.5223 | 1040.8142 | 342.6549 | 613.7271 | 24.8486 | 12.4243 | 25.884 | 57.9802 | 10050.1905 | 362.2079 |  |  | 24.6829 | 1.0109 | 20.9563 | 4085.2495 | 2088.0532 | 1997.1962 | 956.382 | 17.5424 | 11.8359 | 13.0815 | 13.7674 | 11.1516 | 7.3426 | 3663.2177 | 7621.6657 | 11844.6072 | 2512.4354 | 5167.566 | 9424.8329 | 0.10103 | 0.10261 | 0.097481 | 17.0582 | 10.6045 | 11.8869 | 11.8374 | 26.9976 | 83.6809 | 137.756 | 109.8585 | 76.141 | 99.51% | 99.5% | 99.38% | 99.53% | 99.48% | 99.11% | 118.7822 | 116.9471 | 123.1008 |  |  |  | 30 | 24.3 | 16 | 2340 | 1166.4 | 384 | 3890.4 | 116.3108 | 12 | 25 | 56 | 24 | 98.62% | 0.10097 | 0.10115 | 42.4598 | 39.5496 | 124.3578 | 24.0465 | 98.62% | 3990.7679 | 99.38% | 99.45% | 84.98% |  |  | 99.37% | 1.0109
2022-02-10 | 174.557 | 156.9032 | 156.9032 | 144.9795 | 131.7723 | 14.1752 | 14.1752 | 3469.7598 | 1035.8128 | 355.9275 | 613.2686 | 24.7031 | 11.5281 | 24.7031 | 59.2874 | 10085.8427 | 363.556 |  |  | 24.5984 | 1.0138 | 20.3603 | 4083.0284 | 2078.0195 | 2005.0089 | 969.1961 | 17.6538 | 11.9237 | 13.0586 | 13.7012 | 11.098 | 7.627 | 3610.6846 | 7443.1448 | 11728.5713 | 2482.2394 | 5072.7622 | 9263.2919 | 0.099783 | 0.10088 | 0.0989 | 17.1429 | 10.5723 | 11.7274 | 11.0956 | 26.1966 | 90.6927 | 139.2013 | 111.5258 | 78.1807 | 99.54% | 99.51% | 99.36% | 99.55% | 99.48% | 99.02% | 120.2613 | 118.9523 | 121.3352 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 117.5693 | 14 | 30 | 72 | 30 | 98.61% | 0.099993 | 0.10002 | 42.6361 | 39.4425 | 125.9114 | 24.2025 | 98.61% | 3951.1766 | 99.37% | 99.45% | 84.98% |  |  | 99.37% | 1.0138
2022-02-09 | 172.835 | 155.2933 | 155.2933 | 143.4638 | 130.3757 | 14.1271 | 14.1271 | 3450.4843 | 1030.0586 | 353.9502 | 610.0658 | 24.611 | 11.4851 | 24.611 | 59.0664 | 9900.2231 | 357.0347 |  |  | 24.4421 | 1.0192 | 20.2844 | 4060.5501 | 2066.4756 | 1994.0745 | 964.016 | 17.5418 | 11.8295 | 13.0852 | 13.6251 | 11.0363 | 7.5846 | 3561.6681 | 7341.0412 | 11565.9239 | 2448.6577 | 5003.5794 | 9135.5783 | 0.10081 | 0.10193 | 0.09986 | 17.1753 | 10.5745 | 11.8452 | 11.2032 | 26.4535 | 91.596 | 137.7512 | 110.3566 | 77.4101 | 99.53% | 99.51% | 99.35% | 99.54% | 99.47% | 99% | 119.0369 | 117.7333 | 120.1679 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 116.2094 | 14 | 30 | 72 | 30 | 98.6% | 0.10101 | 0.10104 | 42.4564 | 39.595 | 124.6062 | 24.4397 | 98.6% | 3897.3111 | 99.37% | 99.43% | 84.98% |  |  | 99.36% | 1.0192
2022-02-08 | 171.057 | 153.815 | 153.815 | 142.0475 | 128.896 | 14.3106 | 14.3106 | 3418.8611 | 1020.6182 | 350.7063 | 604.4929 | 23.8632 | 11.1361 | 23.8632 | 57.2716 | 9486.3693 | 349.7379 |  |  | 24.1261 | 1.0303 | 19.6681 | 4023.354 | 2047.5366 | 1975.8174 | 955.1992 | 17.242 | 11.7675 | 12.9491 | 13.5002 | 10.9352 | 7.5151 | 3427.0322 | 7063.2749 | 11127.9203 | 2356.135 | 4814.3577 | 8789.7731 | 0.10197 | 0.10273 | 0.099905 | 17.1164 | 10.6652 | 11.8846 | 11.3073 | 26.7003 | 92.4539 | 136.4004 | 109.6682 | 77.4987 | 99.53% | 99.5% | 99.35% | 99.52% | 99.45% | 98.95% | 117.682 | 116.8127 | 120.1139 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 114.5374 | 14 | 30 | 72 | 30 | 98.59% | 0.10188 | 0.10198 | 41.9586 | 39.6662 | 123.6565 | 24.6676 | 98.59% | 3749.9396 | 99.36% | 99.4% | 84.98% |  |  | 99.35% | 1.0303
2022-02-07 | 171.063 | 153.1173 | 153.1173 | 140.9439 | 127.2969 | 14.0977 | 14.0977 | 3471.0133 | 1036.187 | 356.056 | 613.5879 | 21.7486 | 10.1493 | 21.7486 | 52.1966 | 8727.1743 | 354.9907 |  |  | 23.98 | 1.0354 | 17.9252 | 4084.6012 | 2078.7702 | 2005.8309 | 969.6439 | 17.9457 | 12.1734 | 13.3428 | 13.7062 | 11.102 | 7.6298 | 3173.8543 | 6542.2772 | 10308.3758 | 2181.9677 | 4458.933 | 8141.8891 | 0.10349 | 0.1038 | 0.099279 | 17.416 | 10.7868 | 11.9739 | 11.3543 | 26.8085 | 92.8168 | 137.1334 | 110.747 | 79.5742 | 99.53% | 99.51% | 99.36% | 99.48% | 99.4% | 98.86% | 115.9555 | 115.6099 | 120.872 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 113.237 | 14 | 30 | 72 | 30 | 98.61% | 0.10291 | 0.10315 | 43.4619 | 40.1767 | 125.1697 | 24.7678 | 98.61% | 3473.0685 | 99.37% | 99.35% | 84.98% |  |  | 99.35% | 1.0354
2022-02-06 | 171.509 | 153.8601 | 153.8601 | 141.7837 | 128.5233 | 13.9879 | 13.9879 | 3454.0282 | 1031.1165 | 354.3137 | 607.8913 | 22.6671 | 10.578 | 22.6671 | 54.401 | 9270.7215 | 353.1253 |  |  | 23.8279 | 1.0408 | 18.6823 | 4061.9194 | 2068.598 | 1993.3215 | 962.205 | 17.6489 | 12.0764 | 13.2614 | 13.6391 | 11.0477 | 7.5924 | 3345.5147 | 6906.3391 | 10900.0398 | 2299.056 | 4703.162 | 8601.5434 | 0.10343 | 0.10413 | 0.10076 | 17.2776 | 10.8093 | 12.0505 | 11.2346 | 26.4979 | 91.5954 | 137.2543 | 110.4316 | 78.4299 | 99.54% | 99.52% | 99.37% | 99.51% | 99.44% | 98.94% | 116.0222 | 115.2453 | 119.0972 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 114.5385 | 14 | 30 | 72 | 30 | 98.62% | 0.10322 | 0.10336 | 42.9867 | 40.1374 | 124.6991 | 24.4812 | 98.62% | 3663.2519 | 99.38% | 99.4% | 85.03% |  |  | 99.36% | 1.0408
2022-02-05 | 170.3605 | 153.2768 | 153.2768 | 141.6347 | 128.7561 | 14.056 | 14.056 | 3392.1297 | 1012.6382 | 347.9642 | 599.788 | 23.912 | 11.1589 | 23.912 | 57.3888 | 9740.7142 | 343.5145 |  |  | 23.7129 | 1.0449 | 19.7083 | 3991.9177 | 2031.5273 | 1960.3904 | 947.7522 | 17.0837 | 11.6421 | 12.8184 | 13.3947 | 10.8497 | 7.4564 | 3512.2212 | 7239.3508 | 11405.9322 | 2414.6105 | 4934.1821 | 9009.1108 | 0.10311 | 0.10416 | 0.10201 | 17.1599 | 10.6763 | 11.9035 | 11.126 | 26.2703 | 90.9593 | 135.7454 | 108.8484 | 76.3808 | 99.54% | 99.52% | 99.36% | 99.54% | 99.47% | 98.99% | 116.3809 | 115.2109 | 117.6375 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 114.7264 | 14 | 30 | 72 | 30 | 98.62% | 0.10327 | 0.10331 | 41.5441 | 39.7397 | 122.7582 | 24.2707 | 98.62% | 3843.2305 | 99.38% | 99.43% | 84.97% |  |  | 99.36% | 1.0449
2022-02-04 | 174.4699 | 156.5927 | 156.5927 | 144.5271 | 131.2584 | 14.3976 | 14.3976 | 3474.0774 | 1037.1017 | 356.3704 | 613.3057 | 23.9458 | 11.1747 | 23.9458 | 57.47 | 9743.4663 | 362.6757 |  |  | 23.6768 | 1.0462 | 19.7362 | 4087.3831 | 2080.6053 | 2006.7778 | 969.6761 | 17.8772 | 12.0655 | 13.3866 | 13.7183 | 11.1118 | 7.6365 | 3500.0176 | 7217.795 | 11378.4077 | 2405.9132 | 4918.1171 | 8984.6354 | 0.10314 | 0.10409 | 0.10131 | 17.3337 | 10.6859 | 12.016 | 11.4663 | 27.0645 | 93.6585 | 139.16 | 111.6914 | 78.8593 | 99.54% | 99.51% | 99.36% | 99.52% | 99.45% | 98.96% | 116.3499 | 115.2887 | 118.4431 |  |  |  | 30 | 24.3 | 16.7 | 2340 | 1166.4 | 400.8 | 3907.2 | 116.839 | 14 | 30 | 72 | 30 | 98.61% | 0.10315 | 0.10323 | 43.3293 | 40.0356 | 126.1546 | 25.0044 | 98.61% | 3830.7152 | 99.37% | 99.41% | 85% |  |  | 99.35% | 1.0462
2022-02-03 | 173.9874 | 156.2398 | 156.2398 | 144.1612 | 130.7851 | 14.104 | 14.104 | 3471.996 | 1053.763 | 358.5893 | 613.2177 | 24.3004 | 12.0827 | 24.3004 | 64.2611 | 9762.885 | 360.5493 |  |  | 23.5956 | 1.0492 | 21.1798 | 4085.2137 | 2059.6437 | 2025.57 | 971.8069 | 17.7476 | 12.0786 | 13.3084 | 13.5801 | 11.2903 | 7.6841 | 3468.9742 | 7204.1502 | 11379.3194 | 2398.0299 | 4889.5661 | 8975.8279 | 0.10244 | 0.10598 | 0.10229 | 17.1379 | 10.5857 | 11.9227 | 12.3478 | 28.1479 | 105.7758 | 139.0799 | 111.7702 | 78.8113 | 99.5% | 99.5% | 99.28% | 99.49% | 99.42% | 98.82% | 117.1393 | 113.2297 | 117.3109 |  |  |  | 30 | 24.9417 | 16.975 | 2340 | 1197.2 | 407.4 | 3944.6 | 116.6934 | 14.9167 | 30 | 79.3333 | 30 | 98.59% | 0.10355 | 0.1035 | 43.1346 | 39.6463 | 125.9904 | 25.4113 | 98.59% | 3833.5777 | 99.37% | 99.36% | 84.99% |  |  | 99.33% | 1.0492
2022-02-02 | 173.3017 | 155.5625 | 155.5625 | 143.5663 | 130.2548 | 14.131 | 14.131 | 3471.2061 | 1055.0778 | 358.7265 | 612.928 | 24.7855 | 12.3927 | 24.7855 | 66.0946 | 9863.3858 | 358.9322 |  |  | 23.7091 | 1.0451 | 21.7093 | 4084.134 | 2057.4018 | 2026.7323 | 971.6544 | 17.7392 | 11.9962 | 13.3267 | 13.5653 | 11.3044 | 7.687 | 3501.4835 | 7276.6805 | 11496.7978 | 2421.7031 | 4936.8849 | 9067.2568 | 0.10254 | 0.10655 | 0.10329 | 17.1294 | 10.5081 | 11.9442 | 12.4785 | 28.3593 | 107.3192 | 138.2546 | 110.8729 | 77.7738 | 99.49% | 99.5% | 99.27% | 99.48% | 99.43% | 98.82% | 117.0262 | 112.6186 | 116.174 |  |  |  | 30 | 25 | 17 | 2340 | 1200 | 408 | 3948 | 116.1476 | 15 | 30 | 80 | 30 | 98.58% | 0.10395 | 0.10384 | 43.0621 | 39.5817 | 125.0568 | 25.5493 | 98.58% | 3872.9706 | 99.36% | 99.36% | 84.99% |  |  | 99.33% | 1.0451
2022-02-01 | 168.5946 | 151.2349 | 151.2349 | 139.4032 | 126.3524 | 14.0517 | 14.0517 | 3428.2628 | 1030.8226 | 347.1853 | 604.0388 | 24.5703 | 12.2852 | 24.5703 | 65.5209 | 9363.4232 | 343.1641 |  |  | 23.787 | 1.0423 | 21.3704 | 4032.3016 | 2050.2549 | 1982.0467 | 951.2241 | 17.3597 | 11.8318 | 13.0308 | 13.5182 | 11.0445 | 7.4397 | 3368.9044 | 6993.0927 | 10974.8749 | 2317.8917 | 4747.5497 | 8686.9056 | 0.10489 | 0.10693 | 0.10241 | 17.168 | 10.7111 | 12.0108 | 12.8449 | 28.486 | 107.1861 | 134.335 | 107.6524 | 75.7192 | 99.47% | 99.48% | 99.25% | 99.45% | 99.4% | 98.77% | 114.4103 | 112.22 | 117.1777 |  |  |  | 30 | 24.5104 | 16.5104 | 2340 | 1176.5 | 396.25 | 3912.75 | 112.2895 | 15 | 30 | 80 | 30 | 98.52% | 0.10514 | 0.10525 | 42.2223 | 39.8899 | 121.7176 | 26.16 | 98.52% | 3693.4496 | 99.33% | 99.32% | 85.02% |  |  | 99.32% | 1.0423
2022-01-31 | 168.4566 | 150.7129 | 150.7129 | 138.4939 | 125.0463 | 13.935 | 13.935 | 3466.0461 | 1030.1561 | 343.3854 | 611.9557 | 23.321 | 11.6605 | 23.321 | 62.1893 | 8839.9688 | 347.3719 |  |  | 23.6784 | 1.0462 | 20.1321 | 4078.0018 | 2092.5046 | 1985.4972 | 955.3411 | 17.7437 | 12.219 | 13.2871 | 13.7967 | 11.0374 | 7.3583 | 3230.1022 | 6688.0141 | 10405.9488 | 2210.6286 | 4546.8799 | 8274.828 | 0.10719 | 0.10687 | 0.10027 | 17.3349 | 11.019 | 12.1062 | 13.0955 | 28.3179 | 106.0276 | 134.655 | 108.0506 | 76.7719 | 99.47% | 99.49% | 99.25% | 99.41% | 99.38% | 98.72% | 111.9493 | 112.2887 | 119.6747 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 111.123 | 15 | 30 | 80 | 30 | 98.52% | 0.10598 | 0.10641 | 43.2499 | 40.4602 | 122.5718 | 26.546 | 98.52% | 3505.7819 | 99.33% | 99.29% | 84.99% |  |  | 99.31% | 1.0462
2022-01-30 | 167.7708 | 150.1198 | 150.1198 | 138.0647 | 124.7783 | 13.9992 | 13.9992 | 3462.3145 | 1029.047 | 343.0157 | 610.9389 | 23.6805 | 11.8403 | 23.6805 | 63.1481 | 9095.2471 | 345.6194 |  |  | 23.8701 | 1.0393 | 20.4425 | 4073.2533 | 2090.2518 | 1983.0016 | 953.9545 | 17.651 | 12.0551 | 13.3177 | 13.7819 | 11.0255 | 7.3503 | 3312.3928 | 6859.9829 | 10676.111 | 2266.7833 | 4663.1906 | 8488.5541 | 0.10716 | 0.1072 | 0.10146 | 17.2752 | 10.8928 | 12.1621 | 12.8691 | 27.8236 | 104.1518 | 133.6713 | 106.8955 | 75.2953 | 99.48% | 99.49% | 99.26% | 99.43% | 99.4% | 98.77% | 111.9849 | 111.9414 | 118.2742 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 110.7493 | 15 | 30 | 80 | 30 | 98.54% | 0.10626 | 0.10661 | 43.0238 | 40.3301 | 121.3387 | 26.0829 | 98.54% | 3595.4265 | 99.34% | 99.32% | 85% |  |  | 99.32% | 1.0393
2022-01-29 | 168.5184 | 151.0398 | 151.0398 | 139.1992 | 125.7612 | 14.0277 | 14.0277 | 3462.7213 | 1029.168 | 343.056 | 610.9147 | 24.7506 | 12.3753 | 24.7506 | 66.0017 | 9513.149 | 346.6441 |  |  | 23.7281 | 1.0444 | 21.3663 | 4073.6361 | 2090.4974 | 1983.1387 | 953.9707 | 17.4787 | 11.8406 | 13.1492 | 13.7835 | 11.0268 | 7.3512 | 3452.023 | 7149.4519 | 11127.1264 | 2362.3189 | 4859.8501 | 8846.9344 | 0.10743 | 0.10771 | 0.10299 | 17.1044 | 10.6981 | 12.0083 | 12.9712 | 28.0436 | 104.9706 | 134.0017 | 106.9163 | 74.5479 | 99.48% | 99.49% | 99.25% | 99.45% | 99.42% | 98.81% | 111.7035 | 111.4065 | 116.518 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 111.7368 | 15 | 30 | 80 | 30 | 98.53% | 0.10681 | 0.10707 | 42.4685 | 39.8108 | 121.2823 | 26.2891 | 98.53% | 3747.0578 | 99.34% | 99.34% | 85% |  |  | 99.31% | 1.0444
2022-01-28 | 165.5411 | 148.22 | 148.22 | 136.5378 | 123.686 | 14.0077 | 14.0077 | 3426.0062 | 1018.2557 | 339.4186 | 605.4444 | 24.973 | 12.4865 | 24.973 | 66.5947 | 9446.9018 | 335.5277 |  |  | 24.1415 | 1.0297 | 21.5582 | 4031.4506 | 2068.3319 | 1963.1187 | 944.863 | 17.321 | 11.6822 | 12.9482 | 13.6374 | 10.9099 | 7.2733 | 3436.2429 | 7112.485 | 11062.4861 | 2351.9312 | 4836.353 | 8798.5724 | 0.10705 | 0.10769 | 0.10338 | 17.2146 | 10.714 | 11.9919 | 12.8233 | 27.7361 | 103.8854 | 131.1756 | 104.3143 | 72.4443 | 99.47% | 99.48% | 99.24% | 99.45% | 99.43% | 98.82% | 112.0953 | 111.4265 | 116.0754 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 109.5943 | 15 | 30 | 80 | 30 | 98.51% | 0.10667 | 0.10688 | 41.9515 | 39.9205 | 118.5615 | 26.0004 | 98.51% | 3729.0118 | 99.33% | 99.34% | 84.98% |  |  | 99.32% | 1.0297
2022-01-27 | 166.2482 | 148.8923 | 148.8923 | 137.2712 | 124.163 | 14.3157 | 14.3157 | 3447.1031 | 1020.0394 | 307.3741 | 608.0075 | 26.1519 | 13.0759 | 26.1519 | 69.7384 | 9684.1259 | 340.6216 |  |  | 24.1125 | 1.0307 | 21.9978 | 4055.1106 | 2119.6896 | 1935.4211 | 915.3817 | 17.3559 | 11.6211 | 12.8747 | 13.976 | 10.929 | 6.5866 | 3581.0981 | 7542.4895 | 11320.2889 | 2423.928 | 5078.9172 | 9177.127 | 0.1098 | 0.10884 | 0.095803 | 17.2668 | 10.9802 | 12.2412 | 13.3666 | 27.7341 | 94.5485 | 131.2003 | 103.5022 | 70.8644 | 99.46% | 99.49% | 99.24% | 99.45% | 99.45% | 98.97% | 109.2915 | 110.2562 | 125.2568 |  |  |  | 31.9167 | 24.9583 | 15.0417 | 2489.5 | 1198 | 361 | 4048.5 | 109.8186 | 15 | 30 | 80 | 30 | 98.48% | 0.10725 | 0.10827 | 41.8517 | 40.4882 | 118.4862 | 26.8274 | 98.48% | 3811.7462 | 99.31% | 99.37% | 85.01% |  |  | 99.3% | 1.0307
2022-01-26 | 167.4651 | 149.7945 | 149.7945 | 137.9926 | 124.7812 | 14.0483 | 14.0483 | 3473.289 | 1027.6003 | 308.2801 | 614.0803 | 27.0209 | 13.5105 | 27.0209 | 72.0558 | 9753.1704 | 344.944 |  |  | 24.1496 | 1.0294 | 22.704 | 4087.3693 | 2137.4086 | 1949.9607 | 922.3604 | 17.6706 | 11.8018 | 13.1337 | 14.0928 | 11.01 | 6.606 | 3625.1625 | 7633.8467 | 11430.0108 | 2453.2674 | 5140.9834 | 9277.9205 | 0.10959 | 0.10869 | 0.095365 | 17.3758 | 11.0259 | 12.3287 | 13.7422 | 28.4834 | 96.7908 | 132.3826 | 104.2754 | 71.3093 | 99.45% | 99.47% | 99.22% | 99.44% | 99.45% | 98.96% | 109.5014 | 110.4028 | 125.8326 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 110.7828 | 15 | 30 | 80 | 30 | 98.44% | 0.10703 | 0.10806 | 42.6061 | 40.7304 | 119.5237 | 27.5868 | 98.44% | 3854.1881 | 99.3% | 99.36% | 84.98% |  |  | 99.28% | 1.0294
2022-01-25 | 166.8471 | 149.1478 | 149.1478 | 137.2528 | 123.9863 | 13.9144 | 13.9144 | 3469.5073 | 1026.4814 | 307.9444 | 612.8863 | 24.8705 | 12.4352 | 24.8705 | 66.3212 | 9397.7246 | 343.1615 |  |  | 24.0617 | 1.0325 | 20.8971 | 4082.3936 | 2135.0814 | 1947.3122 | 920.8308 | 17.6993 | 11.8949 | 13.1904 | 14.0775 | 10.998 | 6.5988 | 3496.0491 | 7365.4901 | 11032.9537 | 2365.4601 | 4958.9248 | 8953.5664 | 0.10985 | 0.10855 | 0.094279 | 17.4371 | 11.1372 | 12.415 | 13.1433 | 27.2313 | 92.4924 | 132.3179 | 104.6156 | 72.269 | 99.47% | 99.5% | 99.26% | 99.44% | 99.45% | 98.97% | 109.2379 | 110.5506 | 127.2814 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 110.1237 | 15 | 30 | 80 | 30 | 98.51% | 0.10694 | 0.10808 | 42.7847 | 40.9892 | 119.8243 | 26.3755 | 98.51% | 3717.5005 | 99.33% | 99.37% | 84.99% |  |  | 99.31% | 1.0325
2022-01-24 | 165.337 | 147.5914 | 147.5914 | 135.5332 | 122.2504 | 14.2745 | 14.2745 | 3470.4576 | 1026.7626 | 308.0288 | 611.7814 | 23.8909 | 11.9454 | 23.8909 | 63.709 | 8861.9209 | 339.941 |  |  | 24.0404 | 1.0333 | 20.074 | 4082.239 | 2135.6662 | 1946.5728 | 919.8102 | 17.7456 | 12.0582 | 13.3062 | 14.0813 | 11.001 | 6.6006 | 3322.3385 | 7004.3186 | 10498.8798 | 2247.5512 | 4713.9447 | 8517.1465 | 0.11106 | 0.10947 | 0.094268 | 17.4866 | 11.3004 | 12.55 | 13.3013 | 27.5457 | 93.4957 | 131.0117 | 103.8375 | 72.3501 | 99.47% | 99.49% | 99.25% | 99.41% | 99.42% | 98.9% | 108.051 | 109.6183 | 127.2966 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 108.0047 | 15 | 30 | 80 | 30 | 98.5% | 0.10786 | 0.1091 | 43.11 | 41.337 | 118.9795 | 26.681 | 98.5% | 3533.7264 | 99.32% | 99.33% | 85.01% |  |  | 99.3% | 1.0333
2022-01-23 | 164.9092 | 147.3917 | 147.3917 | 135.4747 | 122.1767 | 14.0838 | 14.0838 | 3450.684 | 1020.9124 | 306.2737 | 609.3619 | 24.0513 | 12.0256 | 24.0513 | 64.1368 | 9009.4272 | 335.9232 |  |  | 24.0114 | 1.0343 | 20.2088 | 4060.0458 | 2123.4978 | 1936.548 | 915.6356 | 17.5175 | 11.917 | 13.2384 | 14.0011 | 10.9383 | 6.563 | 3373.3157 | 7107.6678 | 10647.8442 | 2282.3603 | 4785.0575 | 8640.5671 | 0.11079 | 0.10926 | 0.094464 | 17.4011 | 11.2516 | 12.5671 | 13.1242 | 27.1898 | 92.3418 | 130.715 | 103.5444 | 71.8597 | 99.47% | 99.5% | 99.26% | 99.42% | 99.43% | 98.93% | 108.3169 | 109.8265 | 127.0326 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 108.0947 | 15 | 30 | 80 | 30 | 98.51% | 0.10769 | 0.10889 | 42.6729 | 41.2198 | 118.5306 | 26.3355 | 98.51% | 3587.1412 | 99.33% | 99.35% | 84.99% |  |  | 99.31% | 1.0343
2022-01-22 | 165.6058 | 148.177 | 148.177 | 136.455 | 123.3141 | 14.2316 | 14.2316 | 3435.4025 | 1016.3913 | 304.9174 | 606.4504 | 24.9012 | 12.4506 | 24.9012 | 66.4033 | 9366.4358 | 337.8183 |  |  | 23.8599 | 1.0397 | 20.9229 | 4041.8529 | 2114.0938 | 1927.759 | 911.3678 | 17.4288 | 11.722 | 13.0198 | 13.9391 | 10.8899 | 6.5339 | 3491.3425 | 7357.2467 | 11023.0121 | 2362.1422 | 4952.7425 | 8944.4564 | 0.1107 | 0.10945 | 0.095327 | 17.4305 | 11.1439 | 12.4474 | 13.1389 | 27.218 | 92.4262 | 130.9114 | 103.4453 | 71.2627 | 99.47% | 99.5% | 99.26% | 99.44% | 99.45% | 98.97% | 108.3982 | 109.639 | 125.8825 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 109.134 | 15 | 30 | 80 | 30 | 98.51% | 0.10784 | 0.10897 | 42.1706 | 41.0218 | 118.4473 | 26.363 | 98.51% | 3712.8211 | 99.33% | 99.37% | 85% |  |  | 99.31% | 1.0397
2022-01-21 | 164.6217 | 147.0662 | 147.0662 | 135.3081 | 122.297 | 14.3177 | 14.3177 | 3458.2837 | 1023.1609 | 306.9483 | 611.1427 | 26.3049 | 13.1525 | 26.3049 | 70.1464 | 9530.3772 | 336.9426 |  |  | 24.1343 | 1.03 | 22.1024 | 4069.4263 | 2128.1746 | 1941.2518 | 918.0909 | 17.5554 | 11.7581 | 13.1443 | 14.0319 | 10.9624 | 6.5775 | 3545.208 | 7466.8282 | 11181.8341 | 2399.0323 | 5027.9952 | 9075.65 | 0.11152 | 0.11085 | 0.097536 | 17.3775 | 11.0599 | 12.4259 | 13.6286 | 28.2441 | 95.9603 | 129.5968 | 101.861 | 69.4573 | 99.45% | 99.48% | 99.23% | 99.43% | 99.44% | 98.94% | 107.6056 | 108.2576 | 123.0317 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 108.009 | 15 | 30 | 80 | 30 | 98.45% | 0.10907 | 0.11008 | 42.4578 | 40.8634 | 116.9595 | 27.3554 | 98.45% | 3769.4312 | 99.3% | 99.36% | 84.98% |  |  | 99.28% | 1.03
2022-01-20 | 164.6254 | 147.145 | 147.145 | 135.4394 | 122.421 | 14.3456 | 14.3456 | 3466.9962 | 1025.7385 | 307.7216 | 612.2345 | 27.8277 | 13.9138 | 27.8277 | 74.2071 | 9778.4332 | 337.6723 |  |  | 24.2859 | 1.0246 | 23.3818 | 4079.2307 | 2133.5361 | 1945.6945 | 919.956 | 17.4804 | 11.7055 | 12.9322 | 14.0673 | 10.9901 | 6.594 | 3622.1297 | 7629.7278 | 11427.2868 | 2451.1181 | 5137.352 | 9274.2181 | 0.11143 | 0.11106 | 0.098514 | 17.2419 | 10.9741 | 12.1901 | 14.0735 | 29.1652 | 99.0771 | 129.3536 | 101.399 | 68.5846 | 99.43% | 99.46% | 99.2% | 99.43% | 99.43% | 98.93% | 107.6906 | 108.0545 | 121.8104 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 108.0582 | 15 | 30 | 80 | 30 | 98.4% | 0.10924 | 0.11017 | 42.1182 | 40.4062 | 116.5215 | 28.2471 | 98.4% | 3851.4624 | 99.28% | 99.35% | 84.99% |  |  | 99.26% | 1.0246
2022-01-19 | 161.8419 | 144.2721 | 144.2721 | 132.4908 | 119.4009 | 14.1527 | 14.1527 | 3469.0187 | 1026.0113 | 309.3114 | 612.3348 | 27.3619 | 13.681 | 27.3619 | 72.9651 | 9438.3322 | 332.2652 |  |  | 24.2648 | 1.0254 | 23.0133 | 4081.3535 | 2133.696 | 1947.6575 | 921.6462 | 17.5698 | 11.7813 | 13.0106 | 14.0683 | 10.993 | 6.6281 | 3508.6706 | 7384.1946 | 11077.3486 | 2375.0683 | 4974.4985 | 8982.4994 | 0.1135 | 0.11329 | 0.10107 | 17.3125 | 11.0241 | 12.2426 | 14.2924 | 29.6451 | 101.1751 | 127.0973 | 99.493 | 67.2454 | 99.42% | 99.45% | 99.19% | 99.4% | 99.4% | 98.87% | 105.7282 | 105.919 | 118.7327 |  |  |  | 31.9406 | 24.9584 | 15.0484 | 2491.3665 | 1198.0011 | 361.1611 | 4050.5287 | 105.2766 | 15 | 30 | 80 | 30 | 98.37% | 0.11144 | 0.11233 | 42.3617 | 40.5791 | 114.5825 | 28.6928 | 98.37% | 3733.0312 | 99.27% | 99.32% | 85% |  |  | 99.25% | 1.0254
2022-01-18 | 158.4724 | 140.8504 | 140.8504 | 129.043 | 115.9065 | 13.9791 | 13.9791 | 3470.6749 | 1021.3951 | 331.5754 | 612.8848 | 27.6323 | 13.8161 | 27.6323 | 73.6861 | 9070.5057 | 324.7954 |  |  | 24.3225 | 1.0234 | 23.6019 | 4083.5598 | 2117.7044 | 1965.8553 | 944.4603 | 17.622 | 11.8074 | 13.1249 | 13.9629 | 10.9435 | 7.1052 | 3357.8732 | 6959.3923 | 10684.6123 | 2284.3814 | 4728.7781 | 8557.4477 | 0.11493 | 0.11491 | 0.11004 | 17.2761 | 10.8158 | 12.0732 | 14.8648 | 31.2902 | 114.7433 | 124.3295 | 97.4619 | 66.0769 | 99.4% | 99.42% | 99.14% | 99.35% | 99.34% | 98.66% | 104.4122 | 104.4312 | 109.0502 |  |  |  | 31.03 | 24.32 | 15.79 | 2420.3401 | 1167.36 | 378.96 | 3966.66 | 101.9651 | 15 | 30 | 80 | 30 | 98.3% | 0.11414 | 0.11446 | 42.5543 | 40.1651 | 112.1159 | 29.9769 | 98.3% | 3603.0556 | 99.23% | 99.24% | 84.99% |  |  | 99.22% | 1.0234
2022-01-17 | 159.5841 | 141.9892 | 141.9892 | 130.3031 | 116.8015 | 13.8941 | 13.8941 | 3470.7988 | 1021.4315 | 331.5873 | 611.8419 | 24.7634 | 12.3817 | 24.7634 | 66.0358 | 8730.9569 | 326.6619 |  |  | 24.1461 | 1.0296 | 21.1515 | 4082.6407 | 2117.78 | 1964.8607 | 943.4292 | 17.5949 | 11.6861 | 13.093 | 13.9634 | 10.9439 | 7.1054 | 3240.93 | 6723.0081 | 10330.749 | 2204.0906 | 4565.8797 | 8270.1494 | 0.11416 | 0.11319 | 0.10658 | 17.2577 | 10.7159 | 12.068 | 13.8908 | 29.2188 | 107.0501 | 125.934 | 99.5465 | 68.6377 | 99.44% | 99.46% | 99.2% | 99.37% | 99.36% | 98.71% | 105.12 | 106.0197 | 112.5912 |  |  |  | 31.03 | 24.32 | 15.79 | 2420.3401 | 1167.36 | 378.96 | 3966.66 | 103.0418 | 15 | 30 | 80 | 30 | 98.42% | 0.11263 | 0.11315 | 42.374 | 40.0415 | 114.1163 | 27.9944 | 98.42% | 3478.6772 | 99.29% | 99.26% | 85.01% |  |  | 99.27% | 1.0296
2022-01-16 | 159.877 | 142.3459 | 142.3459 | 130.5879 | 117.3706 | 13.8967 | 13.8967 | 3471.7869 | 1021.7223 | 331.6817 | 613.6677 | 26.5552 | 13.2776 | 26.5552 | 70.8139 | 9008.6828 | 327.6985 |  |  | 24.3284 | 1.0232 | 22.6819 | 4085.4546 | 2118.3829 | 1967.0717 | 945.3494 | 17.5311 | 11.758 | 13.1888 | 13.9674 | 10.947 | 7.1075 | 3339.7669 | 6920.6465 | 10622.9168 | 2272.0691 | 4702.9152 | 8508.9829 | 0.11349 | 0.11292 | 0.10711 | 17.1738 | 10.7588 | 12.1125 | 14.3645 | 30.2395 | 110.9119 | 125.9208 | 99.1884 | 67.8917 | 99.42% | 99.44% | 99.17% | 99.37% | 99.36% | 98.7% | 105.7361 | 106.2686 | 112.032 |  |  |  | 31.03 | 24.32 | 15.79 | 2420.3401 | 1167.36 | 378.96 | 3966.66 | 103.4649 | 15 | 30 | 80 | 30 | 98.36% | 0.11229 | 0.11271 | 42.4779 | 40.0451 | 113.7452 | 28.9706 | 98.36% | 3583.3015 | 99.26% | 99.26% | 84.98% |  |  | 99.24% | 1.0232
2022-01-15 | 160.6829 | 143.3217 | 143.3217 | 131.7011 | 118.682 | 14.105 | 14.105 | 3463.4726 | 1019.2755 | 330.8873 | 610.4466 | 27.8757 | 13.9379 | 27.8757 | 74.3353 | 9422.854 | 328.663 |  |  | 24.0715 | 1.0322 | 23.8098 | 4073.9191 | 2113.3098 | 1960.6094 | 941.3339 | 17.3611 | 11.6206 | 12.8916 | 13.9339 | 10.9208 | 7.0904 | 3470.6342 | 7198.4498 | 11060.0148 | 2360.5491 | 4889.1749 | 8854.5157 | 0.114 | 0.11375 | 0.10893 | 17.0834 | 10.6908 | 11.9224 | 14.6066 | 30.7296 | 112.6007 | 126.1643 | 99.1 | 67.1857 | 99.41% | 99.43% | 99.16% | 99.38% | 99.37% | 98.73% | 105.2661 | 105.498 | 110.1612 |  |  |  | 31.03 | 24.32 | 15.79 | 2420.3401 | 1167.36 | 378.96 | 3966.66 | 104.555 | 15 | 30 | 80 | 30 | 98.34% | 0.11311 | 0.11344 | 41.8733 | 39.6966 | 113.6371 | 29.4409 | 98.34% | 3725.1153 | 99.25% | 99.27% | 85.02% |  |  | 99.23% | 1.0322
2022-01-14 | 160.8989 | 143.4478 | 143.4478 | 131.7397 | 118.794 | 14.3593 | 14.3593 | 3471.8887 | 1021.7563 | 331.6791 | 613.8945 | 28.84 | 14.42 | 28.84 | 76.9065 | 9547.0803 | 330.8743 |  |  | 24.1989 | 1.0277 | 24.6332 | 4085.7831 | 2118.4533 | 1967.3299 | 945.5736 | 17.4512 | 11.7081 | 13.0986 | 13.9678 | 10.9474 | 7.1074 | 3525.0824 | 7303.0089 | 11207.1772 | 2398.374 | 4963.376 | 8978.114 | 0.11402 | 0.11415 | 0.11 | 17.093 | 10.7105 | 12.0244 | 14.8449 | 31.2569 | 114.6659 | 125.8943 | 98.5618 | 66.4015 | 99.4% | 99.42% | 99.14% | 99.38% | 99.37% | 98.72% | 105.2435 | 105.1274 | 109.09 |  |  |  | 31.03 | 24.32 | 15.7894 | 2420.3401 | 1167.36 | 378.9445 | 3966.6446 | 104.4175 | 15 | 30 | 80 | 30 | 98.31% | 0.11342 | 0.11367 | 42.2578 | 39.8279 | 113.1585 | 29.9447 | 98.31% | 3781.8197 | 99.24% | 99.27% | 84.97% |  |  | 99.22% | 1.0277
2022-01-13 | 159.7442 | 142.2189 | 142.2189 | 130.6303 | 117.7637 | 14.1787 | 14.1787 | 3468.7499 | 1031.4144 | 325.5144 | 612.6602 | 28.795 | 14.3975 | 28.795 | 76.7866 | 9546.3892 | 327.6048 |  |  | 24.1474 | 1.0295 | 24.5332 | 4081.4101 | 2111.8211 | 1969.589 | 938.1746 | 17.5253 | 11.5886 | 13.0124 | 13.9241 | 11.0509 | 6.9753 | 3527.2816 | 7373.463 | 11250.283 | 2402.8153 | 4986.1052 | 9040.4907 | 0.11481 | 0.11674 | 0.11014 | 17.1746 | 10.6293 | 12.0452 | 14.7741 | 31.4149 | 111.7809 | 124.8607 | 97.4593 | 65.1997 | 99.4% | 99.42% | 99.15% | 99.39% | 99.37% | 98.76% | 104.5228 | 102.7967 | 108.9519 |  |  |  | 31.5 | 25 | 15.78 | 2457 | 1200 | 378.72 | 4035.72 | 103.6118 | 15 | 30 | 80 | 30 | 98.32% | 0.11468 | 0.11494 | 42.1263 | 39.8491 | 112.1454 | 29.8289 | 98.32% | 3793.8356 | 99.24% | 99.28% | 84.99% |  |  | 99.22% | 1.0295
2022-01-12 | 158.1402 | 140.6317 | 140.6317 | 129.0189 | 116.2038 | 13.908 | 13.908 | 3468.2121 | 1031.2545 | 325.4639 | 611.6757 | 28.6178 | 14.3089 | 28.6178 | 76.3142 | 9427.1542 | 325.7118 |  |  | 24.027 | 1.0338 | 24.3823 | 4079.8879 | 2111.4937 | 1968.3942 | 937.1397 | 17.5084 | 11.6128 | 12.9977 | 13.9219 | 11.0492 | 6.9742 | 3481.9257 | 7282.0417 | 11116.1066 | 2371.65 | 4922.9977 | 8930.3847 | 0.11635 | 0.11843 | 0.11189 | 17.1696 | 10.6638 | 12.0551 | 14.9352 | 31.7474 | 112.9094 | 123.6913 | 96.4454 | 64.433 | 99.4% | 99.42% | 99.15% | 99.37% | 99.36% | 98.74% | 103.1343 | 101.3249 | 107.2448 |  |  |  | 31.5 | 25 | 15.78 | 2457 | 1200 | 378.72 | 4035.72 | 102.2408 | 15 | 30 | 80 | 30 | 98.3% | 0.1163 | 0.11655 | 42.119 | 39.8886 | 111.103 | 30.1451 | 98.3% | 3745.7645 | 99.24% | 99.26% | 85.01% |  |  | 99.21% | 1.0338
2022-01-11 | 156.4037 | 138.9098 | 138.9098 | 127.235 | 114.1975 | 13.8254 | 13.8254 | 3472.4557 | 1032.5163 | 325.8622 | 613.314 | 28.7574 | 14.3787 | 28.7574 | 76.6865 | 9192.9951 | 323.7083 |  |  | 24.0125 | 1.0343 | 24.5012 | 4085.7697 | 2114.0772 | 1971.6925 | 939.1762 | 17.4939 | 11.6748 | 13.0212 | 13.939 | 11.0627 | 6.9828 | 3406.8349 | 7120.6431 | 10863.1938 | 2320.9582 | 4815.5359 | 8730.0108 | 0.11788 | 0.12004 | 0.11351 | 17.1164 | 10.6913 | 12.034 | 15.3623 | 32.6704 | 116.2643 | 122.2984 | 95.313 | 63.6242 | 99.38% | 99.4% | 99.12% | 99.34% | 99.32% | 98.67% | 101.7977 | 99.9632 | 105.7165 |  |  |  | 31.5 | 25 | 15.78 | 2457 | 1200 | 378.72 | 4035.72 | 100.3818 | 15 | 30 | 80 | 30 | 98.26% | 0.11787 | 0.11811 | 42.1899 | 39.8417 | 109.9205 | 31.0202 | 98.26% | 3664.1459 | 99.22% | 99.23% | 84.99% |  |  | 99.19% | 1.0343
2022-01-10 | 153.0478 | 135.4077 | 135.4077 | 123.64 | 110.5336 | 13.7756 | 13.7756 | 3472.3427 | 1047.0568 | 321.9089 | 612.439 | 27.6465 | 14.0045 | 27.6465 | 73.1199 | 8608.1128 | 316.415 |  |  | 23.8963 | 1.0384 | 23.5985 | 4084.7817 | 2103.3771 | 1981.4046 | 934.3478 | 17.6401 | 11.7678 | 13.0136 | 13.8684 | 11.2185 | 6.898 | 3186.7345 | 6726.8985 | 10224.2433 | 2177.4536 | 4524.0382 | 8232.9619 | 0.12037 | 0.1249 | 0.11458 | 17.2222 | 10.7493 | 12.0936 | 15.9311 | 34.038 | 116.5866 | 119.6349 | 93.2662 | 62.5119 | 99.36% | 99.39% | 99.11% | 99.27% | 99.25% | 98.58% | 99.6899 | 96.0752 | 104.7266 |  |  |  | 31.1391 | 25.1891 | 15.4883 | 2428.8469 | 1209.075 | 371.72 | 4009.6419 | 96.8003 | 13.2812 | 26.2188 | 69.3438 | 26.2188 | 98.22% | 0.1209 | 0.1212 | 42.4215 | 40.0651 | 107.8666 | 31.8311 | 98.22% | 3446.4324 | 99.2% | 99.15% | 85.01% |  |  | 99.17% | 1.0384
2022-01-09 | 151.3425 | 134.0021 | 134.0021 | 122.5459 | 109.4298 | 13.8343 | 13.8343 | 3464.5345 | 1071.6406 | 317.5076 | 611.3633 | 30.3616 | 15.9798 | 30.3616 | 78.301 | 8904.6969 | 312.9752 |  |  | 23.8321 | 1.0407 | 26.1398 | 4075.8977 | 2075.3863 | 2000.5115 | 928.8709 | 17.3404 | 11.4562 | 12.8446 | 13.6839 | 11.4819 | 6.8037 | 3267.2309 | 7001.6149 | 10597.194 | 2247.706 | 4669.0324 | 8552.4541 | 0.12101 | 0.13095 | 0.11844 | 16.8869 | 10.3918 | 12.0128 | 17.4139 | 37.152 | 118.8015 | 117.6794 | 91.2464 | 59.7828 | 99.29% | 99.35% | 99.08% | 99.23% | 99.2% | 98.61% | 99.1645 | 91.6364 | 101.3197 |  |  |  | 30.45 | 25.55 | 15.14 | 2375.1001 | 1226.4 | 363.36 | 3964.86 | 95.6118 | 10 | 19 | 49 | 19 | 98.12% | 0.12378 | 0.12385 | 41.6412 | 39.2915 | 105.5141 | 33.7033 | 98.12% | 3574.4635 | 99.15% | 99.12% | 85% |  |  | 99.12% | 1.0407
2022-01-08 | 147.9816 | 130.7559 | 130.7559 | 119.6483 | 106.731 | 14.0876 | 14.0876 | 3471.2942 | 1073.7315 | 318.1271 | 613.242 | 36.1976 | 19.0513 | 36.1976 | 93.3516 | 9439.6694 | 310.0648 |  |  | 23.7745 | 1.0427 | 31.1642 | 4084.5362 | 2079.4356 | 2005.1006 | 931.3691 | 17.2257 | 11.1076 | 12.7564 | 13.7106 | 11.5043 | 6.817 | 3455.9606 | 7398.4442 | 11188.0546 | 2378.6239 | 4936.516 | 9033.5138 | 0.12598 | 0.1385 | 0.13067 | 16.7206 | 10.0391 | 11.8796 | 19.6955 | 42.0579 | 134.6217 | 113.4833 | 86.6129 | 54.4012 | 99.2% | 99.27% | 98.97% | 99.17% | 99.15% | 98.51% | 95.254 | 86.6424 | 91.8378 |  |  |  | 30.45 | 25.55 | 15.14 | 2375.1001 | 1226.4 | 363.36 | 3964.86 | 92.6385 | 10 | 19 | 49 | 19 | 97.88% | 0.13074 | 0.13028 | 41.0897 | 38.6393 | 100.78 | 38.1491 | 97.88% | 3779.7124 | 99.04% | 99.06% | 84.99% |  |  | 99% | 1.0427
2022-01-07
2022-01-06
2022-01-05 | 203.7387 | 185.2566 | 185.2566 | 173.2545 | 160.6067 | 14.1762 | 14.1762 | 3473.1888 | 1126.4396 | 211.2074 | 613.4394 | 17.8305 | 11.2614 | 22.5228 | 53.4916 | 9326.6461 | 429.9954 |  |  | 23.7073 | 1.0451 | 17.4818 | 4086.6283 | 2135.5418 | 1951.0865 | 824.6468 | 18.4822 | 12.0021 | 12.6026 | 14.0805 | 12.069 | 4.5259 | 3539.2455 | 8342.9695 | 11197.04 | 2395.3371 | 5270.9668 | 9630.4484 | 0.087387 | 0.090853 | 0.045105 | 18.1721 | 11.8033 | 13.0643 | 11.9003 | 25.7711 | 48.1503 | 168.401 | 138.8371 | 104.8696 | 99.53% | 99.57% | 99.44% | 99.5% | 99.51% | 99.5% | 137.3195 | 132.0808 | 266.0435 |  |  |  | 28 | 24 | 9 | 2184 | 1152 | 216 | 3552 | 146.4528 | 12 | 24 | 57 | 19 | 98.95% | 0.081731 | 0.08594 | 43.0868 | 43.0397 | 156.0896 | 18.9043 | 98.95% | 3767.9468 | 99.53% | 99.51% | 84.99% |  |  | 99.51% | 1.0451
2022-01-04 | 203.8839 | 185.306 | 185.306 | 173.1879 | 160.657 | 13.894 | 13.894 | 3472.0066 | 1085.2167 | 288.4753 | 613.1897 | 18.5471 | 11.7139 | 23.4279 | 55.6412 | 9145.5287 | 429.1998 |  |  | 23.4381 | 1.0548 | 19.025 | 4085.1963 | 2098.3146 | 1986.8817 | 901.665 | 18.5779 | 12.1181 | 12.663 | 13.835 | 11.6273 | 6.1816 | 3332.1559 | 7314.4407 | 10729.3456 | 2278.9973 | 4811.9856 | 8804.8946 | 0.086168 | 0.086734 | 0.059668 | 18.1114 | 11.2261 | 12.1418 | 12.9023 | 28.5518 | 75.5172 | 169.3646 | 141.4102 | 109.2822 | 99.49% | 99.51% | 99.37% | 99.43% | 99.41% | 99.14% | 139.2622 | 138.3542 | 201.1124 |  |  |  | 29.375 | 24.6875 | 13.125 | 2291.25 | 1185 | 315 | 3791.25 | 146.6855 | 12 | 24 | 57 | 19 | 98.86% | 0.082109 | 0.084143 | 43.3589 | 41.4793 | 157.3722 | 20.6912 | 98.86% | 3612.9238 | 99.49% | 99.38% | 84.99% |  |  | 99.46% | 1.0548
2022-01-03 | 202.4113 | 183.8648 | 183.8648 | 171.6763 | 158.8277 | 13.9116 | 13.9116 | 3468.9204 | 1067.3601 | 320.208 | 612.3841 | 17.847 | 11.2718 | 22.5436 | 53.541 | 8633.4936 | 426.4774 |  |  | 23.387 | 1.0567 | 18.6418 | 4081.3046 | 2081.3523 | 1999.9523 | 932.5922 | 18.5465 | 12.1885 | 12.8178 | 13.7232 | 11.436 | 6.8616 | 3118.9042 | 6662.7168 | 10118.5727 | 2142.1767 | 4450.9274 | 8151.3679 | 0.086025 | 0.085272 | 0.065409 | 18.0399 | 11.0381 | 11.9326 | 13.1245 | 29.2654 | 87.2802 | 168.5719 | 141.717 | 110.8513 | 99.47% | 99.49% | 99.34% | 99.39% | 99.34% | 98.93% | 139.4948 | 140.7266 | 183.4609 |  |  |  | 30 | 25 | 15 | 2340 | 1200 | 360 | 3900 | 144.9367 | 12 | 24 | 57 | 19 | 98.84% | 0.082485 | 0.08389 | 43.5528 | 41.0107 | 157.0699 | 21.1303 | 98.84% | 3407.2561 | 99.48% | 99.3% | 85% |  |  | 99.45% | 1.0567
2022-01-02 | 197.4325 | 179.6004 | 179.6004 | 167.8689 | 155.5321 | 13.923 | 13.923 | 3386.2635 | 1041.9272 | 312.5782 | 597.7962 | 18.397 | 11.6191 | 23.2383 | 55.191 | 8619.7173 | 403.8571 |  |  | 23.3822 | 1.0569 | 19.2163 | 3984.0597 | 2031.7581 | 1952.3016 | 910.3744 | 17.8321 | 11.7314 | 12.3088 | 13.3962 | 11.1635 | 6.6981 | 3141.8122 | 6711.0329 | 10191.2674 | 2158.0172 | 4483.4376 | 8210.2235 | 0.086403 | 0.0858 | 0.066158 | 17.9839 | 11.0156 | 11.8807 | 13.1118 | 29.2397 | 87.2108 | 163.8614 | 137.5106 | 107.0023 | 99.46% | 99.48% | 99.33% | 99.39% | 99.35% | 98.94% | 138.8841 | 139.8599 | 181.3839 |  |  |  | 30 | 25 | 15 | 2340 | 1200 | 360 | 3900 | 141.637 | 12 | 24 | 57 | 19 | 98.81% | 0.082971 | 0.084349 | 41.8724 | 40.8802 | 152.3472 | 21.1114 | 98.81% | 3432.1964 | 99.46% | 99.31% | 85% |  |  | 99.45% | 1.0569
2022-01-01 | 201.7952 | 183.3894 | 183.3894 | 171.3498 | 158.4964 | 14.163 | 14.163 | 3467.5443 | 1066.9367 | 320.081 | 611.554 | 17.3626 | 10.9659 | 21.9317 | 52.0879 | 8732.326 | 423.9403 |  |  | 23.5415 | 1.0511 | 18.1359 | 4079.0983 | 2080.5266 | 1998.5717 | 931.635 | 18.4058 | 12.0396 | 12.6453 | 13.7178 | 11.4315 | 6.8589 | 3170.4581 | 6776.2461 | 10295.6007 | 2177.209 | 4525.4915 | 8291.9917 | 0.086032 | 0.085406 | 0.065803 | 17.9188 | 10.9164 | 11.7924 | 12.4914 | 27.8426 | 82.9963 | 167.5981 | 140.6888 | 109.5606 | 99.5% | 99.52% | 99.37% | 99.43% | 99.38% | 99% | 139.4829 | 140.5052 | 182.3627 |  |  |  | 30 | 25 | 15 | 2340 | 1200 | 360 | 3900 | 144.3071 | 12 | 24 | 57 | 19 | 98.89% | 0.082595 | 0.083972 | 43.0907 | 40.6277 | 155.9789 | 20.1038 | 98.89% | 3464.199 | 99.5% | 99.34% | 85.01% |  |  | 99.47% | 1.0511
2021-12-31 | 202.6369 | 184.2517 | 184.2517 | 172.1826 | 159.5294 | 14.1613 | 14.1613 | 3457.2325 | 1063.7638 | 319.1292 | 610.8489 | 17.5142 | 11.0616 | 22.1232 | 52.5426 | 8964.1076 | 425.9512 |  |  | 23.3686 | 1.0574 | 18.2942 | 4068.0813 | 2074.3395 | 1993.7418 | 929.978 | 18.3851 | 12.0691 | 12.629 | 13.677 | 11.3975 | 6.8385 | 3240.5613 | 6922.0011 | 10510.8503 | 2225.6435 | 4624.3654 | 8468.0242 | 0.085974 | 0.085444 | 0.065964 | 17.969 | 10.9795 | 11.8044 | 12.3628 | 27.5669 | 82.224 | 168.2101 | 141.0447 | 109.6173 | 99.5% | 99.52% | 99.38% | 99.44% | 99.4% | 99.03% | 139.5776 | 140.4435 | 181.9169 |  |  |  | 30 | 25 | 15 | 2340 | 1200 | 360 | 3900 | 145.3219 | 12 | 24 | 57 | 19 | 98.9% | 0.082603 | 0.083964 | 43.0832 | 40.7529 | 156.369 | 19.9044 | 98.9% | 3539.9315 | 99.51% | 99.37% | 84.98% |  |  | 99.48% | 1.0574
2021-12-30 | 203.0811 | 184.6102 | 184.6102 | 172.5969 | 159.8524 | 14.172 | 14.172 | 3468.7637 | 1040.6616 | 332.5781 | 612.3916 | 17.9991 | 8.683 | 17.366 | 41.2442 | 9130.0653 | 427.1831 |  |  | 23.3706 | 1.0573 | 14.4099 | 4081.1553 | 2095.524 | 1985.6313 | 944.9697 | 18.4709 | 12.0132 | 12.6987 | 13.8166 | 11.1499 | 7.1267 | 3311.3347 | 6938.8657 | 10684.8315 | 2264.0197 | 4685.8363 | 8543.9977 | 0.086749 | 0.083556 | 0.068789 | 18.0306 | 10.8903 | 11.681 | 9.6367 | 20.89 | 66.6604 | 168.3969 | 141.0892 | 109.5389 | 99.62% | 99.63% | 99.52% | 99.57% | 99.55% | 99.22% | 138.3297 | 143.6167 | 174.4478 |  |  |  | 30.9792 | 25 | 15.9792 | 2416.375 | 1200 | 383.5 | 3999.875 | 145.6383 | 12 | 24 | 57 | 24.875 | 98.89% | 0.082854 | 0.084069 | 43.1828 | 40.6019 | 156.4816 | 20.2209 | 98.89% | 3592.6991 | 99.5% | 99.51% | 84.99% |  |  | 99.47% | 1.0573
2021-12-29 | 202.5202 | 184.1093 | 184.1093 | 172.0025 | 159.4482 | 14.3249 | 14.3249 | 3472.111 | 1041.1128 | 333.1561 | 612.5297 | 19.4966 | 9.3583 | 18.7167 | 44.4522 | 9355.2487 | 425.3891 |  |  | 23.543 | 1.0511 | 15.5318 | 4084.6407 | 2097.8422 | 1986.7985 | 945.6858 | 18.4108 | 12.1068 | 12.5274 | 13.8319 | 11.1548 | 7.1391 | 3396.2184 | 7114.536 | 10959.9683 | 2321.8949 | 4805.3014 | 8762.0232 | 0.086832 | 0.083866 | 0.069598 | 17.9514 | 10.9645 | 11.5139 | 10.0787 | 21.8348 | 69.7648 | 167.4272 | 139.7981 | 107.8126 | 99.6% | 99.61% | 99.49% | 99.57% | 99.55% | 99.2% | 138.1972 | 143.0857 | 172.4188 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 145.1164 | 12 | 24 | 57 | 25 | 98.82% | 0.083126 | 0.084289 | 43.0451 | 40.4298 | 155.2456 | 21.2519 | 98.82% | 3684.4879 | 99.47% | 99.5% | 85% |  |  | 99.44% | 1.0511
2021-12-28 | 202.7761 | 184.2983 | 184.2983 | 172.1731 | 159.466 | 14.347 | 14.347 | 3472.8643 | 1041.3386 | 333.2284 | 612.8923 | 19.4135 | 9.3185 | 18.6369 | 44.2627 | 9144.7432 | 426.3718 |  |  | 23.4308 | 1.0551 | 15.4656 | 4085.7565 | 2098.2973 | 1987.4593 | 946.1206 | 18.4778 | 12.1252 | 12.6083 | 13.8349 | 11.1572 | 7.1406 | 3329.9458 | 6974.506 | 10742.4659 | 2276.7189 | 4711.1769 | 8588.9044 | 0.086965 | 0.083831 | 0.06928 | 18.0088 | 10.975 | 11.5794 | 10.2766 | 22.2666 | 71.1566 | 167.8532 | 140.426 | 108.7493 | 99.59% | 99.6% | 99.48% | 99.55% | 99.53% | 99.17% | 137.9861 | 143.1446 | 173.2105 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 145.1 | 12 | 24 | 57 | 25 | 98.81% | 0.083133 | 0.084329 | 43.2113 | 40.5632 | 155.871 | 21.6718 | 98.81% | 3612.3582 | 99.46% | 99.48% | 85% |  |  | 99.43% | 1.0551
2021-12-27 | 200.0183 | 181.6333 | 181.6333 | 169.4996 | 156.6675 | 14.0811 | 14.0811 | 3467.2946 | 1039.6685 | 332.6939 | 611.3438 | 18.8671 | 9.0562 | 18.1124 | 43.017 | 8647.3492 | 419.8737 |  |  | 23.4827 | 1.0532 | 15.0303 | 4078.6384 | 2094.9321 | 1983.7062 | 944.0377 | 18.385 | 12.1337 | 12.5426 | 13.8127 | 11.1393 | 7.1292 | 3137.8557 | 6573.6284 | 10127.5941 | 2145.321 | 4439.8398 | 8096.1919 | 0.087605 | 0.084177 | 0.069054 | 17.9666 | 11.0156 | 11.5594 | 10.5632 | 22.8848 | 73.1145 | 166.0634 | 139.3767 | 108.7366 | 99.58% | 99.59% | 99.47% | 99.51% | 99.48% | 99.1% | 136.9779 | 142.557 | 173.7777 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 142.5727 | 12 | 24 | 57 | 25 | 98.77% | 0.08354 | 0.084797 | 43.0613 | 40.5416 | 154.667 | 22.2734 | 98.77% | 3404.3307 | 99.45% | 99.43% | 85.01% |  |  | 99.42% | 1.0532
2021-12-26 | 199.2322 | 180.7195 | 180.7195 | 168.4076 | 155.6252 | 14.2485 | 14.2485 | 3469.5644 | 1040.3491 | 332.9117 | 612.7554 | 18.8836 | 9.0641 | 18.1282 | 43.0545 | 8355.7551 | 418.1395 |  |  | 23.4296 | 1.0552 | 15.0434 | 4082.3197 | 2096.3035 | 1986.0162 | 945.6671 | 18.5127 | 12.3119 | 12.8222 | 13.8218 | 11.1466 | 7.1338 | 3028.1214 | 6339.481 | 9760.3473 | 2070.7285 | 4283.3104 | 7805.3962 | 0.088165 | 0.084621 | 0.069086 | 18.0645 | 11.1548 | 11.7825 | 10.9805 | 23.8007 | 76.093 | 165.419 | 138.9891 | 108.9562 | 99.56% | 99.58% | 99.45% | 99.47% | 99.44% | 99.03% | 136.1087 | 141.8088 | 173.6978 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 141.3722 | 12 | 24 | 57 | 25 | 98.72% | 0.083978 | 0.085271 | 43.6467 | 41.0018 | 154.2866 | 23.164 | 98.72% | 3284.4243 | 99.43% | 99.39% | 84.99% |  |  | 99.39% | 1.0552
2021-12-25 | 197.6092 | 179.2692 | 179.2692 | 167.2074 | 154.4081 | 14.3547 | 14.3547 | 3455.0282 | 1035.9905 | 331.517 | 609.4332 | 17.878 | 8.5815 | 17.1629 | 40.7619 | 8434.6054 | 412.5182 |  |  | 23.5584 | 1.0505 | 14.2424 | 4064.4614 | 2087.5208 | 1976.9406 | 940.9502 | 18.34 | 12.0618 | 12.6377 | 13.7639 | 11.0999 | 7.1039 | 3038.9902 | 6366.0359 | 9806.8321 | 2077.7271 | 4299.8114 | 7840.17 | 0.088305 | 0.084821 | 0.069449 | 18.0158 | 11.0058 | 11.7035 | 10.2718 | 22.2541 | 71.1058 | 163.7388 | 137.4704 | 107.4561 | 99.59% | 99.6% | 99.48% | 99.51% | 99.48% | 99.09% | 135.893 | 141.4739 | 172.7898 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 140.0541 | 12 | 24 | 57 | 25 | 98.79% | 0.084173 | 0.085451 | 43.0395 | 40.7251 | 152.6383 | 21.6597 | 98.79% | 3296.9373 | 99.46% | 99.43% | 85.01% |  |  | 99.43% | 1.0505
2021-12-24 | 198.5549 | 180.2386 | 180.2386 | 168.1371 | 155.4461 | 14.4116 | 14.4116 | 3446.8138 | 1033.5274 | 330.7288 | 610.0044 | 17.8338 | 8.5602 | 17.1205 | 40.6611 | 8418.6327 | 413.9813 |  |  | 23.5562 | 1.0506 | 14.2072 | 4056.8183 | 2082.5577 | 1974.2606 | 940.7332 | 18.3163 | 12.1016 | 12.6738 | 13.7311 | 11.0735 | 7.087 | 3036.4438 | 6353.594 | 9776.3044 | 2076.5874 | 4294.1005 | 7820.63 | 0.087617 | 0.084063 | 0.068635 | 18.0387 | 11.0585 | 11.7329 | 10.2284 | 22.1775 | 70.9435 | 164.6451 | 138.3914 | 108.4802 | 99.59% | 99.6% | 99.48% | 99.51% | 99.48% | 99.09% | 136.9603 | 142.7502 | 174.839 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 141.0555 | 12 | 24 | 57 | 25 | 98.8% | 0.083442 | 0.08473 | 43.0916 | 40.8302 | 153.5401 | 21.5844 | 98.8% | 3292.6614 | 99.46% | 99.43% | 84.96% |  |  | 99.44% | 1.0506
2021-12-23 | 198.3877 | 180.2425 | 180.2425 | 168.471 | 155.8915 | 14.7286 | 14.7286 | 3461.2893 | 1037.8679 | 332.1177 | 610.8047 | 22.0353 | 10.5769 | 21.1539 | 50.2405 | 9547.0724 | 414.8028 |  |  | 24.2509 | 1.0259 | 17.5542 | 4072.094 | 2091.3037 | 1980.7902 | 942.9224 | 18.1452 | 11.7716 | 12.4385 | 13.7888 | 11.12 | 7.1168 | 3445.9246 | 7215.5448 | 11111.593 | 2356.3755 | 4874.7062 | 8884.9455 | 0.086858 | 0.084276 | 0.070691 | 17.7737 | 10.7089 | 11.4818 | 10.9213 | 23.6698 | 75.6585 | 162.8575 | 135.3603 | 103.2791 | 99.55% | 99.57% | 99.43% | 99.54% | 99.51% | 99.15% | 138.1561 | 142.3887 | 169.7526 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 141.187 | 12 | 24 | 57 | 25 | 98.69% | 0.083445 | 0.084533 | 42.3552 | 39.9644 | 150.5506 | 23.0364 | 98.69% | 3737.9266 | 99.41% | 99.47% | 85% |  |  | 99.4% | 1.0259
2021-12-22 | 196.552 | 178.5191 | 178.5191 | 166.8704 | 154.178 | 14.3502 | 14.3502 | 3447.4752 | 1033.7257 | 330.7922 | 608.47 | 22.0932 | 10.6047 | 21.2095 | 50.3725 | 9497.2816 | 406.9017 |  |  | 24.6021 | 1.0136 | 17.6004 | 4055.9451 | 2082.9573 | 1972.9879 | 939.2622 | 18.0329 | 11.6487 | 12.3614 | 13.7338 | 11.0756 | 7.0884 | 3431.568 | 7184.9133 | 11063.5773 | 2346.6221 | 4854.228 | 8846.9135 | 0.086196 | 0.08367 | 0.07031 | 17.7691 | 10.6598 | 11.477 | 10.8211 | 23.4541 | 74.9751 | 161.5053 | 134.1795 | 102.1913 | 99.55% | 99.56% | 99.43% | 99.54% | 99.52% | 99.15% | 139.2171 | 143.4213 | 170.6717 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 139.9438 | 12 | 24 | 57 | 25 | 98.68% | 0.082846 | 0.083914 | 42.043 | 39.9059 | 149.2653 | 22.8264 | 98.68% | 3722.244 | 99.41% | 99.47% | 85% |  |  | 99.4% | 1.0136
2021-12-21 | 195.8579 | 177.6116 | 177.6116 | 165.7433 | 153.0709 | 14.2223 | 14.2223 | 3467.9625 | 988.5389 | 425.7825 | 611.7491 | 21.4584 | 10.4744 | 20.9489 | 47.6728 | 9117.463 | 407.7068 |  |  | 24.5987 | 1.0138 | 18.0272 | 4079.7117 | 2053.6412 | 2026.0705 | 1037.5316 | 18.2463 | 11.8683 | 12.5159 | 13.5405 | 10.5915 | 9.1239 | 3249.0149 | 6324.6503 | 10693.4784 | 2247.6327 | 4450.3554 | 8130.1428 | 0.085087 | 0.079354 | 0.088281 | 17.6411 | 10.0659 | 10.5639 | 11.003 | 24.1664 | 99.3962 | 161.3267 | 135.3081 | 104.7725 | 99.53% | 99.53% | 99.41% | 99.51% | 99.46% | 98.78% | 141.0322 | 151.2215 | 135.9293 |  |  |  | 30.5625 | 23.9062 | 20.5938 | 2383.875 | 1147.5 | 494.25 | 4025.625 | 138.8822 | 11.5625 | 23.125 | 52.625 | 23.6875 | 98.67% | 0.083763 | 0.083845 | 42.6305 | 38.2709 | 149.2973 | 23.0767 | 98.67% | 3597.7473 | 99.4% | 99.38% | 85.01% |  |  | 99.4% | 1.0138
2021-12-20 | 194.6021 | 176.3125 | 176.3125 | 164.4459 | 151.5664 | 14.182 | 14.182 | 3467.7492 | 809.9852 | 749.2363 | 611.3429 | 20.5758 | 10.8294 | 21.6587 | 40.0687 | 8637.0794 | 404.7992 |  |  | 24.391 | 1.021 | 19.6763 | 4079.0921 | 1908.5277 | 2170.5644 | 1360.5792 | 18.2896 | 11.8665 | 12.5293 | 12.5837 | 8.6784 | 16.0551 | 2895.4103 | 4606.223 | 10202.3112 | 2081.2453 | 3619.3775 | 6677.8808 | 0.079837 | 0.064109 | 0.14816 | 17.0758 | 8.1333 | 8.0891 | 11.4985 | 25.3517 | 180.2492 | 160.9232 | 138.2086 | 110.6351 | 99.48% | 99.4% | 99.4% | 99.45% | 99.3% | 97.3% | 150.3066 | 187.1814 | 80.9932 |  |  |  | 29 | 20 | 37 | 2262 | 960 | 888 | 4110 | 137.4591 | 10 | 20 | 37 | 19 | 98.67% | 0.085736 | 0.090925 | 42.6855 | 33.2981 | 149.0424 | 23.3484 | 98.67% | 3433.6587 | 99.4% | 99.06% | 85.01% |  |  | 99.39% | 1.021
2021-12-19 | 195.1838 | 176.8435 | 176.8435 | 164.8656 | 152.4039 | 14.1868 | 14.1868 | 3473.2542 | 811.271 | 750.4257 | 612.7665 | 20.7158 | 10.9031 | 21.8062 | 40.3414 | 8947.2482 | 407.4641 |  |  | 24.4833 | 1.0178 | 19.8102 | 4086.0207 | 1911.5574 | 2174.4632 | 1363.1922 | 18.3402 | 11.9779 | 12.702 | 12.6037 | 8.6922 | 16.0806 | 2993.2699 | 4761.6651 | 10543.6438 | 2151.6011 | 3741.6189 | 6902.3927 | 0.079613 | 0.064074 | 0.1486 | 17.0787 | 8.1869 | 8.1754 | 11.1807 | 24.6518 | 175.2985 | 161.1234 | 138.0687 | 110.1377 | 99.49% | 99.42% | 99.42% | 99.48% | 99.34% | 97.46% | 150.7294 | 187.2849 | 80.7554 |  |  |  | 29 | 20 | 37 | 2262 | 960 | 888 | 4110 | 138.1274 | 10 | 20 | 37 | 19 | 98.7% | 0.085678 | 0.090888 | 43.0201 | 33.441 | 148.8403 | 22.705 | 98.7% | 3549.4405 | 99.42% | 99.11% | 85% |  |  | 99.41% | 1.0178
2021-12-18 | 196.4625 | 178.1951 | 178.1951 | 166.3236 | 153.9185 | 14.2596 | 14.2596 | 3467.2058 | 1082.4826 | 322.6592 | 611.195 | 21.6661 | 11.2664 | 21.6661 | 57.1985 | 9451.2484 | 409.273 |  |  | 24.5727 | 1.0147 | 18.7877 | 4078.4008 | 2062.0641 | 2016.3368 | 933.8542 | 18.2675 | 11.8714 | 12.5618 | 13.596 | 11.598 | 6.9141 | 3377.9789 | 7268.469 | 11075.4087 | 2331.1832 | 4835.8888 | 8906.2736 | 0.085436 | 0.087868 | 0.069039 | 17.7096 | 10.6547 | 11.6934 | 11.4677 | 25.2095 | 82.571 | 161.4696 | 133.9286 | 101.6161 | 99.52% | 99.55% | 99.36% | 99.51% | 99.48% | 99.07% | 140.4558 | 136.5683 | 173.8145 |  |  |  | 31.03 | 26.47 | 15.78 | 2420.3401 | 1270.56 | 378.72 | 4069.62 | 139.5558 | 13 | 25 | 66 | 25 | 98.71% | 0.083591 | 0.08467 | 42.7007 | 40.0577 | 149.0798 | 22.5188 | 98.71% | 3725.0472 | 99.42% | 99.43% | 85.01% |  |  | 99.41% | 1.0147
2021-12-17 | 196.1877 | 178.0307 | 178.0307 | 166.1581 | 153.4553 | 14.1772 | 14.1772 | 3466.1668 | 1082.1582 | 322.5625 | 612.4103 | 21.6465 | 11.2562 | 21.6465 | 57.1469 | 9491.0178 | 407.1541 |  |  | 24.6331 | 1.0126 | 18.7707 | 4078.577 | 2061.4461 | 2017.131 | 934.9727 | 18.157 | 11.8726 | 12.5091 | 13.592 | 11.5946 | 6.9121 | 3392.3055 | 7293.581 | 11105.0814 | 2341.5023 | 4854.7375 | 8933.8304 | 0.085334 | 0.087777 | 0.069128 | 17.5983 | 10.6454 | 11.6181 | 11.38 | 25.0298 | 82.0481 | 161.2807 | 133.7517 | 101.2461 | 99.52% | 99.55% | 99.36% | 99.51% | 99.48% | 99.08% | 140.6232 | 136.7104 | 173.591 |  |  |  | 31.03 | 26.47 | 15.78 | 2420.3401 | 1270.56 | 378.72 | 4069.62 | 139.3859 | 13 | 25 | 66 | 25 | 98.71% | 0.083523 | 0.084589 | 42.5387 | 39.8617 | 148.8405 | 22.3579 | 98.71% | 3739.6335 | 99.42% | 99.44% | 84.98% |  |  | 99.41% | 1.0126
2021-12-16 | 197.3313 | 179.1218 | 179.1218 | 167.2517 | 154.5586 | 14.2891 | 14.2891 | 3471.6313 | 1083.8643 | 323.071 | 611.7442 | 21.2723 | 11.0616 | 21.2723 | 56.1588 | 9433.9013 | 409.5057 |  |  | 24.353 | 1.0223 | 18.4462 | 4083.3755 | 2064.696 | 2018.6795 | 934.8152 | 18.2095 | 11.87 | 12.5927 | 13.6134 | 11.6128 | 6.9229 | 3373.9137 | 7261.108 | 11066.1461 | 2328.2282 | 4830.4719 | 8897.9845 | 0.085721 | 0.088036 | 0.06911 | 17.6216 | 10.6356 | 11.705 | 11.3729 | 24.9974 | 81.8608 | 162.3516 | 134.8517 | 102.407 | 99.52% | 99.56% | 99.37% | 99.51% | 99.48% | 99.08% | 139.9893 | 136.3083 | 173.6371 |  |  |  | 31.03 | 26.47 | 15.78 | 2420.3401 | 1270.56 | 378.72 | 4069.62 | 140.2585 | 13 | 25 | 66 | 25 | 98.73% | 0.083804 | 0.084898 | 42.6722 | 39.9622 | 149.9533 | 22.3297 | 98.73% | 3720.8272 | 99.43% | 99.43% | 85.02% |  |  | 99.42% | 1.0223
2021-12-15 | 195.7703 | 177.7879 | 177.7879 | 166.0314 | 153.3093 | 14.1436 | 14.1436 | 3441.459 | 1035.9692 | 329.2677 | 607.1357 | 20.6195 | 9.9485 | 16.5901 | 36.9318 | 9172.9034 | 401.6212 |  |  | 24.1568 | 1.0292 | 14.5295 | 4048.5947 | 2076.2221 | 1972.3726 | 936.4034 | 17.9825 | 11.7565 | 12.554 | 13.6894 | 11.0997 | 7.0557 | 3341.7016 | 7020.365 | 10807.6879 | 2286.9245 | 4734.0985 | 8643.3697 | 0.087372 | 0.085137 | 0.070849 | 17.7546 | 10.7777 | 11.7033 | 10.5419 | 19.1411 | 56.8631 | 161.2506 | 134.1785 | 102.4945 | 99.56% | 99.65% | 99.57% | 99.54% | 99.6% | 99.34% | 137.344 | 140.9499 | 169.3754 |  |  |  | 31.0028 | 25.1378 | 15.9794 | 2418.2194 | 1206.615 | 383.505 | 4008.3394 | 139.1943 | 11.1875 | 18.6562 | 41.5312 | 23.1875 | 98.74% | 0.084013 | 0.085118 | 42.2929 | 40.2356 | 149.1821 | 22.1305 | 98.74% | 3631.7521 | 99.43% | 99.53% | 85% |  |  | 99.42% | 1.0292
2021-12-14 | 194.7465 | 176.4948 | 176.4948 | 164.6154 | 151.8157 | 14.2517 | 14.2517 | 3469.1055 | 1040.2116 | 332.8677 | 613.4522 | 20.7321 | 9.9154 | 16.2251 | 35.1544 | 9014.3788 | 402.7899 |  |  | 24.3648 | 1.0219 | 14.2291 | 4082.5578 | 2096.0263 | 1986.5315 | 946.3199 | 18.2517 | 11.8794 | 12.6036 | 13.82 | 11.1451 | 7.1329 | 3292.0589 | 6892.9133 | 10614.0285 | 2251.494 | 4656.9108 | 8487.3994 | 0.088176 | 0.085567 | 0.071669 | 17.8065 | 10.7565 | 11.5666 | 10.6975 | 18.9728 | 55.3291 | 160.161 | 133.1 | 101.7026 | 99.56% | 99.65% | 99.59% | 99.52% | 99.59% | 99.35% | 136.0912 | 140.2403 | 167.4353 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 137.5769 | 11 | 18 | 39 | 23 | 98.71% | 0.0847 | 0.08581 | 42.7347 | 40.1297 | 148.3046 | 22.6494 | 98.71% | 3571.1061 | 99.42% | 99.52% | 84.97% |  |  | 99.41% | 1.0219
2021-12-13 | 190.9232 | 172.6704 | 172.6704 | 160.8058 | 148.0629 | 14.2004 | 14.2004 | 3473.0641 | 1041.3985 | 333.2475 | 613.1672 | 21.6681 | 10.363 | 16.9576 | 36.7415 | 8762.7196 | 395.3634 |  |  | 24.9817 | 1.0006 | 14.8715 | 4086.2313 | 2098.418 | 1987.8133 | 946.4147 | 18.2528 | 11.8646 | 12.5288 | 13.8357 | 11.1578 | 7.141 | 3213.8988 | 6731.6905 | 10370.2987 | 2198.003 | 4547.0666 | 8290.5626 | 0.088373 | 0.085957 | 0.072202 | 17.7858 | 10.7355 | 11.5001 | 11.2271 | 19.9085 | 58.0342 | 156.6582 | 129.8872 | 98.9648 | 99.53% | 99.63% | 99.56% | 99.49% | 99.56% | 99.3% | 135.7884 | 139.6039 | 166.2005 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 133.9472 | 11 | 18 | 39 | 23 | 98.62% | 0.085013 | 0.086097 | 42.6462 | 40.0215 | 145.0559 | 23.7658 | 98.62% | 3486.9633 | 99.38% | 99.48% | 84.99% |  |  | 99.38% | 1.0006
2021-12-12 | 188.1944 | 170.5278 | 170.5278 | 159.0601 | 146.8124 | 14.2064 | 14.2064 | 3416.8777 | 1024.551 | 327.8563 | 602.0396 | 22.3186 | 10.6741 | 17.4667 | 37.8445 | 9157.5144 | 381.9236 |  |  | 25.1358 | 0.99539 | 15.3179 | 4018.9173 | 2064.4704 | 1954.447 | 929.8959 | 17.6666 | 11.4677 | 12.1503 | 13.6119 | 10.9773 | 7.0255 | 3334.861 | 6989.9366 | 10775.8794 | 2280.2959 | 4719.6532 | 8611.4851 | 0.088093 | 0.085986 | 0.07295 | 17.6517 | 10.6468 | 11.4559 | 10.9092 | 19.3352 | 56.3221 | 153.8066 | 127.0766 | 95.8616 | 99.53% | 99.63% | 99.56% | 99.52% | 99.59% | 99.35% | 136.2204 | 139.558 | 164.4955 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 132.5692 | 11 | 18 | 39 | 23 | 98.63% | 0.084996 | 0.086008 | 41.2846 | 39.7544 | 141.8653 | 23.082 | 98.63% | 3619.2278 | 99.38% | 99.52% | 85.02% |  |  | 99.4% | 0.99539
2021-12-11 | 188.6421 | 171.1246 | 171.1246 | 159.7546 | 147.4337 | 14.3079 | 14.3079 | 3413.562 | 1023.5568 | 327.5382 | 604.0092 | 22.9886 | 10.9946 | 17.9911 | 38.9807 | 9604.9651 | 383.051 |  |  | 25.2324 | 0.99213 | 15.7778 | 4017.5712 | 2062.467 | 1955.1042 | 931.5474 | 17.5175 | 11.37 | 12.0665 | 13.5987 | 10.9667 | 7.0187 | 3483.0682 | 7290.3929 | 11222.6416 | 2382.4628 | 4926.3821 | 8975.5464 | 0.087769 | 0.08595 | 0.073607 | 17.5057 | 10.5434 | 11.3367 | 10.7092 | 18.999 | 55.4237 | 153.7181 | 126.5897 | 94.6034 | 99.54% | 99.63% | 99.57% | 99.55% | 99.61% | 99.38% | 136.7224 | 139.6159 | 163.0283 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 133.1082 | 11 | 18 | 39 | 23 | 98.65% | 0.084921 | 0.085865 | 40.954 | 39.3859 | 141.3398 | 22.6799 | 98.65% | 3777.8769 | 99.39% | 99.54% | 84.97% |  |  | 99.41% | 0.99213
2021-12-10 | 190.9102 | 172.7077 | 172.7077 | 160.9342 | 148.5456 | 14.3488 | 14.3488 | 3471.4953 | 1040.9281 | 333.097 | 613.7725 | 23.2349 | 11.1123 | 18.1838 | 39.3982 | 9697.4062 | 396.4314 |  |  | 25.3079 | 0.9896 | 15.9468 | 4085.2678 | 2097.4702 | 1987.7976 | 946.8695 | 18.2024 | 11.7735 | 12.402 | 13.8295 | 11.1528 | 7.1378 | 3532.326 | 7395.5505 | 11387.7663 | 2415.9715 | 4996.6613 | 9106.2165 | 0.088046 | 0.086509 | 0.074308 | 17.741 | 10.6508 | 11.3721 | 10.8272 | 19.2044 | 56.0069 | 155.4359 | 127.5798 | 95.057 | 99.54% | 99.64% | 99.57% | 99.55% | 99.62% | 99.38% | 136.2917 | 138.7144 | 161.4894 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 134.1736 | 11 | 18 | 39 | 23 | 98.65% | 0.085356 | 0.086267 | 42.3779 | 39.7639 | 142.8869 | 22.9254 | 98.65% | 3831.7341 | 99.39% | 99.55% | 84.98% |  |  | 99.4% | 0.9896
2021-12-09 | 189.7336 | 171.9592 | 171.9592 | 160.5085 | 148.5419 | 14.0212 | 14.0212 | 3439.8197 | 1031.4302 | 330.0577 | 607.5773 | 27.1445 | 12.9821 | 21.2435 | 46.0276 | 10298.0291 | 388.3903 |  |  | 25.3452 | 0.98834 | 18.6301 | 4047.397 | 2078.3318 | 1969.0652 | 937.635 | 17.7744 | 11.4507 | 12.1666 | 13.7033 | 11.051 | 7.0727 | 3714.3538 | 7776.9 | 11976.5854 | 2540.7743 | 5254.221 | 9576.3743 | 0.087839 | 0.086651 | 0.075283 | 17.5689 | 10.5086 | 11.3237 | 11.9029 | 21.1147 | 61.573 | 154.1863 | 126.0478 | 92.8523 | 99.49% | 99.6% | 99.52% | 99.53% | 99.6% | 99.36% | 136.6136 | 138.4859 | 159.398 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 134.3441 | 11 | 18 | 39 | 23 | 98.5% | 0.08545 | 0.086278 | 41.3916 | 39.4012 | 141.083 | 25.2042 | 98.5% | 4029.4816 | 99.33% | 99.52% | 84.99% |  |  | 99.34% | 0.98834
2021-12-08 | 191.7535 | 173.6765 | 173.6765 | 162.0525 | 149.6283 | 14.2139 | 14.2139 | 3473.5161 | 1041.5341 | 333.2909 | 613.6656 | 23.8124 | 11.3885 | 18.6358 | 40.3776 | 9906.4071 | 397.6322 |  |  | 25.7335 | 0.97542 | 16.3432 | 4087.1817 | 2098.6912 | 1988.4906 | 946.9565 | 18.0771 | 11.624 | 12.3941 | 13.8375 | 11.1593 | 7.1419 | 3622.5178 | 7586.3386 | 11684.6621 | 2477.4911 | 5124.8222 | 9342.2928 | 0.086427 | 0.08496 | 0.073241 | 17.6075 | 10.5113 | 11.3651 | 10.672 | 18.9258 | 55.1795 | 156.1706 | 128.1197 | 95.117 | 99.54% | 99.64% | 99.57% | 99.57% | 99.63% | 99.41% | 138.8447 | 141.2432 | 163.8437 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 135.4254 | 11 | 18 | 39 | 23 | 98.65% | 0.083848 | 0.084722 | 42.0951 | 39.4839 | 143.3442 | 22.5929 | 98.65% | 3929.9852 | 99.39% | 99.56% | 84.99% |  |  | 99.41% | 0.97542
2021-12-07 | 190.55 | 172.4474 | 172.4474 | 160.7289 | 148.2369 | 14.1459 | 14.1459 | 3472.1701 | 1043.8575 | 312.7092 | 613.1342 | 22.6217 | 10.8191 | 17.7039 | 38.3585 | 9546.4219 | 394.7374 |  |  | 25.4811 | 0.9838 | 15.3691 | 4085.3043 | 2115.6034 | 1969.7009 | 925.8434 | 18.1027 | 11.7185 | 12.5546 | 13.949 | 11.1842 | 6.7009 | 3534.547 | 7499.6698 | 11305.0701 | 2405.0946 | 5029.1574 | 9143.538 | 0.088318 | 0.086376 | 0.069531 | 17.7228 | 10.8166 | 11.756 | 10.6181 | 18.5199 | 50.6838 | 155.3815 | 127.385 | 94.8111 | 99.55% | 99.65% | 99.58% | 99.56% | 99.63% | 99.45% | 135.8721 | 138.9278 | 172.584 |  |  |  | 30.2708 | 24.2708 | 14.5417 | 2361.125 | 1165 | 349 | 3875.125 | 134.1089 | 11 | 18 | 39 | 23 | 98.68% | 0.084691 | 0.086042 | 42.3758 | 40.2954 | 142.9185 | 22.3742 | 98.68% | 3800.856 | 99.4% | 99.56% | 84.99% |  |  | 99.41% | 0.9838
2021-12-06 | 186.8682 | 168.8627 | 168.8627 | 157.1056 | 144.6173 | 13.9198 | 13.9198 | 3451.9055 | 1038.8179 | 302.9886 | 609.8475 | 20.8179 | 9.9564 | 16.2923 | 35.3 | 8804.7356 | 382.2597 |  |  | 25.5149 | 0.98267 | 14.0876 | 4061.753 | 2110.099 | 1951.654 | 912.8361 | 18.0054 | 11.7571 | 12.3812 | 13.9127 | 11.1302 | 6.4926 | 3294.9605 | 7026.1226 | 10499.3506 | 2237.7468 | 4698.4633 | 8531.4599 | 0.08947 | 0.087043 | 0.067542 | 17.8108 | 11.0292 | 11.7802 | 10.4629 | 18.1339 | 48.3794 | 152.8067 | 125.6535 | 94.4609 | 99.56% | 99.65% | 99.59% | 99.53% | 99.61% | 99.43% | 134.1229 | 137.8622 | 177.6665 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 130.7585 | 11 | 18 | 39 | 23 | 98.69% | 0.085185 | 0.086815 | 42.1438 | 40.6203 | 141.1488 | 22.0111 | 98.69% | 3530.7021 | 99.41% | 99.54% | 84.99% |  |  | 99.42% | 0.98267
2021-12-05 | 189.2719 | 171.123 | 171.123 | 159.4619 | 146.9282 | 14.1762 | 14.1762 | 3473.1318 | 1045.2058 | 304.8517 | 614.1305 | 22.5952 | 10.8064 | 17.6832 | 38.3136 | 9461.8263 | 391.7556 |  |  | 25.66 | 0.97785 | 15.2903 | 4087.2623 | 2123.0743 | 1964.188 | 918.9822 | 18.1489 | 11.6611 | 12.5738 | 13.9983 | 11.1986 | 6.5325 | 3516.6954 | 7496.302 | 11198.4145 | 2388.5976 | 5013.8733 | 9101.0324 | 0.088809 | 0.086817 | 0.06817 | 17.7837 | 10.8329 | 11.8416 | 10.6518 | 18.4664 | 49.2833 | 154.1322 | 126.1352 | 93.7052 | 99.55% | 99.65% | 99.58% | 99.55% | 99.63% | 99.46% | 135.1218 | 138.2225 | 176.031 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 132.7844 | 11 | 18 | 39 | 23 | 98.67% | 0.084869 | 0.086398 | 42.3837 | 40.4582 | 141.8066 | 22.4139 | 98.67% | 3767.8284 | 99.4% | 99.56% | 84.97% |  |  | 99.41% | 0.97785
2021-12-04 | 189.9836 | 172.1199 | 172.1199 | 160.601 | 147.9571 | 14.2515 | 14.2515 | 3466.6819 | 1043.2648 | 304.2856 | 611.5042 | 23.2747 | 11.1314 | 18.215 | 39.4658 | 9851.9214 | 391.9053 |  |  | 25.8103 | 0.97289 | 15.7502 | 4078.186 | 2119.1316 | 1959.0545 | 915.7897 | 17.8636 | 11.519 | 12.4299 | 13.9723 | 11.1778 | 6.5204 | 3644.2214 | 7774.9564 | 11624.1504 | 2474.6452 | 5197.6854 | 9442.9269 | 0.087994 | 0.086163 | 0.068204 | 17.566 | 10.7474 | 11.7731 | 10.5174 | 18.222 | 48.5887 | 154.4827 | 126.2116 | 93.0102 | 99.55% | 99.65% | 99.58% | 99.57% | 99.65% | 99.49% | 136.3731 | 139.2702 | 175.9433 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 133.76 | 11 | 18 | 39 | 23 | 98.67% | 0.084242 | 0.085706 | 41.8125 | 40.0865 | 141.7556 | 22.1185 | 98.67% | 3905.7541 | 99.4% | 99.58% | 85.01% |  |  | 99.42% | 0.97289
2021-12-03 | 189.8319 | 171.8335 | 171.8335 | 160.2881 | 147.8609 | 14.3096 | 14.3096 | 3471.8991 | 1055.2757 | 305.672 | 612.4575 | 23.5196 | 11.2485 | 18.4066 | 39.881 | 9888.5927 | 392.7409 |  |  | 25.8995 | 0.96996 | 15.945 | 4084.3567 | 2110.9514 | 1973.4052 | 918.1295 | 17.9984 | 11.5454 | 12.481 | 13.9184 | 11.3065 | 6.5501 | 3638.6228 | 7799.6114 | 11672.4218 | 2478.8679 | 5200.3846 | 9477.1944 | 0.087559 | 0.087149 | 0.068627 | 17.6087 | 10.679 | 11.7833 | 10.5371 | 18.56 | 48.9972 | 154.185 | 125.8413 | 92.5784 | 99.55% | 99.65% | 99.58% | 99.57% | 99.64% | 99.48% | 137.0505 | 137.6958 | 174.8588 |  |  |  | 30.2234 | 24.5519 | 14.2234 | 2357.4281 | 1178.4907 | 341.3625 | 3877.2814 | 133.5394 | 11 | 18 | 39 | 23 | 98.67% | 0.084398 | 0.085767 | 42.0248 | 40.0709 | 141.3929 | 22.2238 | 98.67% | 3922.2113 | 99.4% | 99.58% | 85% |  |  | 99.42% | 0.96996
2021-12-02 | 186.6676 | 168.9936 | 168.9936 | 157.5979 | 145.4142 | 14.1961 | 14.1961 | 3432.3497 | 1077.1746 | 305.2063 | 606.8212 | 23.8843 | 11.4229 | 18.6921 | 40.4995 | 9799.1414 | 381.9734 |  |  | 25.8862 | 0.9704 | 16.2897 | 4039.1708 | 2049.9688 | 1989.2021 | 912.0275 | 17.6741 | 11.3956 | 12.1915 | 13.5163 | 11.5412 | 6.5401 | 3545.5854 | 7711.1179 | 11569.1256 | 2441.43 | 5099.5678 | 9380.6937 | 0.086584 | 0.090541 | 0.070043 | 17.418 | 10.4877 | 11.6437 | 10.5555 | 19.6281 | 50.215 | 151.4845 | 123.6953 | 90.609 | 99.53% | 99.63% | 99.57% | 99.57% | 99.62% | 99.46% | 138.5931 | 132.5362 | 171.3229 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 131.2004 | 11 | 18 | 39 | 23 | 98.64% | 0.085204 | 0.086355 | 41.2612 | 39.5493 | 138.7084 | 22.4908 | 98.64% | 3892.6765 | 99.39% | 99.57% | 84.98% |  |  | 99.41% | 0.9704
2021-12-01 | 187.9121 | 169.9489 | 169.9489 | 158.3604 | 145.9605 | 14.1378 | 14.1378 | 3470.1357 | 1089.033 | 308.5662 | 612.4678 | 23.6568 | 11.3141 | 18.514 | 40.1137 | 9816.7276 | 388.5058 |  |  | 26.125 | 0.9626 | 16.1345 | 4082.6035 | 2072.5364 | 2010.067 | 921.034 | 17.9632 | 11.5885 | 12.3131 | 13.6651 | 11.6682 | 6.6121 | 3547.7582 | 7720.7457 | 11590.3102 | 2442.5268 | 5104.1057 | 9394.9537 | 0.086179 | 0.090151 | 0.069753 | 17.4234 | 10.5025 | 11.5916 | 10.4804 | 19.4799 | 49.8045 | 152.6367 | 124.5889 | 91.2485 | 99.54% | 99.64% | 99.57% | 99.57% | 99.62% | 99.47% | 139.2455 | 133.1097 | 172.0357 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 131.8854 | 11 | 18 | 39 | 23 | 98.65% | 0.084822 | 0.085965 | 41.8648 | 39.5176 | 139.841 | 22.3216 | 98.65% | 3896.0237 | 99.39% | 99.57% | 85% |  |  | 99.42% | 0.9626
2021-11-30 | 187.6951 | 169.6433 | 169.6433 | 157.9421 | 145.7302 | 14.143 | 14.143 | 3472.2614 | 1089.7001 | 308.7552 | 613.6951 | 23.9154 | 11.4378 | 18.7164 | 40.5522 | 9803.781 | 387.6752 |  |  | 26.1467 | 0.9619 | 16.3109 | 4085.9564 | 2073.806 | 2012.1504 | 922.4503 | 18.0518 | 11.7012 | 12.4109 | 13.6734 | 11.6754 | 6.6162 | 3547.5652 | 7716.2308 | 11577.9303 | 2442.7343 | 5102.648 | 9387.3422 | 0.086319 | 0.090401 | 0.069967 | 17.4859 | 10.5857 | 11.6535 | 10.5928 | 19.6961 | 50.3837 | 152.3697 | 124.2301 | 90.9592 | 99.53% | 99.63% | 99.57% | 99.57% | 99.61% | 99.46% | 139.0185 | 132.742 | 171.5106 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 131.5886 | 11 | 18 | 39 | 23 | 98.64% | 0.085009 | 0.086146 | 42.1639 | 39.7252 | 139.5491 | 22.5687 | 98.64% | 3895.0133 | 99.39% | 99.57% | 84.98% |  |  | 99.41% | 0.9619
2021-11-29 | 185.8574 | 167.9177 | 167.9177 | 156.1444 | 143.7237 | 14.142 | 14.142 | 3472.8077 | 1089.8716 | 308.8038 | 611.9178 | 23.0544 | 11.026 | 18.0426 | 39.0922 | 9156.0401 | 384.355 |  |  | 26.1054 | 0.96324 | 15.7237 | 4084.7255 | 2074.1323 | 2010.5932 | 920.7216 | 17.9397 | 11.7733 | 12.4874 | 13.6756 | 11.6772 | 6.6172 | 3339.0863 | 7270.254 | 10919.4538 | 2298.6827 | 4804.9374 | 8848.822 | 0.087061 | 0.090742 | 0.069476 | 17.3893 | 10.6689 | 11.7656 | 10.8682 | 20.1948 | 51.6056 | 151.3072 | 123.9545 | 91.7434 | 99.52% | 99.62% | 99.56% | 99.53% | 99.58% | 99.42% | 137.8352 | 132.2424 | 172.7211 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 129.5324 | 11 | 18 | 39 | 23 | 98.6% | 0.085425 | 0.086652 | 42.2004 | 39.8238 | 139.0705 | 23.1407 | 98.6% | 3667.6625 | 99.37% | 99.53% | 85.02% |  |  | 99.39% | 0.96324
2021-11-28 | 185.2697 | 167.2836 | 167.2836 | 155.4764 | 143.1133 | 14.1544 | 14.1544 | 3469.4906 | 1088.8306 | 308.5089 | 611.2829 | 22.7807 | 10.8951 | 17.8283 | 38.6281 | 8992.4004 | 382.6589 |  |  | 26.1114 | 0.96304 | 15.537 | 4080.7735 | 2072.1512 | 2008.6223 | 919.7918 | 17.9861 | 11.8072 | 12.4372 | 13.6625 | 11.666 | 6.6109 | 3295.4363 | 7175.401 | 10777.2646 | 2268.6224 | 4742.179 | 8733.4774 | 0.087233 | 0.090894 | 0.069454 | 17.4597 | 10.7155 | 11.7363 | 10.8689 | 20.1956 | 51.6065 | 150.8336 | 123.6039 | 91.6662 | 99.52% | 99.62% | 99.56% | 99.52% | 99.57% | 99.41% | 137.5632 | 132.0212 | 172.7762 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 128.9071 | 11 | 18 | 39 | 23 | 98.6% | 0.08556 | 0.086801 | 42.2305 | 39.9115 | 138.7514 | 23.1417 | 98.6% | 3619.7571 | 99.37% | 99.52% | 85.02% |  |  | 99.39% | 0.96304
2021-11-27 | 186.1053 | 168.1243 | 168.1243 | 156.3644 | 143.8561 | 14.2223 | 14.2223 | 3470.5046 | 1089.1488 | 308.599 | 611.1457 | 23.3949 | 11.1889 | 18.3091 | 39.6696 | 9174.0221 | 384.1004 |  |  | 26.0603 | 0.96471 | 15.9559 | 4081.6504 | 2072.7568 | 2008.8936 | 919.7448 | 17.981 | 11.7599 | 12.4661 | 13.6665 | 11.6695 | 6.6128 | 3350.9969 | 7297.5189 | 10962.3816 | 2306.8125 | 4822.4603 | 8882.754 | 0.087074 | 0.090786 | 0.06959 | 17.4498 | 10.6714 | 11.7658 | 10.9993 | 20.4362 | 52.2127 | 151.4144 | 124.0013 | 91.6726 | 99.51% | 99.62% | 99.55% | 99.52% | 99.58% | 99.41% | 137.8142 | 132.1785 | 172.4394 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 129.5865 | 11 | 18 | 39 | 23 | 98.59% | 0.085464 | 0.086684 | 42.2071 | 39.8869 | 139.1549 | 23.4174 | 98.59% | 3681.0345 | 99.36% | 99.52% | 85.03% |  |  | 99.39% | 0.96471
2021-11-26 | 185.2 | 167.4176 | 167.4176 | 155.8411 | 143.3161 | 14.2167 | 14.2167 | 3450.1102 | 1082.7484 | 306.7855 | 609.5888 | 22.3426 | 10.6856 | 17.4855 | 37.8853 | 9240.2089 | 379.5386 |  |  | 26.0866 | 0.96385 | 15.2382 | 4059.699 | 2060.5762 | 1999.1228 | 916.3744 | 17.7824 | 11.5765 | 12.3062 | 13.5862 | 11.6009 | 6.574 | 3383.215 | 7360.0159 | 11044.9979 | 2329.4178 | 4866.6175 | 8954.5695 | 0.087012 | 0.090784 | 0.0698 | 17.3928 | 10.576 | 11.6711 | 10.3323 | 19.2091 | 49.1299 | 150.4984 | 123.167 | 90.7785 | 99.54% | 99.64% | 99.58% | 99.56% | 99.61% | 99.45% | 137.9127 | 132.1826 | 171.9196 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 129.0922 | 11 | 18 | 39 | 23 | 98.66% | 0.085465 | 0.086665 | 41.6651 | 39.64 | 138.1924 | 22.0111 | 98.66% | 3714.7793 | 99.4% | 99.56% | 84.98% |  |  | 99.42% | 0.96385
2021-11-25 | 188.7502 | 170.9553 | 170.9553 | 159.4179 | 147.1584 | 14.4525 | 14.4525 | 3445.7349 | 1081.3753 | 306.3965 | 607.8621 | 22.5888 | 10.8033 | 17.6782 | 38.3027 | 9875.3023 | 386.7387 |  |  | 25.9857 | 0.96714 | 15.4061 | 4053.597 | 2057.9631 | 1995.6339 | 914.2586 | 17.7949 | 11.5374 | 12.2629 | 13.569 | 11.5862 | 6.5656 | 3590.4384 | 7816.2612 | 11736.7873 | 2471.551 | 5166.2678 | 9512.3491 | 0.085718 | 0.08965 | 0.069424 | 17.4465 | 10.5707 | 11.6741 | 9.8665 | 18.3335 | 46.8587 | 153.0965 | 124.9911 | 91.4654 | 99.56% | 99.66% | 99.6% | 99.6% | 99.65% | 99.51% | 139.9938 | 133.8537 | 172.8506 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 132.6883 | 11 | 18 | 39 | 23 | 98.73% | 0.084369 | 0.085503 | 41.5952 | 39.6913 | 140.1521 | 21.0088 | 98.73% | 3943.3055 | 99.43% | 99.6% | 85% |  |  | 99.45% | 0.96714
2021-11-24 | 186.2698 | 168.2541 | 168.2541 | 156.6531 | 144.3636 | 14.5144 | 14.5144 | 3472.0282 | 1089.6269 | 308.7345 | 613.3264 | 23.4984 | 11.2384 | 18.39 | 39.8451 | 9795.2066 | 384.7959 |  |  | 26.4946 | 0.95068 | 16.0265 | 4085.3546 | 2073.6667 | 2011.6879 | 922.061 | 18.0157 | 11.6009 | 12.3426 | 13.6725 | 11.6746 | 6.6157 | 3561.2574 | 7747.9695 | 11628.063 | 2451.9538 | 5122.9062 | 9426.9034 | 0.086342 | 0.090664 | 0.070622 | 17.4556 | 10.4996 | 11.5981 | 10.2474 | 19.0501 | 48.7194 | 150.544 | 122.4167 | 89.0587 | 99.54% | 99.64% | 99.58% | 99.58% | 99.63% | 99.48% | 138.9824 | 132.3563 | 169.9195 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 129.9088 | 11 | 18 | 39 | 23 | 98.66% | 0.08521 | 0.086301 | 41.9593 | 39.5532 | 137.7128 | 21.829 | 98.66% | 3910.3951 | 99.4% | 99.58% | 84.99% |  |  | 99.43% | 0.95068
2021-11-23 | 184.5599 | 166.6418 | 166.6418 | 154.9992 | 142.5948 | 14.4837 | 14.4837 | 3472.9821 | 1089.9263 | 308.8193 | 613.7982 | 23.0345 | 11.0165 | 18.027 | 39.0586 | 9529.5934 | 381.1752 |  |  | 26.6343 | 0.94622 | 15.7101 | 4086.7803 | 2074.2365 | 2012.5438 | 922.6175 | 17.9182 | 11.6426 | 12.3511 | 13.6763 | 11.6778 | 6.6176 | 3471.852 | 7551.9986 | 11331.9725 | 2390.5226 | 4993.8753 | 9187.7185 | 0.086723 | 0.090977 | 0.070698 | 17.3513 | 10.5297 | 11.5943 | 10.2577 | 19.072 | 48.7845 | 149.2197 | 121.4576 | 88.57 | 99.54% | 99.64% | 99.57% | 99.57% | 99.62% | 99.47% | 138.371 | 131.902 | 169.7368 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 128.1321 | 11 | 18 | 39 | 23 | 98.66% | 0.08552 | 0.086633 | 41.9118 | 39.4753 | 136.6381 | 21.8538 | 98.66% | 3811.9432 | 99.4% | 99.57% | 84.98% |  |  | 99.43% | 0.94622
2021-11-22 | 183.2879 | 165.2081 | 165.2081 | 153.4725 | 141.076 | 14.3162 | 14.3162 | 3472.4908 | 1089.7721 | 308.7756 | 613.0247 | 22.7819 | 10.8957 | 17.8293 | 38.6302 | 9060.0246 | 377.8997 |  |  | 26.6124 | 0.94692 | 15.5379 | 4085.5155 | 2073.943 | 2011.5725 | 921.8004 | 18.0797 | 11.7357 | 12.5278 | 13.6743 | 11.6761 | 6.6166 | 3313.8746 | 7210.5298 | 10822.9581 | 2281.6793 | 4767.2662 | 8773.5629 | 0.08715 | 0.091166 | 0.070175 | 17.5174 | 10.6236 | 11.7785 | 10.6355 | 19.7712 | 50.5572 | 148.5779 | 121.2769 | 89.2834 | 99.52% | 99.63% | 99.56% | 99.53% | 99.59% | 99.42% | 137.694 | 131.6275 | 171.0022 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 126.7722 | 11 | 18 | 39 | 23 | 98.61% | 0.085719 | 0.086901 | 42.3432 | 39.9195 | 136.4643 | 22.6549 | 98.61% | 3638.9928 | 99.37% | 99.53% | 85% |  |  | 99.41% | 0.94692
2021-11-21 | 183.0488 | 165.4464 | 165.4464 | 154.0111 | 141.591 | 14.2286 | 14.2286 | 3439.676 | 1079.4738 | 305.8577 | 606.5988 | 23.7503 | 11.3588 | 18.5872 | 40.2722 | 9467.1068 | 373.576 |  |  | 26.5405 | 0.94922 | 16.1983 | 4046.2748 | 2054.3444 | 1991.9304 | 912.4565 | 17.6024 | 11.4353 | 12.2596 | 13.5451 | 11.5658 | 6.5541 | 3441.0852 | 7490.042 | 11246.3462 | 2369.0726 | 4951.0522 | 9115.1171 | 0.086738 | 0.090853 | 0.070537 | 17.305 | 10.507 | 11.7063 | 10.6033 | 19.7066 | 50.3736 | 148.2304 | 120.8378 | 88.1982 | 99.52% | 99.62% | 99.56% | 99.55% | 99.6% | 99.45% | 138.3471 | 132.0819 | 170.1229 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 127.3618 | 11 | 18 | 39 | 23 | 98.6% | 0.085463 | 0.086589 | 41.2973 | 39.5183 | 135.729 | 22.5811 | 98.6% | 3779.2372 | 99.37% | 99.55% | 85.01% |  |  | 99.41% | 0.94922
2021-11-20 | 184.1383 | 166.2509 | 166.2509 | 154.7882 | 142.2676 | 14.2603 | 14.2603 | 3471.4931 | 1089.459 | 308.6869 | 612.2309 | 24.1034 | 11.5277 | 18.8635 | 40.8709 | 9693.2547 | 379.5331 |  |  | 26.4395 | 0.95245 | 16.4391 | 4083.724 | 2073.3471 | 2010.3769 | 920.9179 | 17.8874 | 11.4627 | 12.2672 | 13.6704 | 11.6728 | 6.6147 | 3518.8658 | 7659.4186 | 11500.6914 | 2422.5944 | 5062.985 | 9321.252 | 0.087456 | 0.091853 | 0.071702 | 17.3438 | 10.3875 | 11.5524 | 10.6567 | 19.8055 | 50.6261 | 148.8789 | 121.0386 | 87.8657 | 99.52% | 99.63% | 99.56% | 99.56% | 99.61% | 99.46% | 137.2117 | 130.644 | 167.3584 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 127.999 | 11 | 18 | 39 | 23 | 98.61% | 0.086342 | 0.087435 | 41.6173 | 39.2837 | 136.1929 | 22.6945 | 98.61% | 3864.6606 | 99.38% | 99.56% | 85.01% |  |  | 99.41% | 0.95245
2021-11-19 | 183.707 | 165.8242 | 165.8242 | 154.265 | 141.7777 | 14.4926 | 14.4926 | 3470.9082 | 1089.2755 | 308.6349 | 613.9092 | 24.5425 | 11.7377 | 19.2072 | 41.6156 | 9679.0764 | 379.1143 |  |  | 26.5559 | 0.94872 | 16.7386 | 4084.8175 | 2072.9979 | 2011.8196 | 922.5441 | 17.8828 | 11.5592 | 12.3627 | 13.6681 | 11.6708 | 6.6136 | 3515.8223 | 7644.3803 | 11466.5718 | 2421.1896 | 5056.1811 | 9298.5889 | 0.087483 | 0.091988 | 0.071919 | 17.3285 | 10.4585 | 11.6048 | 10.8129 | 20.1112 | 51.4634 | 148.2258 | 120.3672 | 87.2439 | 99.52% | 99.62% | 99.55% | 99.55% | 99.6% | 99.45% | 137.1692 | 130.4514 | 166.8547 |  |  |  | 31 | 26.47 | 15 | 2418 | 1270.56 | 360 | 4048.56 | 127.2913 | 11 | 18 | 39 | 23 | 98.59% | 0.086435 | 0.087513 | 41.8047 | 39.3919 | 135.5109 | 23.0435 | 98.59% | 3859.6711 | 99.36% | 99.55% | 84.97% |  |  | 99.4% | 0.94872
2021-11-18 | 182.7412 | 164.9855 | 164.9855 | 153.4629 | 141.033 | 14.259 | 14.259 | 3460.1326 | 1052.6995 | 329.2204 | 610.5513 | 24.6304 | 11.5135 | 21.6651 | 57.3261 | 9709.9813 | 374.4161 |  |  | 26.5464 | 0.94903 | 18.9609 | 4070.6838 | 2078.2126 | 1992.4713 | 939.7717 | 17.7557 | 11.5226 | 12.3134 | 13.7025 | 11.2789 | 7.0547 | 3533.5342 | 7467.4076 | 11463.0594 | 2424.9223 | 5018.8604 | 9181.559 | 0.088141 | 0.089215 | 0.076631 | 17.3481 | 10.4367 | 11.4038 | 10.62 | 22.0931 | 76.6084 | 147.5373 | 119.9792 | 87.3678 | 99.53% | 99.57% | 99.38% | 99.56% | 99.56% | 99.17% | 136.146 | 134.5059 | 156.5937 |  |  |  | 30.2747 | 24.92 | 15.5869 | 2361.4286 | 1196.16 | 374.0862 | 3931.6747 | 126.8244 | 13.0989 | 24.6484 | 65.2198 | 28.022 | 98.58% | 0.086643 | 0.087373 | 41.5917 | 39.1885 | 134.8437 | 23.0778 | 98.58% | 3856.9658 | 99.36% | 99.5% | 85% |  |  | 99.4% | 0.94903
2021-11-17 | 183.0567 | 165.2184 | 165.2184 | 153.6896 | 141.2221 | 14.2756 | 14.2756 | 3469.4899 | 1039.3039 | 329.2658 | 613.2341 | 24.9258 | 11.0781 | 20.0791 | 54.6982 | 9691.0918 | 375.7105 |  |  | 26.669 | 0.94512 | 17.9141 | 4082.7239 | 2100.9202 | 1981.8037 | 942.4999 | 17.8383 | 11.5288 | 12.4772 | 13.8522 | 11.1354 | 7.0557 | 3563.8246 | 7471.5475 | 11453.901 | 2434.2166 | 5044.1966 | 9180.876 | 0.088612 | 0.08766 | 0.076168 | 17.4229 | 10.4849 | 11.4952 | 10.2483 | 20.0309 | 72.8112 | 147.7463 | 120.0579 | 87.5494 | 99.54% | 99.6% | 99.4% | 99.58% | 99.6% | 99.21% | 135.4225 | 136.8921 | 157.5458 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 126.9429 | 16 | 29 | 79 | 36 | 98.56% | 0.086316 | 0.087146 | 41.8443 | 39.403 | 135.0886 | 23.3252 | 98.56% | 3856.3296 | 99.35% | 99.53% | 84.98% |  |  | 99.39% | 0.94512
2021-11-16 | 180.0943 | 162.5783 | 162.5783 | 151.2651 | 138.8629 | 14.18 | 14.18 | 3431.4856 | 1027.9195 | 325.6591 | 607.2424 | 25.326 | 11.256 | 20.4015 | 55.5764 | 9536.2552 | 364.8698 |  |  | 26.6634 | 0.9453 | 18.2017 | 4038.728 | 2077.907 | 1960.821 | 932.9015 | 17.516 | 11.3132 | 12.1961 | 13.7005 | 11.0134 | 6.9784 | 3519.4969 | 7374.9827 | 11300.3197 | 2404.3212 | 4980.3795 | 9060.1535 | 0.0892 | 0.088272 | 0.07683 | 17.3868 | 10.4524 | 11.4073 | 10.4288 | 20.3913 | 74.1587 | 145.191 | 117.9418 | 85.8611 | 99.53% | 99.59% | 99.39% | 99.57% | 99.59% | 99.18% | 134.5289 | 135.9432 | 156.1895 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 124.7356 | 16 | 29 | 79 | 36 | 98.52% | 0.086924 | 0.087748 | 41.0253 | 39.2464 | 132.7171 | 23.7442 | 98.52% | 3807.653 | 99.33% | 99.51% | 84.96% |  |  | 99.38% | 0.9453
2021-11-15 | 178.0938 | 160.38 | 160.38 | 148.8134 | 136.4071 | 14.2159 | 14.2159 | 3444.6452 | 1031.8615 | 326.908 | 609.4893 | 23.9639 | 10.6506 | 19.3042 | 52.5874 | 8897.9119 | 361.5833 |  |  | 26.9254 | 0.93701 | 17.2228 | 4054.1345 | 2085.8757 | 1968.2588 | 936.3973 | 17.7138 | 11.5666 | 12.3632 | 13.753 | 11.0557 | 7.0052 | 3312.2431 | 6940.8917 | 10635.5282 | 2262.7334 | 4687.1581 | 8527.0019 | 0.08964 | 0.08851 | 0.076305 | 17.4832 | 10.6262 | 11.4992 | 10.4333 | 20.3999 | 74.1875 | 143.7606 | 117.0415 | 86.0223 | 99.53% | 99.59% | 99.38% | 99.54% | 99.56% | 99.13% | 133.8681 | 135.5785 | 157.2635 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 122.2322 | 16 | 29 | 79 | 36 | 98.51% | 0.087145 | 0.088036 | 41.6436 | 39.6086 | 131.8762 | 23.7541 | 98.51% | 3583.4818 | 99.33% | 99.48% | 84.97% |  |  | 99.38% | 0.93701
2021-11-14 | 178.5049 | 160.8298 | 160.8298 | 149.3361 | 137.3486 | 14.2084 | 14.2084 | 3442.0875 | 1031.0953 | 326.6652 | 606.5373 | 24.8294 | 11.0353 | 20.0014 | 54.4867 | 9334.7443 | 361.9585 |  |  | 27.1135 | 0.93112 | 17.8448 | 4048.6249 | 2084.327 | 1964.2979 | 933.2026 | 17.6751 | 11.4937 | 12.2978 | 13.7428 | 11.0475 | 7 | 3449.6388 | 7239.0445 | 11108.4607 | 2355.7141 | 4884.6192 | 8899.2708 | 0.089026 | 0.088257 | 0.076761 | 17.4862 | 10.5984 | 11.507 | 10.3105 | 20.1397 | 73.134 | 143.7355 | 116.5514 | 84.91 | 99.53% | 99.59% | 99.39% | 99.56% | 99.59% | 99.18% | 134.7921 | 135.9663 | 156.3286 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 123.1079 | 16 | 29 | 79 | 36 | 98.52% | 0.086818 | 0.087632 | 41.4667 | 39.5916 | 131.4309 | 23.4523 | 98.52% | 3734.2656 | 99.34% | 99.51% | 85.02% |  |  | 99.39% | 0.93112
2021-11-13 | 179.2707 | 161.7205 | 161.7205 | 150.3712 | 138.0875 | 14.2484 | 14.2484 | 3446.256 | 1032.344 | 327.0608 | 607.8688 | 26.4565 | 11.7585 | 21.3122 | 58.0574 | 9559.6839 | 364.3495 |  |  | 27.2774 | 0.92602 | 19.0143 | 4054.1248 | 2086.8512 | 1967.2737 | 934.9296 | 17.5502 | 11.3494 | 12.2917 | 13.7595 | 11.0608 | 7.0084 | 3547.8888 | 7441.9148 | 11414.7632 | 2423.1834 | 5022.7601 | 9146.8051 | 0.088366 | 0.0877 | 0.07677 | 17.3259 | 10.4398 | 11.4671 | 10.6346 | 20.7801 | 75.4937 | 144.1901 | 116.7902 | 84.5372 | 99.51% | 99.58% | 99.37% | 99.56% | 99.59% | 99.17% | 135.799 | 136.8299 | 156.3106 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 123.845 | 16 | 29 | 79 | 36 | 98.47% | 0.086298 | 0.087066 | 41.1912 | 39.2328 | 131.5851 | 24.1973 | 98.47% | 3839.9936 | 99.31% | 99.51% | 85.01% |  |  | 99.37% | 0.92602
2021-11-12 | 180.2033 | 162.6019 | 162.6019 | 151.2897 | 138.9568 | 14.218 | 14.218 | 3447.1669 | 1032.6169 | 327.1473 | 608.4553 | 27 | 12 | 21.75 | 59.25 | 9333 | 366.5499 |  |  | 27.2709 | 0.92622 | 19.4048 | 4055.6222 | 2087.4027 | 1968.2195 | 935.6026 | 17.6014 | 11.3121 | 12.2211 | 13.7631 | 11.0638 | 7.0103 | 3593.62 | 7535.8636 | 11555.8036 | 2454.6057 | 5086.9169 | 9261.137 | 0.087932 | 0.087285 | 0.076483 | 17.366 | 10.3969 | 11.3872 | 10.7193 | 20.9496 | 76.1301 | 144.9716 | 117.402 | 84.8958 | 99.51% | 99.57% | 99.36% | 99.56% | 99.59% | 99.18% | 136.4689 | 137.4802 | 156.8978 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 124.7663 | 16 | 29 | 79 | 36 | 98.46% | 0.085893 | 0.086652 | 41.1346 | 39.1501 | 132.2657 | 24.3944 | 98.46% | 3889.0901 | 99.31% | 99.51% | 85% |  |  | 99.36% | 0.92622
2021-11-11 | 180.2357 | 162.819 | 162.819 | 151.6123 | 139.6774 | 14.2311 | 14.2311 | 3420.3813 | 1024.5931 | 324.6052 | 603.0431 | 27 | 12 | 21.75 | 59.25 | 9333 | 363.1528 |  |  | 27.0184 | 0.93409 | 19.4048 | 4023.4244 | 2071.1829 | 1952.2415 | 927.6484 | 17.4167 | 11.2067 | 12.0095 | 13.6562 | 10.9778 | 6.9558 | 3690.6508 | 7742.9736 | 11878.9583 | 2520.4986 | 5225.3446 | 9517.7338 | 0.088123 | 0.087668 | 0.077238 | 17.392 | 10.4287 | 11.337 | 10.446 | 20.4082 | 74.1269 | 144.7538 | 116.9666 | 84.1213 | 99.52% | 99.58% | 99.38% | 99.59% | 99.61% | 99.22% | 136.1734 | 136.8793 | 155.3631 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 125.4175 | 16 | 29 | 79 | 36 | 98.5% | 0.086236 | 0.086954 | 40.6329 | 39.1576 | 131.7761 | 23.7646 | 98.5% | 3994.8096 | 99.32% | 99.53% | 85.01% |  |  | 99.38% | 0.93409
2021-11-10 | 181.6648 | 164.1237 | 164.1237 | 152.8219 | 140.541 | 14.2798 | 14.2798 | 3439.785 | 1030.4056 | 326.4467 | 608.1708 | 27.2151 | 12.0956 | 21.9233 | 59.7221 | 9468.6894 | 369.2621 |  |  | 26.7735 | 0.94181 | 19.5595 | 4047.9557 | 2082.9327 | 1965.0231 | 934.6175 | 17.5412 | 11.3017 | 12.215 | 13.7336 | 11.0401 | 6.9953 | 3692.0041 | 7738.2282 | 11859.806 | 2522.0863 | 5225.0138 | 9507.4813 | 0.088553 | 0.087983 | 0.07736 | 17.3534 | 10.4098 | 11.3956 | 10.6697 | 20.8597 | 75.8436 | 146.0645 | 118.1776 | 85.1629 | 99.52% | 99.58% | 99.37% | 99.58% | 99.6% | 99.2% | 135.5123 | 136.3901 | 155.1187 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 126.2608 | 16 | 29 | 79 | 36 | 98.49% | 0.08658 | 0.08732 | 41.0579 | 39.1588 | 133.0503 | 24.2894 | 98.49% | 3994.6989 | 99.32% | 99.52% | 84.98% |  |  | 99.36% | 0.94181
2021-11-09 | 182.9594 | 165.0873 | 165.0873 | 153.5006 | 141.0373 | 14.3977 | 14.3977 | 3470.9664 | 1048.7084 | 332.2453 | 612.8559 | 27.994 | 12.4418 | 22.5507 | 61.4313 | 9461.342 | 376.8909 |  |  | 26.5706 | 0.94825 | 20.1854 | 4083.8223 | 2090.0128 | 1993.8095 | 945.1011 | 17.8721 | 11.5867 | 12.4577 | 13.7803 | 11.2362 | 7.1195 | 3567.3304 | 7500.7084 | 11533.7363 | 2444.9781 | 5055.614 | 9229.7744 | 0.088614 | 0.088989 | 0.077573 | 17.3994 | 10.4591 | 11.4527 | 11.4374 | 22.7239 | 82.3486 | 147.463 | 119.731 | 87.0295 | 99.49% | 99.55% | 99.33% | 99.53% | 99.55% | 99.11% | 135.4195 | 134.8483 | 154.6933 |  |  |  | 30.5625 | 24.92 | 15.79 | 2383.875 | 1196.16 | 378.96 | 3958.995 | 126.6178 | 16 | 29 | 79 | 36 | 98.4% | 0.086967 | 0.08767 | 41.9165 | 39.3113 | 134.6779 | 26.1124 | 98.4% | 3883.1978 | 99.28% | 99.47% | 84.99% |  |  | 99.32% | 0.94825
2021-11-08 | 179.8046 | 162.1024 | 162.1024 | 150.5814 | 138.0838 | 14.3954 | 14.3954 | 3447.2182 | 1053.2051 | 333.6699 | 609.5083 | 27.5113 | 12.2273 | 22.1619 | 60.3721 | 8963.416 | 367.4988 |  |  | 26.5574 | 0.94868 | 19.9227 | 4056.7265 | 2060.3431 | 1996.3834 | 943.1782 | 17.7022 | 11.5209 | 12.3231 | 13.5847 | 11.2843 | 7.1501 | 3380.0642 | 7129.6841 | 10999.7164 | 2327.0371 | 4796.9308 | 8786.7653 | 0.088889 | 0.090666 | 0.078594 | 17.3389 | 10.3963 | 11.3867 | 11.6475 | 23.6479 | 85.4116 | 144.9841 | 118.0727 | 86.3053 | 99.47% | 99.54% | 99.31% | 99.5% | 99.51% | 99.03% | 135.0002 | 132.3539 | 152.683 |  |  |  | 30 | 24.92 | 15.79 | 2340 | 1196.16 | 378.96 | 3915.12 | 123.6418 | 16 | 29 | 79 | 36 | 98.35% | 0.08781 | 0.088435 | 41.5463 | 39.1219 | 132.6773 | 26.7106 | 98.35% | 3706.9097 | 99.26% | 99.43% | 84.98% |  |  | 99.3% | 0.94868
2021-11-07 | 179.7346 | 162.1551 | 162.1551 | 150.7462 | 138.3642 | 14.3098 | 14.3098 | 3441.3618 | 1051.4159 | 333.1031 | 607.9254 | 28.0804 | 12.4802 | 22.6203 | 61.6208 | 9285.6727 | 365.7393 |  |  | 26.7019 | 0.94407 | 20.3347 | 4049.2872 | 2056.8429 | 1992.4443 | 941.0284 | 17.5796 | 11.4089 | 12.3189 | 13.5616 | 11.2652 | 7.1379 | 3482.7778 | 7348.8295 | 11341.74 | 2397.519 | 4943.4341 | 9058.299 | 0.088475 | 0.090484 | 0.079036 | 17.2674 | 10.3272 | 11.424 | 11.4634 | 23.2685 | 84.0119 | 144.7099 | 117.5368 | 85.262 | 99.48% | 99.54% | 99.32% | 99.52% | 99.53% | 99.07% | 135.6319 | 132.6205 | 151.8303 |  |  |  | 30 | 24.92 | 15.79 | 2340 | 1196.16 | 378.96 | 3915.12 | 124.0102 | 16 | 29 | 79 | 36 | 98.37% | 0.087607 | 0.088175 | 41.3074 | 39.0187 | 132.0714 | 26.2824 | 98.37% | 3820.0784 | 99.26% | 99.45% | 84.99% |  |  | 99.31% | 0.94407
2021-11-06 | 181.0869 | 163.5449 | 163.5449 | 152.1728 | 139.8199 | 14.3721 | 14.3721 | 3441.934 | 1051.5907 | 333.1585 | 608.0315 | 29.5873 | 13.1499 | 23.8342 | 64.9276 | 9734.5479 | 368.6659 |  |  | 26.6954 | 0.94428 | 21.426 | 4049.9655 | 2057.1849 | 1992.7806 | 941.1899 | 17.5421 | 11.3721 | 12.2909 | 13.5639 | 11.267 | 7.1391 | 3630.9444 | 7661.1656 | 11823.3694 | 2499.5724 | 5153.6517 | 9443.1377 | 0.088021 | 0.090288 | 0.07956 | 17.2263 | 10.2913 | 11.3951 | 11.5899 | 23.5262 | 84.9456 | 145.5117 | 117.8377 | 84.7332 | 99.47% | 99.54% | 99.31% | 99.54% | 99.54% | 99.1% | 136.3307 | 132.9086 | 150.8303 |  |  |  | 30 | 24.92 | 15.79 | 2340 | 1196.16 | 378.96 | 3915.12 | 125.4756 | 16 | 29 | 79 | 36 | 98.35% | 0.087393 | 0.087895 | 41.2051 | 38.9127 | 132.4064 | 26.5733 | 98.35% | 3982.5505 | 99.26% | 99.47% | 84.99% |  |  | 99.3% | 0.94428
2021-11-05 | 180.9725 | 163.5554 | 163.5554 | 152.3334 | 139.9682 | 14.513 | 14.513 | 3434.8377 | 1049.4226 | 332.4716 | 606.199 | 30.1877 | 13.4167 | 24.3178 | 66.2451 | 9818.3265 | 368.1859 |  |  | 26.7723 | 0.94184 | 21.8607 | 4041.0367 | 2052.9435 | 1988.0932 | 938.6705 | 17.4171 | 11.222 | 12.1302 | 13.5359 | 11.2438 | 7.1244 | 3639.6052 | 7681.454 | 11858.0374 | 2505.4223 | 5166.5385 | 9469.389 | 0.087746 | 0.089958 | 0.079294 | 17.1615 | 10.193 | 11.2937 | 11.7427 | 23.8327 | 86.0281 | 145.2909 | 117.7203 | 84.6221 | 99.46% | 99.53% | 99.3% | 99.53% | 99.54% | 99.09% | 136.7584 | 133.3952 | 151.3347 |  |  |  | 30 | 24.92 | 15.79 | 2340 | 1196.16 | 378.96 | 3915.12 | 125.4467 | 16 | 29 | 79 | 36 | 98.32% | 0.087102 | 0.087604 | 40.7693 | 38.6481 | 132.1978 | 26.9193 | 98.32% | 3992.525 | 99.24% | 99.46% | 85% |  |  | 99.3% | 0.94184
2021-11-04 | 182.0236 | 164.2654 | 164.2654 | 152.8364 | 140.3438 | 14.593 | 14.593 | 3468.6385 | 1040.7429 | 329.7217 | 612.2128 | 29.7164 | 12.0165 | 24.6825 | 65.3598 | 9708.8939 | 374.471 |  |  | 26.8184 | 0.94039 | 20.8875 | 4080.8513 | 2098.1738 | 1982.6775 | 941.9345 | 17.7582 | 11.4289 | 12.277 | 13.8341 | 11.1508 | 7.0655 | 3627.4151 | 7608.0723 | 11670.3791 | 2479.1889 | 5135.1521 | 9351.3094 | 0.088974 | 0.088561 | 0.077649 | 17.3489 | 10.3924 | 11.3281 | 10.8458 | 24.0992 | 85.1072 | 146.2156 | 118.4055 | 85.5673 | 99.52% | 99.52% | 99.3% | 99.56% | 99.53% | 99.09% | 134.8708 | 135.5005 | 154.5407 |  |  |  | 30.9167 | 24.92 | 15.79 | 2411.5 | 1196.16 | 378.96 | 3986.62 | 125.7449 | 12.3333 | 25.3333 | 67.0833 | 30.5 | 98.32% | 0.08703 | 0.087773 | 41.4641 | 39.0695 | 133.3822 | 27.148 | 98.32% | 3929.3436 | 99.24% | 99.48% | 85% |  |  | 99.29% | 0.94039
2021-11-03 | 181.3266 | 163.5735 | 163.5735 | 151.9433 | 139.4096 | 14.5631 | 14.5631 | 3471.047 | 1039.7703 | 329.4136 | 614.4593 | 28.7999 | 11.52 | 23.9999 | 63.3597 | 9564.1724 | 373.2827 |  |  | 26.9586 | 0.93597 | 20.1782 | 4085.5063 | 2101.8631 | 1983.6432 | 943.8729 | 17.7531 | 11.6302 | 12.4375 | 13.8584 | 11.1404 | 7.0589 | 3586.3726 | 7510.682 | 11503.2149 | 2450.1034 | 5073.6989 | 9224.9861 | 0.089029 | 0.088405 | 0.07745 | 17.3198 | 10.5597 | 11.43 | 10.4901 | 23.5831 | 83.1621 | 145.6941 | 117.9469 | 85.3053 | 99.53% | 99.53% | 99.31% | 99.57% | 99.54% | 99.1% | 134.7868 | 135.7393 | 154.9391 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 124.8744 | 12 | 25 | 66 | 30 | 98.35% | 0.086977 | 0.087743 | 41.8207 | 39.3095 | 132.9323 | 26.5456 | 98.35% | 3878.9734 | 99.26% | 99.48% | 84.96% |  |  | 99.31% | 0.93597
2021-11-02 | 179.9511 | 162.0719 | 162.0719 | 150.4606 | 137.9415 | 14.4192 | 14.4192 | 3471.0116 | 1039.7597 | 329.4102 | 612.5301 | 27.9525 | 11.181 | 23.2938 | 61.4956 | 9259.7784 | 369.404 |  |  | 26.9009 | 0.93779 | 19.5845 | 4083.5417 | 2101.8416 | 1981.7 | 941.9404 | 17.8792 | 11.6113 | 12.5314 | 13.8583 | 11.1403 | 7.0588 | 3481.8497 | 7299.5722 | 11192.1095 | 2378.0355 | 4928.1362 | 8970.2441 | 0.089778 | 0.089047 | 0.07766 | 17.4597 | 10.5635 | 11.5593 | 10.5103 | 23.6109 | 83.1678 | 144.758 | 117.3228 | 85.2381 | 99.53% | 99.53% | 99.31% | 99.56% | 99.52% | 99.07% | 133.6627 | 134.7609 | 154.5187 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 123.5465 | 12 | 25 | 66 | 30 | 98.35% | 0.087605 | 0.088409 | 42.0219 | 39.5825 | 132.3217 | 26.5778 | 98.35% | 3767.5534 | 99.26% | 99.47% | 85% |  |  | 99.3% | 0.93779
2021-11-01 | 175.4403 | 157.9478 | 157.9478 | 146.5644 | 134.2235 | 13.9345 | 13.9345 | 3421.3893 | 1024.8951 | 324.7009 | 604.4746 | 27.1016 | 10.8406 | 22.5847 | 59.6236 | 8808.4664 | 351.8307 |  |  | 26.8351 | 0.93986 | 18.9883 | 4025.8639 | 2071.7933 | 1954.0706 | 929.1755 | 17.4925 | 11.3835 | 12.2758 | 13.6602 | 10.981 | 6.9579 | 3327.4982 | 6972.8692 | 10686.4034 | 2272.9124 | 4708.7485 | 8566.9854 | 0.090765 | 0.08983 | 0.077922 | 17.4489 | 10.5746 | 11.5549 | 10.5324 | 23.6684 | 83.4085 | 141.4493 | 114.8908 | 83.9227 | 99.52% | 99.52% | 99.3% | 99.54% | 99.5% | 99.03% | 132.2097 | 133.5862 | 154.0003 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 120.2664 | 12 | 25 | 66 | 30 | 98.33% | 0.088411 | 0.089266 | 41.1518 | 39.5785 | 129.5222 | 26.642 | 98.33% | 3599.9078 | 99.25% | 99.44% | 84.99% |  |  | 99.3% | 0.93986
2021-10-31 | 176.2117 | 158.7419 | 158.7419 | 147.3988 | 135.1199 | 14.228 | 14.228 | 3430.4747 | 1027.6167 | 325.5631 | 605.0946 | 27.3296 | 10.9318 | 22.7747 | 60.1251 | 9161.9659 | 356.5042 |  |  | 27.0238 | 0.93392 | 19.148 | 4035.5693 | 2077.2949 | 1958.2744 | 930.6578 | 17.4698 | 11.3432 | 12.217 | 13.6964 | 11.0102 | 6.9764 | 3441.9112 | 7217.2643 | 11068.0682 | 2350.6126 | 4872.0292 | 8869.9014 | 0.090367 | 0.08973 | 0.078515 | 17.3656 | 10.5061 | 11.4759 | 10.2322 | 22.9828 | 80.9392 | 141.5504 | 114.596 | 82.9824 | 99.53% | 99.53% | 99.32% | 99.56% | 99.53% | 99.09% | 132.7922 | 133.7349 | 152.8365 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 120.8999 | 12 | 25 | 66 | 30 | 98.37% | 0.088267 | 0.089051 | 41.0299 | 39.3476 | 129.2813 | 25.8711 | 98.37% | 3724.6177 | 99.27% | 99.48% | 85.01% |  |  | 99.32% | 0.93392
2021-10-30 | 176.3645 | 159.1035 | 159.1035 | 147.9581 | 135.683 | 13.9949 | 13.9949 | 3418.2377 | 1023.951 | 324.4018 | 604.2401 | 28.8325 | 11.533 | 24.0271 | 63.4316 | 9638.7388 | 353.6243 |  |  | 27.3495 | 0.92379 | 20.201 | 4022.4777 | 2069.8849 | 1952.5929 | 928.6419 | 17.2609 | 11.1455 | 12.0868 | 13.6476 | 10.9709 | 6.9515 | 3609.8365 | 7563.6676 | 11590.362 | 2465.7937 | 5108.0341 | 9292.2989 | 0.089119 | 0.088811 | 0.078619 | 17.2389 | 10.3644 | 11.3855 | 10.1427 | 22.7938 | 80.3363 | 141.4678 | 114.1159 | 81.6813 | 99.53% | 99.53% | 99.32% | 99.59% | 99.55% | 99.14% | 134.6515 | 135.1181 | 152.6356 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 121.7373 | 12 | 25 | 66 | 30 | 98.36% | 0.08734 | 0.08803 | 40.4932 | 38.9888 | 128.7131 | 25.6576 | 98.36% | 3905.1481 | 99.26% | 99.5% | 84.98% |  |  | 99.33% | 0.92379
2021-10-29 | 175.9389 | 158.5488 | 158.5488 | 147.3353 | 135.1883 | 14.0912 | 14.0912 | 3433.4589 | 1028.5106 | 325.8464 | 605.9061 | 26.1609 | 10.4644 | 21.8008 | 57.554 | 9590.3717 | 355.7646 |  |  | 27.5372 | 0.918 | 18.3292 | 4039.3651 | 2079.102 | 1960.2631 | 931.7525 | 17.39 | 11.2136 | 12.0616 | 13.7084 | 11.0198 | 6.9824 | 3586.4314 | 7521.2322 | 11535.0755 | 2449.0387 | 5076.8724 | 9243.7917 | 0.089276 | 0.08907 | 0.078901 | 17.2614 | 10.3695 | 11.3089 | 9.2488 | 20.7705 | 73.1403 | 140.9598 | 113.5755 | 81.2394 | 99.57% | 99.57% | 99.38% | 99.62% | 99.59% | 99.21% | 134.4149 | 134.7257 | 152.0891 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 121.0947 | 12 | 25 | 66 | 30 | 98.5% | 0.08755 | 0.08823 | 40.6652 | 38.9397 | 128.302 | 23.3816 | 98.5% | 3881.064 | 99.33% | 99.55% | 85% |  |  | 99.39% | 0.918
2021-10-28 | 176.5814 | 159.1278 | 159.1278 | 147.8463 | 135.4936 | 14.4154 | 14.4154 | 3440.885 | 1030.7351 | 326.5511 | 607.1833 | 25.6687 | 10.2675 | 21.3906 | 56.4712 | 9509.5941 | 358.0409 |  |  | 27.4614 | 0.92033 | 17.9844 | 4048.0683 | 2083.5988 | 1964.4695 | 933.7344 | 17.4536 | 11.2816 | 12.2338 | 13.738 | 11.0436 | 6.9975 | 3554.0739 | 7453.7489 | 11432.1016 | 2426.8898 | 5031.1788 | 9161.0477 | 0.089445 | 0.089138 | 0.078795 | 17.2687 | 10.3989 | 11.434 | 9.2007 | 20.6616 | 72.7533 | 141.356 | 114.0227 | 81.7316 | 99.58% | 99.57% | 99.38% | 99.62% | 99.59% | 99.21% | 134.1613 | 134.6225 | 152.2938 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 121.0868 | 12 | 25 | 66 | 30 | 98.52% | 0.087643 | 0.088342 | 40.9689 | 39.1016 | 128.7558 | 23.2592 | 98.52% | 3846.1116 | 99.33% | 99.54% | 85% |  |  | 99.39% | 0.92033
2021-10-27 | 178.4074 | 160.7105 | 160.7105 | 149.3192 | 136.6335 | 14.3703 | 14.3703 | 3470.015 | 1039.4611 | 329.3156 | 612.3711 | 26.9875 | 10.795 | 22.4896 | 59.3725 | 9503.4291 | 365.9969 |  |  | 27.2075 | 0.92819 | 18.9083 | 4082.3861 | 2101.2382 | 1981.1479 | 941.6867 | 17.697 | 11.3912 | 12.382 | 13.8543 | 11.1371 | 7.0568 | 3553.4899 | 7451.1105 | 11426.1755 | 2426.7214 | 5029.9334 | 9157.1053 | 0.089858 | 0.089418 | 0.078804 | 17.2891 | 10.3676 | 11.426 | 9.8393 | 22.0995 | 77.8306 | 143.109 | 115.6073 | 83.1174 | 99.56% | 99.55% | 99.35% | 99.59% | 99.56% | 99.15% | 133.5446 | 134.2018 | 152.2759 |  |  |  | 31 | 24.92 | 15.79 | 2418 | 1196.16 | 378.96 | 3993.12 | 122.283 | 12 | 25 | 66 | 30 | 98.44% | 0.087948 | 0.088677 | 41.4702 | 39.0827 | 130.5021 | 24.8772 | 98.44% | 3845.2624 | 99.3% | 99.51% | 85% |  |  | 99.35% | 0.92819
2021-10-26 | 177.8494 | 160.1316 | 160.1316 | 148.6107 | 135.9446 | 14.4034 | 14.4034 | 3472.2163 | 1040.4201 | 329.6194 | 612.8276 | 25.8707 | 10.4584 | 21.7883 | 57.521 | 9260.7396 | 366.3316 |  |  | 26.9169 | 0.93728 | 18.321 | 4085.0439 | 2102.1768 | 1982.8671 | 942.447 | 17.7178 | 11.5209 | 12.4395 | 13.8605 | 11.1474 | 7.0633 | 3473.627 | 7284.3052 | 11171.3505 | 2372.4298 | 4917.0821 | 8952.4691 | 0.090989 | 0.090468 | 0.07938 | 17.2907 | 10.4722 | 11.4656 | 9.8505 | 22.1367 | 77.9545 | 142.7772 | 115.4913 | 83.3995 | 99.56% | 99.56% | 99.36% | 99.58% | 99.55% | 99.13% | 131.8836 | 132.6442 | 151.1711 |  |  |  | 30.9853 | 24.92 | 15.79 | 2416.8505 | 1196.16 | 378.96 | 3991.9705 | 121.5283 | 12 | 25 | 66 | 29.6842 | 98.47% | 0.088965 | 0.089731 | 41.6782 | 39.2285 | 130.3761 | 24.6459 | 98.47% | 3759.56 | 99.31% | 99.5% | 85% |  |  | 99.36% | 0.93728
2021-10-25 | 175.6071 | 157.9521 | 157.9521 | 146.4505 | 133.6412 | 14.3661 | 14.3661 | 3468.812 | 1053.5059 | 333.7652 | 612.3625 | 25.2201 | 20.176 | 42.0334 | 110.9682 | 8838.163 | 360.7329 |  |  | 26.8263 | 0.94014 | 35.5502 | 4081.1744 | 2081.5408 | 1999.6336 | 946.1277 | 17.655 | 11.5016 | 12.4268 | 13.7244 | 11.2876 | 7.1521 | 3284.0025 | 6893.9103 | 10590.9204 | 2258.7158 | 4650.8076 | 8479.4732 | 0.091367 | 0.092445 | 0.080203 | 17.1746 | 10.3461 | 11.4184 | 19.8243 | 45.8578 | 161.2639 | 141.2208 | 114.7913 | 83.8372 | 99.11% | 99.1% | 98.69% | 99.12% | 99.01% | 98.1% | 131.3389 | 129.8071 | 149.6209 |  |  |  | 30.3 | 24.92 | 15.79 | 2363.3999 | 1196.16 | 378.96 | 3938.5199 | 119.2656 | 12 | 25 | 66 | 15 | 98.44% | 0.089925 | 0.09062 | 41.5834 | 38.9391 | 129.1622 | 25.2566 | 98.44% | 3583.7675 | 99.3% | 98.92% | 85% |  |  | 99.34% | 0.94014
2021-10-24 | 175.1922 | 157.4061 | 157.4061 | 145.8913 | 133.3052 | 14.3196 | 14.3196 | 3467.9546 | 1053.2456 | 333.6827 | 612.8653 | 25.2257 | 20.1806 | 42.0428 | 110.993 | 8968.5311 | 359.9338 |  |  | 27.3076 | 0.92508 | 35.5582 | 4080.82 | 2081.0263 | 1999.7936 | 946.5481 | 17.7861 | 11.5148 | 12.4758 | 13.7211 | 11.2848 | 7.1503 | 3327.0285 | 6982.3067 | 10723.4854 | 2288.4161 | 4711.171 | 8586.9973 | 0.090253 | 0.091586 | 0.079792 | 17.303 | 10.3549 | 11.4533 | 19.2532 | 44.5441 | 156.6905 | 140.6383 | 113.9834 | 82.8986 | 99.12% | 99.11% | 98.71% | 99.16% | 99.05% | 98.18% | 132.959 | 131.0238 | 150.3909 |  |  |  | 30.3 | 24.92 | 15.79 | 2363.3999 | 1196.16 | 378.96 | 3938.5199 | 119.0237 | 12 | 25 | 66 | 15 | 98.46% | 0.089006 | 0.089652 | 41.7767 | 39.1111 | 128.4665 | 24.5332 | 98.46% | 3630.2686 | 99.31% | 98.97% | 84.98% |  |  | 99.36% | 0.92508
2021-10-23 | 175.9453 | 158.3987 | 158.3987 | 147.0357 | 134.5434 | 14.4055 | 14.4055 | 3458.9805 | 1050.52 | 332.8192 | 610.2074 | 25.8218 | 20.6574 | 43.0364 | 113.616 | 9377.5732 | 360.2502 |  |  | 27.1527 | 0.9299 | 36.3985 | 4069.1878 | 2075.6412 | 1993.5467 | 943.0266 | 17.5466 | 11.363 | 12.3393 | 13.6855 | 11.2556 | 7.1318 | 3461.7326 | 7270.1181 | 11173.4167 | 2380.5739 | 4903.4295 | 8943.8939 | 0.090277 | 0.091804 | 0.080648 | 17.1455 | 10.2694 | 11.3957 | 18.9946 | 43.9231 | 154.394 | 140.9669 | 114.0097 | 82.2326 | 99.13% | 99.12% | 98.73% | 99.2% | 99.1% | 98.27% | 132.9235 | 130.7137 | 148.7953 |  |  |  | 30.3 | 24.92 | 15.79 | 2363.3999 | 1196.16 | 378.96 | 3938.5199 | 120.1298 | 12 | 25 | 66 | 15 | 98.49% | 0.089225 | 0.089814 | 41.2489 | 38.8106 | 128.373 | 24.1919 | 98.49% | 3778.3007 | 99.32% | 99.02% | 85% |  |  | 99.37% | 0.9299
2021-10-22 | 176.0574 | 158.4807 | 158.4807 | 147.0834 | 134.5306 | 14.2928 | 14.2928 | 3463.1563 | 1051.7883 | 333.221 | 611.6993 | 25.4469 | 20.3575 | 42.4115 | 111.9664 | 9504.8047 | 360.0709 |  |  | 27.3032 | 0.92522 | 35.87 | 4074.8556 | 2078.147 | 1996.7086 | 944.9203 | 17.5767 | 11.3973 | 12.4199 | 13.7021 | 11.2692 | 7.1405 | 3487.8187 | 7322.8922 | 11251.0188 | 2398.5872 | 4939.7846 | 9007.5148 | 0.089857 | 0.091458 | 0.080531 | 17.1375 | 10.2739 | 11.4327 | 18.5071 | 42.8023 | 150.4994 | 141.0851 | 114.0023 | 82.0364 | 99.15% | 99.14% | 98.76% | 99.23% | 99.13% | 98.33% | 133.5461 | 131.2075 | 149.0107 |  |  |  | 30.3 | 24.92 | 15.79 | 2363.3999 | 1196.16 | 378.96 | 3938.5199 | 120.2773 | 12 | 25 | 66 | 15 | 98.52% | 0.088877 | 0.089446 | 41.3939 | 38.844 | 128.3966 | 23.5749 | 98.52% | 3806.2728 | 99.33% | 99.05% | 84.99% |  |  | 99.38% | 0.92522
2021-10-21 | 175.9139 | 158.2946 | 158.2946 | 146.9512 | 134.423 | 14.3747 | 14.3747 | 3466.752 | 1049.1632 | 323.1875 | 611.4693 | 25.7099 | 20.5679 | 42.8498 | 113.1234 | 9464.8007 | 360.3849 |  |  | 27.3663 | 0.92326 | 35.9397 | 4078.2213 | 2094.4013 | 1983.8201 | 934.6569 | 17.6193 | 11.3434 | 12.3304 | 13.8092 | 11.241 | 6.9254 | 3479.7628 | 7337.7377 | 11156.2537 | 2383.5231 | 4937.7596 | 8981.9058 | 0.090477 | 0.09122 | 0.078006 | 17.2195 | 10.3472 | 11.4661 | 18.9236 | 43.0632 | 147.5841 | 140.9148 | 113.7737 | 81.9685 | 99.14% | 99.13% | 98.74% | 99.21% | 99.13% | 98.36% | 132.6301 | 131.55 | 153.8347 |  |  |  | 30.6646 | 24.9617 | 15.3785 | 2391.8375 | 1198.16 | 369.085 | 3959.0825 | 120.07 | 12 | 25 | 66 | 15 | 98.49% | 0.08872 | 0.089539 | 41.2931 | 39.0328 | 128.4033 | 24.0112 | 98.49% | 3771.6599 | 99.32% | 99.05% | 85.01% |  |  | 99.37% | 0.92326
2021-10-20 | 175.8707 | 158.2704 | 158.2704 | 147.0362 | 134.4182 | 14.3789 | 14.3789 | 3464.988 | 1045.2452 | 313.5736 | 611.6998 | 25.8164 | 20.6531 | 43.0273 | 113.5921 | 9542.5196 | 361.0264 |  |  | 27.324 | 0.92457 | 35.8133 | 4076.6878 | 2106.1692 | 1970.5186 | 925.2734 | 17.6003 | 11.2343 | 12.2706 | 13.8868 | 11.1991 | 6.7194 | 3531.6842 | 7472.6838 | 11245.1495 | 2410.5233 | 5018.937 | 9103.3818 | 0.091226 | 0.091312 | 0.076323 | 17.2643 | 10.3683 | 11.5126 | 18.9216 | 42.4435 | 142.0697 | 140.7423 | 113.3949 | 81.3994 | 99.14% | 99.14% | 98.75% | 99.22% | 99.15% | 98.44% | 131.541 | 131.417 | 157.2272 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 120.0856 | 12 | 25 | 66 | 15 | 98.5% | 0.088869 | 0.089904 | 41.1052 | 39.1451 | 128.2149 | 23.9333 | 98.5% | 3803.0637 | 99.32% | 99.07% | 85% |  |  | 99.37% | 0.92457
2021-10-19 | 175.0959 | 157.2674 | 157.2674 | 145.712 | 133.3997 | 14.4602 | 14.4602 | 3470.3431 | 1046.8607 | 314.0582 | 613.2406 | 25.0207 | 20.0166 | 41.7012 | 110.0912 | 9283.2809 | 360.0567 |  |  | 27.2625 | 0.92648 | 34.7095 | 4083.5837 | 2109.4242 | 1974.1595 | 927.2988 | 17.8285 | 11.5554 | 12.5922 | 13.9083 | 11.2164 | 6.7298 | 3455.5129 | 7309.4866 | 10996.5046 | 2358.6589 | 4910.0923 | 8903.4169 | 0.092023 | 0.092218 | 0.076854 | 17.4426 | 10.6335 | 11.7732 | 18.8093 | 42.1991 | 141.2921 | 140.0282 | 112.6875 | 81.129 | 99.15% | 99.15% | 98.76% | 99.2% | 99.14% | 98.41% | 130.4025 | 130.1271 | 156.1409 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 118.9567 | 12 | 25 | 66 | 15 | 98.51% | 0.089658 | 0.090709 | 41.9761 | 39.8493 | 127.6415 | 23.7954 | 98.51% | 3720.6079 | 99.33% | 99.06% | 84.98% |  |  | 99.38% | 0.92648
2021-10-18 | 170.3788 | 152.8833 | 152.8833 | 141.444 | 128.8751 | 14.0956 | 14.0956 | 3447.7541 | 1040.0465 | 312.0139 | 609.3779 | 22.9906 | 18.3925 | 38.3176 | 101.1585 | 8599.438 | 345.8369 |  |  | 27.2259 | 0.92762 | 31.8932 | 4057.1319 | 2095.6936 | 1961.4383 | 921.3918 | 17.4955 | 11.4393 | 12.4807 | 13.8178 | 11.1434 | 6.686 | 3232.764 | 6838.5836 | 10288.2831 | 2206.5213 | 4593.6609 | 8329.9074 | 0.093837 | 0.093722 | 0.077603 | 17.2841 | 10.6288 | 11.7809 | 18.3771 | 41.2267 | 138.0319 | 136.5948 | 110.2914 | 79.9202 | 99.17% | 99.17% | 98.79% | 99.17% | 99.1% | 98.34% | 127.8819 | 128.0378 | 154.633 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 114.7915 | 12 | 25 | 66 | 15 | 98.54% | 0.091203 | 0.092333 | 41.4155 | 39.6938 | 124.8825 | 23.2475 | 98.54% | 3480.7763 | 99.34% | 99.01% | 84.98% |  |  | 99.39% | 0.92762
2021-10-17 | 172.4983 | 154.7293 | 154.7293 | 143.2176 | 130.9405 | 14.4455 | 14.4455 | 3471.4911 | 1047.207 | 314.1621 | 613.8886 | 24.7308 | 19.7846 | 41.218 | 108.8155 | 9035.7169 | 353.2532 |  |  | 27.524 | 0.91841 | 34.3073 | 4085.3797 | 2110.122 | 1975.2576 | 928.0507 | 17.7689 | 11.5118 | 12.5372 | 13.9129 | 11.2201 | 6.732 | 3375.7388 | 7138.3927 | 10735.8316 | 2304.4484 | 4796.0469 | 8693.7771 | 0.092763 | 0.093041 | 0.077567 | 17.3718 | 10.5832 | 11.7059 | 18.8691 | 42.3438 | 141.8228 | 137.745 | 110.7538 | 79.7087 | 99.14% | 99.14% | 98.75% | 99.18% | 99.12% | 98.37% | 129.3612 | 128.9759 | 154.7051 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 116.3759 | 12 | 25 | 66 | 15 | 98.49% | 0.090421 | 0.091472 | 41.8179 | 39.6609 | 125.6182 | 23.8764 | 98.49% | 3634.2816 | 99.32% | 99.03% | 84.97% |  |  | 99.38% | 0.91841
2021-10-16 | 172.8473 | 155.3614 | 155.3614 | 144.1497 | 131.7904 | 14.4956 | 14.4956 | 3460.1683 | 1043.7913 | 313.1374 | 609.3594 | 25.2665 | 20.2132 | 42.1109 | 111.1728 | 9456.1966 | 351.8045 |  |  | 27.7895 | 0.9103 | 35.0505 | 4069.5277 | 2103.2395 | 1966.2881 | 922.4968 | 17.4859 | 11.2118 | 12.3527 | 13.8675 | 11.1835 | 6.7101 | 3511.6719 | 7437.4283 | 11202.2419 | 2396.2146 | 4992.5823 | 9064.2595 | 0.091655 | 0.092123 | 0.077604 | 17.2007 | 10.3852 | 11.6477 | 18.3159 | 41.0567 | 137.2962 | 137.7287 | 110.5075 | 78.709 | 99.16% | 99.16% | 98.77% | 99.24% | 99.18% | 98.49% | 130.9256 | 130.2607 | 154.6303 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 117.2529 | 12 | 25 | 66 | 15 | 98.52% | 0.089557 | 0.090525 | 41.0504 | 39.2336 | 125.2133 | 23.1527 | 98.52% | 3782.8756 | 99.33% | 99.1% | 85.03% |  |  | 99.39% | 0.9103
2021-10-15 | 173.6058 | 155.9944 | 155.9944 | 144.6891 | 132.2311 | 14.4498 | 14.4498 | 3471.4445 | 1047.1929 | 314.1579 | 613.2831 | 25.525 | 20.42 | 42.5417 | 112.3101 | 9493.5301 | 356.5843 |  |  | 27.7328 | 0.91202 | 35.4091 | 4084.7276 | 2110.0937 | 1974.6339 | 927.441 | 17.6114 | 11.3053 | 12.322 | 13.9127 | 11.2199 | 6.732 | 3549.8616 | 7510.0493 | 11299.5845 | 2422.9479 | 5044.4467 | 9148.2245 | 0.091723 | 0.092285 | 0.077885 | 17.2233 | 10.4 | 11.5185 | 18.3936 | 41.2622 | 138.1371 | 138.3377 | 110.8824 | 78.8307 | 99.16% | 99.16% | 98.77% | 99.24% | 99.18% | 98.49% | 130.8291 | 130.0314 | 154.0742 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 117.7551 | 12 | 25 | 66 | 15 | 98.52% | 0.089689 | 0.09064 | 41.2387 | 39.1418 | 125.732 | 23.2673 | 98.52% | 3822.3693 | 99.33% | 99.1% | 84.99% |  |  | 99.39% | 0.91202
2021-10-14 | 173.4732 | 155.9489 | 155.9489 | 144.7091 | 132.1847 | 14.3195 | 14.3195 | 3462.3203 | 1043.9813 | 314.7169 | 612.3007 | 25.9104 | 19.4662 | 40.6519 | 106.4795 | 9595.4163 | 354.6338 |  |  | 27.5326 | 0.91814 | 33.7635 | 4074.621 | 2103.6222 | 1970.9988 | 927.0175 | 17.5243 | 11.2399 | 12.3372 | 13.87 | 11.1855 | 6.7439 | 3624.8178 | 7661.2054 | 11544.2643 | 2474.4161 | 5148.7769 | 9338.8581 | 0.092202 | 0.092966 | 0.079418 | 17.1965 | 10.3615 | 11.5486 | 17.2319 | 38.7702 | 129.3832 | 138.1169 | 110.4689 | 77.9656 | 99.21% | 99.21% | 98.86% | 99.3% | 99.25% | 98.61% | 130.1487 | 129.0788 | 151.0985 |  |  |  | 31 | 25 | 15.0729 | 2418 | 1200 | 361.75 | 3979.75 | 117.8838 | 12.1458 | 25.3646 | 66.4375 | 16.1667 | 98.53% | 0.090401 | 0.091271 | 41.1014 | 39.1066 | 125.278 | 23.2142 | 98.53% | 3904.7685 | 99.34% | 99.18% | 84.97% |  |  | 99.39% | 0.91814
2021-10-13 | 172.0231 | 154.8106 | 154.8106 | 143.6034 | 131.547 | 14.4151 | 14.4151 | 3425.0512 | 1027.0019 | 328.6406 | 605.2134 | 25.4318 | 11.4853 | 24.6114 | 59.0674 | 9627.535 | 346.8217 |  |  | 27.4641 | 0.92025 | 19.9868 | 4030.2646 | 2069.4087 | 1960.8559 | 933.854 | 17.2125 | 11.2072 | 12.1558 | 13.6445 | 11.0036 | 7.0423 | 3625.4535 | 7585.4637 | 11672.4175 | 2479.5739 | 5126.8923 | 9337.1704 | 0.091879 | 0.092661 | 0.084417 | 17.1216 | 10.3491 | 11.3816 | 10.0038 | 23.2422 | 75.1336 | 136.6613 | 109.2805 | 76.7696 | 99.54% | 99.52% | 99.37% | 99.6% | 99.55% | 99.2% | 130.6067 | 129.5043 | 142.1513 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 117.1109 | 14 | 30 | 72 | 31 | 98.56% | 0.090935 | 0.091397 | 40.5755 | 38.8523 | 123.7732 | 22.439 | 98.56% | 3931.3728 | 99.35% | 99.52% | 84.98% |  |  | 99.41% | 0.92025
2021-10-12 | 173.1557 | 155.6372 | 155.6372 | 144.245 | 131.4844 | 14.5308 | 14.5308 | 3459.9306 | 1046.1687 | 334.774 | 612.4735 | 23.717 | 10.7109 | 22.952 | 55.0847 | 9302.3451 | 354.6976 |  |  | 27.2248 | 0.92765 | 18.7057 | 4072.404 | 2078.9879 | 1993.4162 | 947.2475 | 17.5185 | 11.3922 | 12.4269 | 13.7076 | 11.209 | 7.1737 | 3509.5939 | 7360.3466 | 11353.3549 | 2408.2732 | 4968.1779 | 9070.2122 | 0.092226 | 0.093943 | 0.085035 | 17.105 | 10.2743 | 11.405 | 9.7276 | 22.9683 | 74.0672 | 137.8779 | 110.6842 | 78.2583 | 99.56% | 99.54% | 99.39% | 99.6% | 99.54% | 99.18% | 130.1154 | 127.737 | 141.1177 |  |  |  | 30.5729 | 25 | 16 | 2384.6875 | 1200 | 384 | 3968.6875 | 117.1054 | 14 | 30 | 72 | 31 | 98.62% | 0.091625 | 0.092049 | 41.3375 | 38.7843 | 125.2332 | 21.8909 | 98.62% | 3826.8959 | 99.38% | 99.51% | 84.96% |  |  | 99.43% | 0.92765
2021-10-11 | 168.8686 | 151.2841 | 151.2841 | 139.8812 | 127.3171 | 14.4537 | 14.4537 | 3472.2829 | 1061.8602 | 339.7953 | 612.8734 | 23.3264 | 10.5345 | 22.5739 | 54.1774 | 8810.0744 | 346.7554 |  |  | 27.6999 | 0.91302 | 18.4871 | 4085.1562 | 2070.6274 | 2014.5288 | 952.6686 | 17.5845 | 11.4029 | 12.5333 | 13.6525 | 11.3771 | 7.2813 | 3290.2539 | 6932.4639 | 10745.991 | 2267.2603 | 4667.1779 | 8562.4101 | 0.092788 | 0.096265 | 0.086784 | 17.0267 | 10.1463 | 11.4386 | 9.962 | 24.0226 | 77.0897 | 134.339 | 107.9059 | 76.6043 | 99.54% | 99.52% | 99.37% | 99.56% | 99.49% | 99.1% | 129.327 | 124.6561 | 138.2742 |  |  |  | 30 | 25 | 16 | 2340 | 1200 | 384 | 3924 | 112.7819 | 14 | 30 | 72 | 31 | 98.57% | 0.09294 | 0.093264 | 41.5207 | 38.6116 | 122.2364 | 22.4992 | 98.57% | 3617.2192 | 99.36% | 99.46% | 85% |  |  | 99.41% | 0.91302
2021-10-10 | 166.5993 | 149.2437 | 149.2437 | 138.0582 | 125.4911 | 14.3287 | 14.3287 | 3452.2875 | 1055.7454 | 337.8385 | 608.3076 | 24.7764 | 11.1893 | 23.9772 | 57.5452 | 9072.1907 | 339.7891 |  |  | 28.0658 | 0.90195 | 19.6363 | 4060.5951 | 2058.7035 | 2001.8915 | 946.1461 | 17.3557 | 11.1854 | 12.2418 | 13.5739 | 11.3116 | 7.2394 | 3376.0446 | 7116.4074 | 11036.7195 | 2326.1887 | 4789.8108 | 8791.6696 | 0.092737 | 0.096712 | 0.088506 | 16.96 | 10.05 | 11.2923 | 10.1294 | 24.4196 | 78.3254 | 132.0178 | 105.493 | 73.7753 | 99.52% | 99.5% | 99.35% | 99.56% | 99.49% | 99.11% | 129.3984 | 124.0799 | 135.5841 |  |  |  | 30 | 25 | 16 | 2340 | 1200 | 384 | 3924 | 111.2793 | 14 | 30 | 72 | 31 | 98.52% | 0.093332 | 0.093538 | 40.7829 | 38.3024 | 119.7 | 22.8708 | 98.52% | 3712.2976 | 99.33% | 99.47% | 85.02% |  |  | 99.4% | 0.90195
2021-10-09 | 167.0607 | 149.7717 | 149.7717 | 138.7513 | 126.4454 | 14.5186 | 14.5186 | 3447.4578 | 1054.2684 | 337.3659 | 608.0795 | 23.5705 | 10.6448 | 22.8102 | 54.7445 | 9284.8028 | 338.0915 |  |  | 28.1426 | 0.89965 | 18.6807 | 4055.5373 | 2055.8234 | 1999.7138 | 945.4454 | 17.2889 | 11.0205 | 12.1379 | 13.5549 | 11.2957 | 7.2293 | 3454.133 | 7280.4093 | 11289.2485 | 2379.8856 | 4900.4223 | 8993.6073 | 0.092347 | 0.096456 | 0.088625 | 16.9251 | 9.9163 | 11.2065 | 9.3818 | 22.6171 | 72.5527 | 132.0514 | 105.3549 | 73.3854 | 99.55% | 99.53% | 99.39% | 99.61% | 99.54% | 99.19% | 129.9444 | 124.4086 | 135.4022 |  |  |  | 30 | 25 | 16 | 2340 | 1200 | 384 | 3924 | 111.9358 | 14 | 30 | 72 | 31 | 98.62% | 0.093067 | 0.09324 | 40.4473 | 38.0479 | 119.5468 | 21.1833 | 98.62% | 3797.9063 | 99.38% | 99.52% | 85.01% |  |  | 99.45% | 0.89965
2021-10-08 | 169.3368 | 151.8987 | 151.8987 | 140.7019 | 128.4768 | 14.3803 | 14.3803 | 3467.0564 | 1057.439 | 338.9156 | 612.2944 | 25.7049 | 11.6087 | 24.8757 | 59.7017 | 9653.8419 | 346.7088 |  |  | 28.3619 | 0.8931 | 20.3563 | 4079.3508 | 2070.7019 | 2008.649 | 951.21 | 17.4381 | 11.1968 | 12.2764 | 13.653 | 11.3297 | 7.2625 | 3535.2418 | 7437.6376 | 11521.4535 | 2434.165 | 5011.4384 | 9183.5491 | 0.090912 | 0.094578 | 0.086957 | 16.9335 | 10 | 11.2261 | 10.0023 | 24.0153 | 77.2759 | 134.1247 | 106.9872 | 74.5898 | 99.52% | 99.5% | 99.35% | 99.59% | 99.52% | 99.16% | 131.9961 | 126.88 | 137.9986 |  |  |  | 30.0789 | 24.9605 | 16 | 2346.1579 | 1198.1053 | 384 | 3928.2632 | 114.0531 | 14 | 30 | 72 | 31 | 98.53% | 0.091452 | 0.091643 | 40.9113 | 38.1596 | 121.3441 | 22.5759 | 98.53% | 3879.9969 | 99.34% | 99.5% | 84.99% |  |  | 99.41% | 0.8931
2021-10-07 | 168.8078 | 151.5022 | 151.5022 | 140.4704 | 128.1482 | 14.2524 | 14.2524 | 3455.9935 | 987.4267 | 329.1422 | 610.0788 | 26.109 | 11.7912 | 25.2668 | 60.6404 | 9601.5301 | 343.2741 |  |  | 28.34 | 0.89375 | 20.2937 | 4066.0723 | 2139.4245 | 1926.6478 | 939.2211 | 17.3055 | 11.0318 | 12.157 | 14.1061 | 10.5796 | 7.053 | 3656.5372 | 7474.1832 | 11473.8468 | 2464.3768 | 5118.0747 | 9190.0337 | 0.094339 | 0.088977 | 0.084716 | 17.2072 | 10.3413 | 11.27 | 10.3756 | 22.3195 | 76.2291 | 133.6396 | 106.2698 | 74.4099 | 99.52% | 99.51% | 99.34% | 99.58% | 99.56% | 99.17% | 127.2014 | 134.8669 | 141.6503 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 113.8536 | 14 | 30 | 72 | 31 | 98.5% | 0.091083 | 0.09189 | 40.4943 | 38.8186 | 121.1489 | 22.9742 | 98.5% | 3863.115 | 99.32% | 99.51% | 85% |  |  | 99.4% | 0.89375
2021-10-06 | 168.3022 | 150.8895 | 150.8895 | 139.7813 | 127.3362 | 14.2352 | 14.2352 | 3469.8505 | 991.3859 | 330.462 | 612.6605 | 25.03 | 11.3039 | 24.2226 | 58.1342 | 9505.7534 | 343.9731 |  |  | 28.5509 | 0.88751 | 19.455 | 4082.511 | 2148.0027 | 1934.5083 | 943.1225 | 17.4127 | 11.1083 | 12.2755 | 14.1627 | 10.622 | 7.0813 | 3618.3161 | 7396.334 | 11354.4736 | 2438.5149 | 5064.6601 | 9094.363 | 0.094348 | 0.089021 | 0.084766 | 17.209 | 10.3492 | 11.3088 | 10.0221 | 21.5578 | 73.6256 | 133.2246 | 105.898 | 74.1424 | 99.54% | 99.52% | 99.36% | 99.59% | 99.57% | 99.19% | 127.1885 | 134.8 | 141.5663 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 113.0924 | 14 | 30 | 72 | 31 | 98.55% | 0.09111 | 0.091913 | 40.7964 | 38.867 | 120.8318 | 22.1906 | 98.55% | 3822.7324 | 99.35% | 99.52% | 84.99% |  |  | 99.42% | 0.88751
2021-10-05 | 167.8267 | 150.4046 | 150.4046 | 139.2748 | 126.6944 | 14.2458 | 14.2458 | 3468.9421 | 991.1263 | 330.3754 | 613.6804 | 24.407 | 11.0225 | 23.6197 | 56.6872 | 9272.3194 | 342.3871 |  |  | 28.5006 | 0.88899 | 18.9707 | 4082.6225 | 2147.4404 | 1935.1821 | 944.0558 | 17.4221 | 11.1298 | 12.3222 | 14.1589 | 10.6192 | 7.0795 | 3549.0548 | 7250.2676 | 11122.9387 | 2392.2381 | 4966.3581 | 8912.0468 | 0.094666 | 0.089161 | 0.084521 | 17.2149 | 10.3606 | 11.3305 | 9.9757 | 21.4675 | 73.365 | 132.9638 | 105.8802 | 74.462 | 99.54% | 99.52% | 99.36% | 99.58% | 99.57% | 99.18% | 126.7608 | 134.5877 | 141.9766 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 112.4003 | 14 | 30 | 72 | 31 | 98.55% | 0.091282 | 0.092127 | 40.874 | 38.906 | 120.7734 | 22.097 | 98.55% | 3748.6351 | 99.35% | 99.51% | 84.97% |  |  | 99.42% | 0.88899
2021-10-04 | 165.5541 | 148.1217 | 148.1217 | 136.8465 | 124.4155 | 14.2075 | 14.2075 | 3462.1681 | 989.1909 | 329.7303 | 610.441 | 23.8217 | 10.7582 | 23.0532 | 55.3277 | 8856.8597 | 336.0754 |  |  | 28.6879 | 0.88348 | 18.5158 | 4072.6091 | 2143.2469 | 1929.3622 | 940.1713 | 17.4324 | 11.2753 | 12.323 | 14.1313 | 10.5985 | 7.0656 | 3408.6167 | 6970.7 | 10706.0449 | 2296.9352 | 4772.0496 | 8572.8663 | 0.095159 | 0.089576 | 0.084544 | 17.2933 | 10.5493 | 11.4095 | 10.0579 | 21.6283 | 73.8327 | 131.1996 | 104.5317 | 73.8358 | 99.53% | 99.52% | 99.35% | 99.56% | 99.55% | 99.14% | 126.1052 | 133.9637 | 141.9377 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 110.1735 | 14 | 30 | 72 | 31 | 98.53% | 0.091674 | 0.092553 | 41.0307 | 39.2521 | 119.383 | 22.2635 | 98.53% | 3601.8185 | 99.34% | 99.49% | 85.01% |  |  | 99.42% | 0.88348
2021-10-03 | 166.061 | 148.6589 | 148.6589 | 137.4602 | 124.8987 | 14.1878 | 14.1878 | 3462.6491 | 989.3283 | 329.7761 | 610.7503 | 23.9604 | 10.8208 | 23.1875 | 55.65 | 9081.2666 | 337.3656 |  |  | 28.7118 | 0.88278 | 18.6236 | 4073.3994 | 2143.5447 | 1929.8547 | 940.5264 | 17.402 | 11.1987 | 12.2743 | 14.1333 | 10.5999 | 7.0666 | 3480.4323 | 7117.066 | 10929.8945 | 2345.3403 | 4872.4406 | 8752.5207 | 0.094879 | 0.089437 | 0.084866 | 17.2576 | 10.473 | 11.3571 | 9.9012 | 21.2921 | 72.6908 | 131.4995 | 104.6255 | 73.5073 | 99.54% | 99.52% | 99.36% | 99.58% | 99.56% | 99.17% | 126.4765 | 134.172 | 141.3988 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 110.7966 | 14 | 30 | 72 | 31 | 98.55% | 0.091536 | 0.092371 | 40.8751 | 39.0878 | 119.4934 | 21.9175 | 98.55% | 3677.5766 | 99.35% | 99.51% | 85.01% |  |  | 99.43% | 0.88278
2021-10-02 | 167.6682 | 150.3247 | 150.3247 | 139.2039 | 126.57 | 14.1743 | 14.1743 | 3467.2526 | 990.6436 | 330.2145 | 613.4731 | 25.0783 | 11.3257 | 24.2694 | 58.2465 | 9518.7538 | 341.2452 |  |  | 28.6684 | 0.88406 | 19.4925 | 4080.7257 | 2146.3945 | 1934.3312 | 943.6876 | 17.3435 | 11.1208 | 12.2107 | 14.1521 | 10.614 | 7.076 | 3635.3144 | 7426.0376 | 11391.9029 | 2450.4301 | 5086.93 | 9127.8462 | 0.094334 | 0.089131 | 0.085267 | 17.149 | 10.3588 | 11.2343 | 9.9463 | 21.4051 | 73.1563 | 132.6266 | 105.2767 | 73.3647 | 99.54% | 99.52% | 99.36% | 99.59% | 99.58% | 99.2% | 127.2076 | 134.6336 | 140.7342 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 112.415 | 14 | 30 | 72 | 31 | 98.55% | 0.091218 | 0.091984 | 40.675 | 38.742 | 120.1873 | 22.0327 | 98.55% | 3839.6602 | 99.35% | 99.53% | 84.97% |  |  | 99.42% | 0.88406
2021-10-01 | 168.4207 | 151.0089 | 151.0089 | 140.0005 | 127.5163 | 14.3416 | 14.3416 | 3470.5254 | 991.5787 | 330.5262 | 612.44 | 25.7965 | 11.65 | 24.9643 | 59.9143 | 9710.0132 | 344.2126 |  |  | 28.6404 | 0.88488 | 20.0507 | 4082.9654 | 2148.4205 | 1934.5449 | 942.9662 | 17.4118 | 11.0084 | 12.4457 | 14.1654 | 10.6241 | 7.0827 | 3699.6343 | 7563.7435 | 11613.4666 | 2493.2283 | 5178.841 | 9300.9477 | 0.09427 | 0.089199 | 0.085606 | 17.206 | 10.2568 | 11.4699 | 10.0743 | 21.6678 | 73.989 | 132.9653 | 105.3937 | 73.2116 | 99.53% | 99.52% | 99.36% | 99.6% | 99.58% | 99.2% | 127.2939 | 134.5311 | 140.1778 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 113.1382 | 14 | 30 | 72 | 31 | 98.53% | 0.091261 | 0.091996 | 40.8659 | 38.9327 | 120.3063 | 22.3039 | 98.53% | 3908.9004 | 99.34% | 99.53% | 85% |  |  | 99.42% | 0.88488
2021-09-30 | 166.1921 | 149.0731 | 149.0731 | 138.1115 | 125.7392 | 14.148 | 14.148 | 3438.6598 | 982.4742 | 327.4914 | 608.4743 | 25.8889 | 11.6918 | 25.0538 | 60.1292 | 9573.0129 | 335.295 |  |  | 28.6423 | 0.88482 | 20.1226 | 4047.1341 | 2128.6942 | 1918.4399 | 935.9657 | 17.119 | 10.9616 | 12.034 | 14.0353 | 10.5265 | 7.0177 | 3677.3262 | 7511.0817 | 11521.3135 | 2478.87 | 5145.4833 | 9231.9884 | 0.094692 | 0.089695 | 0.08634 | 17.138 | 10.3375 | 11.2088 | 10.075 | 21.6842 | 74.1174 | 131.1487 | 103.8421 | 71.918 | 99.53% | 99.51% | 99.35% | 99.59% | 99.58% | 99.2% | 126.7262 | 133.7873 | 138.9858 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 111.5803 | 14 | 30 | 72 | 31 | 98.52% | 0.091757 | 0.092469 | 40.1146 | 38.6843 | 118.6088 | 22.3196 | 98.52% | 3883.9136 | 99.33% | 99.53% | 84.97% |  |  | 99.42% | 0.88482
2021-09-29 | 167.2245 | 149.8301 | 149.8301 | 138.6572 | 126.1076 | 14.1837 | 14.1837 | 3470.9486 | 991.6996 | 330.5665 | 614.112 | 25.5578 | 11.5422 | 24.7334 | 59.3601 | 9491.9486 | 340.8634 |  |  | 28.5552 | 0.88738 | 19.8652 | 4085.0606 | 2148.6824 | 1936.3781 | 944.6785 | 17.3944 | 11.1729 | 12.3028 | 14.1671 | 10.6254 | 7.0836 | 3645.9037 | 7447.3166 | 11424.1337 | 2457.6392 | 5101.6413 | 9153.8482 | 0.095159 | 0.090076 | 0.086432 | 17.172 | 10.3908 | 11.3013 | 10.1556 | 21.8566 | 74.7027 | 132.1131 | 104.6754 | 72.7263 | 99.53% | 99.52% | 99.35% | 99.59% | 99.57% | 99.18% | 126.1053 | 133.2204 | 138.8381 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 111.9055 | 14 | 30 | 72 | 31 | 98.53% | 0.092136 | 0.092875 | 40.8701 | 38.8641 | 119.6167 | 22.4973 | 98.53% | 3850.8026 | 99.34% | 99.52% | 84.97% |  |  | 99.41% | 0.88738
2021-09-28 | 166.5546 | 149.1108 | 149.1108 | 137.8958 | 125.5959 | 14.2892 | 14.2892 | 3462.8729 | 989.3922 | 329.7974 | 611.6629 | 25.1322 | 11.2662 | 25.1322 | 61.5306 | 9374.7527 | 338.3272 |  |  | 28.4534 | 0.89039 | 20.015 | 4074.5358 | 2143.6832 | 1930.8526 | 941.4603 | 17.4438 | 11.2149 | 12.3436 | 14.1342 | 10.6006 | 7.0671 | 3601.4541 | 7359.8548 | 11294.9774 | 2427.2437 | 5040.4506 | 9048.2088 | 0.095729 | 0.090637 | 0.086765 | 17.2898 | 10.4776 | 11.4009 | 10.0473 | 22.5024 | 78.4207 | 131.4636 | 104.1375 | 72.5233 | 99.54% | 99.5% | 99.32% | 99.59% | 99.55% | 99.13% | 125.3534 | 132.3965 | 138.305 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 111.3061 | 13 | 29 | 71 | 29 | 98.53% | 0.092665 | 0.093421 | 41.0024 | 39.1684 | 119.087 | 22.4158 | 98.53% | 3804.4423 | 99.34% | 99.5% | 84.99% |  |  | 99.41% | 0.89039
2021-09-27 | 165.4614 | 147.8695 | 147.8695 | 136.4212 | 123.9297 | 14.3334 | 14.3334 | 3471.5508 | 991.8717 | 330.6239 | 613.7737 | 23.928 | 10.7263 | 23.928 | 58.5823 | 8891.6729 | 337.2008 |  |  | 28.2813 | 0.8955 | 19.056 | 4085.3244 | 2149.0553 | 1936.2692 | 944.3975 | 17.5919 | 11.4483 | 12.4958 | 14.1696 | 10.6272 | 7.0848 | 3433.1633 | 7013.7781 | 10760.3609 | 2314.0191 | 4804.2648 | 8621.4391 | 0.096998 | 0.091585 | 0.086877 | 17.3662 | 10.6492 | 11.4854 | 10.1169 | 22.6631 | 79.0063 | 130.8155 | 103.9102 | 73.0277 | 99.54% | 99.5% | 99.32% | 99.56% | 99.53% | 99.08% | 123.7135 | 131.0252 | 138.126 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 109.634 | 13 | 29 | 71 | 29 | 98.53% | 0.093647 | 0.094488 | 41.536 | 39.5008 | 118.8904 | 22.5756 | 98.53% | 3626.2246 | 99.34% | 99.48% | 84.98% |  |  | 99.41% | 0.8955
2021-09-26 | 164.6758 | 147.2181 | 147.2181 | 135.939 | 123.4145 | 14.1775 | 14.1775 | 3469.8451 | 991.3843 | 330.4614 | 611.0228 | 24.0499 | 10.781 | 24.0499 | 58.8807 | 8965.8792 | 334.462 |  |  | 28.3411 | 0.89372 | 19.153 | 4080.8679 | 2147.9994 | 1932.8685 | 941.4842 | 17.4577 | 11.2792 | 12.3779 | 14.1626 | 10.622 | 7.0813 | 3452.3386 | 7062.3318 | 10850.0311 | 2326.0768 | 4833.9299 | 8686.7681 | 0.097221 | 0.091852 | 0.087462 | 17.2676 | 10.5264 | 11.4393 | 10.0906 | 22.5827 | 78.6163 | 130.193 | 103.3516 | 72.3598 | 99.54% | 99.5% | 99.32% | 99.57% | 99.53% | 99.09% | 123.4305 | 130.6445 | 137.2026 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 109.2578 | 13 | 29 | 71 | 29 | 98.53% | 0.093941 | 0.094757 | 41.1147 | 39.2333 | 118.2324 | 22.4969 | 98.53% | 3648.3864 | 99.34% | 99.48% | 85.03% |  |  | 99.41% | 0.89372
2021-09-25 | 165.0424 | 147.7473 | 147.7473 | 136.6632 | 124.2303 | 14.2129 | 14.2129 | 3458.8758 | 988.2502 | 329.4167 | 608.9971 | 25.4513 | 11.4092 | 25.4513 | 62.3119 | 9455.3545 | 334.4902 |  |  | 28.6981 | 0.88319 | 20.2691 | 4067.8728 | 2141.2088 | 1926.664 | 938.4138 | 17.2951 | 11.084 | 12.2459 | 14.1179 | 10.5884 | 7.0589 | 3619.7218 | 7404.8735 | 11376.5884 | 2438.8636 | 5068.3379 | 9108.2116 | 0.09588 | 0.090988 | 0.087802 | 17.189 | 10.3946 | 11.3733 | 10.0329 | 22.4534 | 78.1646 | 130.0446 | 102.7779 | 71.0043 | 99.53% | 99.5% | 99.32% | 99.59% | 99.56% | 99.14% | 125.1564 | 131.8861 | 136.6707 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 110.1057 | 13 | 29 | 71 | 29 | 98.52% | 0.093022 | 0.093713 | 40.625 | 38.9569 | 117.6187 | 22.368 | 98.52% | 3825.318 | 99.33% | 99.51% | 85.03% |  |  | 99.41% | 0.88319
2021-09-24 | 165.7718 | 148.4669 | 148.4669 | 137.4483 | 124.9538 | 14.3419 | 14.3419 | 3470.415 | 991.5472 | 330.5157 | 611.7306 | 26.3885 | 11.8293 | 26.3885 | 64.6064 | 9676.1995 | 337.3314 |  |  | 28.7378 | 0.88202 | 21.0155 | 4082.1456 | 2148.3522 | 1933.7934 | 942.2463 | 17.3049 | 11.0186 | 12.3369 | 14.165 | 10.6237 | 7.0825 | 3698.1678 | 7562.0645 | 11612.9129 | 2492.0561 | 5177.1863 | 9299.6359 | 0.095829 | 0.091096 | 0.088378 | 17.107 | 10.2741 | 11.3852 | 10.2008 | 22.8366 | 79.5344 | 130.3763 | 102.8617 | 70.684 | 99.53% | 99.49% | 99.31% | 99.59% | 99.56% | 99.14% | 125.2235 | 131.7285 | 135.7808 |  |  |  | 32 | 24 | 16 | 2496 | 1152 | 384 | 4032 | 110.6194 | 13 | 29 | 71 | 29 | 98.5% | 0.093122 | 0.093767 | 40.6603 | 38.7664 | 117.7131 | 22.7491 | 98.5% | 3907.5771 | 99.32% | 99.51% | 85.01% |  |  | 99.4% | 0.88202
2021-09-23 | 165.1152 | 147.7733 | 147.7733 | 136.6823 | 124.4243 | 14.3701 | 14.3701 | 3472.0548 | 1029.7835 | 332.5794 | 611.717 | 26.7533 | 11.8413 | 28.0086 | 64.7202 | 9616.6325 | 336.3178 |  |  | 28.9864 | 0.87478 | 21.7016 | 4083.7718 | 2109.692 | 1974.0798 | 944.2964 | 17.3419 | 11.0911 | 12.2899 | 13.9101 | 11.0334 | 7.1267 | 3618.5089 | 7534.0569 | 11594.9987 | 2466.0963 | 5106.1091 | 9274.5181 | 0.093744 | 0.094194 | 0.088891 | 16.966 | 10.1175 | 11.3197 | 10.0498 | 25.3144 | 79.7295 | 129.8029 | 102.4672 | 70.1342 | 99.52% | 99.45% | 99.3% | 99.59% | 99.5% | 99.14% | 128.0076 | 127.3961 | 134.9963 |  |  |  | 31.2292 | 24.7708 | 16 | 2435.875 | 1189 | 384 | 4008.875 | 109.9982 | 14.5417 | 34.3958 | 79.4792 | 32.8542 | 98.48% | 0.093112 | 0.093413 | 40.7229 | 38.4032 | 117.0471 | 22.9222 | 98.48% | 3901.2643 | 99.31% | 99.49% | 85.02% |  |  | 99.4% | 0.87478
2021-09-22 | 164.5537 | 147.1948 | 147.1948 | 136.0726 | 123.791 | 14.3843 | 14.3843 | 3471.5711 | 1040.9509 | 333.1043 | 613.4929 | 26.561 | 11.7181 | 28.1234 | 64.0589 | 9560.6005 | 335.8395 |  |  | 29.328 | 0.86496 | 21.6594 | 4085.064 | 2097.516 | 1987.548 | 946.5972 | 17.3589 | 11.1223 | 12.2178 | 13.8298 | 11.153 | 7.1379 | 3600.2521 | 7528.4387 | 11581.3249 | 2462.4844 | 5089.9787 | 9265.7351 | 0.09256 | 0.094633 | 0.088785 | 16.9208 | 10.0643 | 11.2092 | 9.7911 | 25.4856 | 78.2255 | 129.2362 | 101.9401 | 69.5391 | 99.52% | 99.45% | 99.31% | 99.6% | 99.5% | 99.16% | 129.6451 | 126.8058 | 135.1584 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 109.3982 | 15 | 36 | 82 | 34 | 98.49% | 0.092619 | 0.09282 | 40.699 | 38.1943 | 116.4667 | 22.4879 | 98.49% | 3903.1245 | 99.32% | 99.5% | 84.98% |  |  | 99.41% | 0.86496
2021-09-21 | 164.5114 | 147.0989 | 147.0989 | 136.049 | 123.4692 | 14.3821 | 14.3821 | 3472.5671 | 1041.2495 | 333.1998 | 613.8329 | 26.4326 | 11.6615 | 27.9875 | 63.7493 | 9345.2597 | 336.1125 |  |  | 29.2187 | 0.86808 | 21.5547 | 4086.4 | 2098.1178 | 1988.2822 | 947.0327 | 17.4125 | 11.0499 | 12.4987 | 13.8337 | 11.1562 | 7.14 | 3530.6969 | 7381.8779 | 11354.2937 | 2415.0355 | 4991.3117 | 9084.77 | 0.0928 | 0.094599 | 0.088202 | 16.9644 | 9.9928 | 11.4583 | 9.974 | 25.9648 | 79.7082 | 129.4062 | 102.3752 | 70.2719 | 99.52% | 99.44% | 99.3% | 99.59% | 99.48% | 99.12% | 129.3107 | 126.8517 | 136.0514 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 109.1399 | 15 | 36 | 82 | 34 | 98.47% | 0.09264 | 0.092898 | 40.9611 | 38.4155 | 116.8152 | 22.9105 | 98.47% | 3827.5066 | 99.31% | 99.48% | 84.98% |  |  | 99.4% | 0.86808
2021-09-20 | 163.2672 | 145.7059 | 145.7059 | 134.3196 | 121.7155 | 14.3417 | 14.3417 | 3473.5214 | 1041.5357 | 333.2914 | 613.2982 | 24.7419 | 10.9156 | 26.1974 | 59.6717 | 8654.6609 | 333.9166 |  |  | 28.7544 | 0.88154 | 20.1761 | 4086.8197 | 2098.6944 | 1988.1253 | 946.5897 | 17.5613 | 11.3863 | 12.6311 | 13.8375 | 11.1593 | 7.142 | 3291.5453 | 6884.4182 | 10593.2653 | 2251.2437 | 4653.9829 | 8474.0873 | 0.094602 | 0.095944 | 0.087927 | 17.1082 | 10.3002 | 11.5906 | 10.1733 | 26.4767 | 81.2483 | 128.9433 | 102.5322 | 71.6038 | 99.52% | 99.44% | 99.3% | 99.55% | 99.43% | 99.04% | 126.8473 | 125.0732 | 136.4773 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 107.3859 | 15 | 36 | 82 | 34 | 98.46% | 0.093963 | 0.094364 | 41.5787 | 38.999 | 117.0162 | 23.3625 | 98.46% | 3568.7997 | 99.31% | 99.43% | 84.99% |  |  | 99.39% | 0.88154
2021-09-19 | 163.586 | 145.9907 | 145.9907 | 134.5745 | 122.2453 | 14.257 | 14.257 | 3471.9564 | 1041.0664 | 333.1412 | 611.6513 | 24.9498 | 11.0073 | 26.4175 | 60.1731 | 8807.612 | 333.9374 |  |  | 28.6499 | 0.8846 | 20.3456 | 4083.6077 | 2097.7488 | 1985.8589 | 944.7925 | 17.5954 | 11.4162 | 12.6089 | 13.8313 | 11.1543 | 7.1387 | 3341.5264 | 6994.4432 | 10771.2542 | 2284.9486 | 4726.2804 | 8612.744 | 0.094728 | 0.096239 | 0.088457 | 17.1646 | 10.3488 | 11.6087 | 10.138 | 26.3703 | 80.8557 | 129.1616 | 102.5263 | 71.39 | 99.52% | 99.44% | 99.3% | 99.56% | 99.44% | 99.06% | 126.6791 | 124.689 | 135.6596 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 107.9449 | 15 | 36 | 82 | 34 | 98.47% | 0.094208 | 0.094579 | 41.6205 | 39.122 | 117.0762 | 23.2691 | 98.47% | 3624.1469 | 99.31% | 99.44% | 85.02% |  |  | 99.39% | 0.8846
2021-09-18 | 164.1337 | 146.925 | 146.925 | 135.8851 | 123.4351 | 14.3128 | 14.3128 | 3449.322 | 1034.2795 | 330.9694 | 609.6426 | 26.3832 | 11.6397 | 27.9352 | 63.6302 | 9335.4553 | 332.5757 |  |  | 28.7234 | 0.88244 | 21.5145 | 4058.9646 | 2084.0731 | 1974.8915 | 940.612 | 17.2087 | 11.0399 | 12.236 | 13.7411 | 11.0816 | 7.0922 | 3533.5268 | 7388.21 | 11364.6578 | 2416.9303 | 4995.4357 | 9092.7948 | 0.09386 | 0.095632 | 0.08915 | 16.9362 | 10.0858 | 11.3329 | 10.0444 | 26.147 | 80.263 | 129.1902 | 102.2548 | 70.2015 | 99.52% | 99.44% | 99.3% | 99.58% | 99.48% | 99.12% | 127.8501 | 125.4807 | 134.6045 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 109.1132 | 15 | 36 | 82 | 34 | 98.47% | 0.093674 | 0.093939 | 40.4846 | 38.3549 | 116.6073 | 23.0713 | 98.47% | 3830.658 | 99.31% | 99.48% | 84.98% |  |  | 99.4% | 0.88244
2021-09-17 | 164.1131 | 146.9301 | 146.9301 | 135.8802 | 123.5044 | 14.2974 | 14.2974 | 3450.064 | 1034.502 | 331.0406 | 609.79 | 26.5531 | 11.7146 | 28.115 | 64.0398 | 9501.9224 | 333.2045 |  |  | 28.8202 | 0.87962 | 21.653 | 4059.8541 | 2084.5214 | 1975.3326 | 940.8307 | 17.183 | 11.0499 | 12.2306 | 13.7441 | 11.0839 | 7.0937 | 3582.2072 | 7490.153 | 11521.6146 | 2450.1991 | 5064.3032 | 9218.3122 | 0.093694 | 0.095653 | 0.089621 | 16.9053 | 10.0914 | 11.3238 | 9.942 | 25.8798 | 79.4416 | 129.0317 | 101.9268 | 69.6235 | 99.52% | 99.44% | 99.31% | 99.59% | 99.49% | 99.14% | 128.0762 | 125.4532 | 133.8966 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 109.2129 | 15 | 36 | 82 | 34 | 98.48% | 0.093669 | 0.093891 | 40.4634 | 38.3206 | 116.2898 | 22.8357 | 98.48% | 3883.4525 | 99.32% | 99.49% | 84.98% |  |  | 99.4% | 0.87962
2021-09-16 | 164.2057 | 146.8738 | 146.8738 | 135.7971 | 123.5836 | 14.2429 | 14.2429 | 3462.6433 | 1038.2738 | 332.2476 | 610.3434 | 27.8138 | 12.2708 | 29.4499 | 67.0803 | 9614.8547 | 334.1131 |  |  | 28.7865 | 0.8806 | 22.681 | 4072.9867 | 2092.1218 | 1980.8649 | 942.5911 | 17.3318 | 11.0767 | 12.3356 | 13.7942 | 11.1244 | 7.1196 | 3599.461 | 7531.8653 | 11595.4088 | 2461.6099 | 5090.3683 | 9273.2246 | 0.094127 | 0.09624 | 0.090317 | 16.973 | 10.0782 | 11.3956 | 10.4152 | 27.0983 | 83.1149 | 129.0502 | 101.788 | 69.4167 | 99.5% | 99.42% | 99.28% | 99.58% | 99.47% | 99.1% | 127.4868 | 124.6881 | 132.8656 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 109.3133 | 15 | 36 | 82 | 34 | 98.42% | 0.094194 | 0.094395 | 40.7442 | 38.4467 | 116.2415 | 23.9109 | 98.42% | 3903.4315 | 99.29% | 99.47% | 85.01% |  |  | 99.37% | 0.8806
2021-09-15 | 162.7396 | 145.5784 | 145.5784 | 134.6265 | 122.3083 | 14.2369 | 14.2369 | 3445.5256 | 1033.1411 | 330.6052 | 608.6382 | 28.299 | 12.4849 | 29.9637 | 68.2506 | 9560.1077 | 329.3856 |  |  | 28.8844 | 0.87775 | 23.0767 | 4054.1637 | 2081.7793 | 1972.3844 | 939.2433 | 17.1612 | 10.9519 | 12.203 | 13.726 | 11.0694 | 7.0844 | 3586.4889 | 7498.5661 | 11534.6267 | 2453.3079 | 5070.1962 | 9228.6926 | 0.094332 | 0.09652 | 0.090873 | 16.9202 | 10.0253 | 11.3282 | 10.5459 | 27.4547 | 84.279 | 127.718 | 100.6644 | 68.4283 | 99.49% | 99.41% | 99.26% | 99.57% | 99.46% | 99.09% | 127.2096 | 124.327 | 132.0521 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 108.0839 | 15 | 36 | 82 | 34 | 98.38% | 0.094479 | 0.094656 | 40.316 | 38.2738 | 114.9786 | 24.2246 | 98.38% | 3888.0939 | 99.27% | 99.46% | 84.99% |  |  | 99.37% | 0.87775
2021-09-14 | 162.0335 | 144.7084 | 144.7084 | 133.6014 | 121.2466 | 14.0791 | 14.0791 | 3466.5955 | 1038.4631 | 329.4617 | 611.2784 | 27.7182 | 12.2286 | 29.3487 | 66.8498 | 9436.4351 | 328.8651 |  |  | 28.978 | 0.87503 | 22.5483 | 4077.8739 | 2098.6707 | 1979.2032 | 940.74 | 17.3251 | 11.107 | 12.3461 | 13.8374 | 11.1264 | 7.0599 | 3551.0166 | 7438.5117 | 11411.6277 | 2425.7812 | 5024.2356 | 9143.3982 | 0.095172 | 0.097261 | 0.090898 | 16.9528 | 10.1239 | 11.4153 | 10.4988 | 27.1926 | 82.7741 | 127.2241 | 100.1014 | 67.9621 | 99.5% | 99.42% | 99.27% | 99.57% | 99.46% | 99.09% | 126.088 | 123.3799 | 132.0163 |  |  |  | 30.625 | 24.625 | 15.625 | 2388.75 | 1182 | 375 | 3945.75 | 107.1649 | 15 | 36 | 82 | 34 | 98.4% | 0.095156 | 0.095391 | 40.7782 | 38.4921 | 114.5902 | 24.0802 | 98.4% | 3842.6169 | 99.28% | 99.46% | 85.01% |  |  | 99.37% | 0.87503
2021-09-13 | 159.1465 | 141.691 | 141.691 | 130.3693 | 117.7901 | 14.0277 | 14.0277 | 3470.6557 | 1037.9531 | 324.3603 | 612.4707 | 26.1512 | 11.5373 | 27.6895 | 63.0705 | 8741.4445 | 324.3252 |  |  | 29.0367 | 0.87333 | 21.184 | 4083.1264 | 2108.3422 | 1974.7842 | 936.831 | 17.4554 | 11.3217 | 12.5332 | 13.9012 | 11.1209 | 6.9506 | 3335.9594 | 7001.3258 | 10675.7789 | 2274.4351 | 4723.8992 | 8581.7136 | 0.097063 | 0.09858 | 0.089983 | 17.0769 | 10.3639 | 11.6188 | 10.5925 | 27.22 | 81.7584 | 125.0766 | 98.5214 | 67.4588 | 99.49% | 99.41% | 99.27% | 99.53% | 99.42% | 99.05% | 123.6314 | 121.7289 | 133.3587 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 103.7937 | 15 | 36 | 82 | 34 | 98.39% | 0.096415 | 0.096855 | 41.3104 | 39.0596 | 113.1054 | 24.2551 | 98.39% | 3596.4504 | 99.27% | 99.42% | 85% |  |  | 99.37% | 0.87333
2021-09-12 | 158.7963 | 141.2943 | 141.2943 | 129.9672 | 117.768 | 14.0746 | 14.0746 | 3471.8658 | 1038.315 | 324.4734 | 612.0377 | 26.8895 | 11.863 | 28.4713 | 64.8512 | 8966.9084 | 323.2774 |  |  | 29.2808 | 0.86631 | 21.7822 | 4083.9034 | 2109.0774 | 1974.8261 | 936.5111 | 17.5019 | 11.3272 | 12.4236 | 13.906 | 11.1248 | 6.953 | 3406.1218 | 7150.9416 | 10907.6519 | 2322.087 | 4823.9525 | 8766.4977 | 0.096824 | 0.098766 | 0.090872 | 17.1189 | 10.3704 | 11.5256 | 10.5859 | 27.1971 | 81.6615 | 124.4196 | 97.5788 | 66.2848 | 99.49% | 99.41% | 99.26% | 99.54% | 99.44% | 99.07% | 123.9357 | 121.4991 | 132.0539 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 103.6542 | 15 | 36 | 82 | 34 | 98.37% | 0.096493 | 0.096849 | 41.2527 | 39.0149 | 112.2628 | 24.235 | 98.37% | 3672.5898 | 99.27% | 99.43% | 85.01% |  |  | 99.37% | 0.86631
2021-09-11 | 159.5402 | 142.2739 | 142.2739 | 131.2406 | 118.8606 | 14.2889 | 14.2889 | 3469.7156 | 1037.672 | 324.2725 | 611.3106 | 28.5461 | 12.5939 | 30.2253 | 68.8465 | 9374.8511 | 324.6178 |  |  | 29.4483 | 0.86153 | 23.1241 | 4081.0262 | 2107.7712 | 1973.255 | 935.5831 | 17.2663 | 11.0333 | 12.2805 | 13.8974 | 11.1179 | 6.9487 | 3537.1732 | 7426.7919 | 11329.8476 | 2411.4192 | 5009.7671 | 9105.2026 | 0.096073 | 0.098169 | 0.091285 | 16.907 | 10.1144 | 11.4112 | 10.7554 | 27.6312 | 82.9556 | 124.624 | 97.5707 | 65.5799 | 99.48% | 99.4% | 99.24% | 99.55% | 99.45% | 99.09% | 124.9053 | 122.2386 | 131.4559 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 104.5703 | 15 | 36 | 82 | 34 | 98.34% | 0.095977 | 0.096252 | 40.5801 | 38.4325 | 112.1048 | 24.6216 | 98.34% | 3814.0824 | 99.25% | 99.45% | 85.02% |  |  | 99.36% | 0.86153
2021-09-10 | 157.0645 | 140.1639 | 140.1639 | 129.4706 | 117.183 | 14.0265 | 14.0265 | 3424.0385 | 1023.9389 | 320.2057 | 604.1356 | 28.7985 | 12.7052 | 30.4926 | 69.4553 | 9392.9274 | 313.8047 |  |  | 29.3644 | 0.86391 | 23.3315 | 4028.1741 | 2079.8939 | 1948.2802 | 924.3414 | 16.9005 | 10.6933 | 11.943 | 13.7136 | 10.9708 | 6.8616 | 3549.0139 | 7446.6549 | 11356.7398 | 2419.9199 | 5025.0577 | 9128.2805 | 0.096672 | 0.098915 | 0.092613 | 16.8732 | 9.9886 | 11.2988 | 10.699 | 27.4989 | 82.6592 | 122.5516 | 95.818 | 64.0062 | 99.47% | 99.39% | 99.24% | 99.56% | 99.45% | 99.09% | 124.1305 | 121.3166 | 129.5717 |  |  |  | 30.0208 | 24.0165 | 15.0208 | 2341.625 | 1152.79 | 360.5 | 3854.915 | 103.19 | 15 | 36 | 82 | 34 | 98.33% | 0.09674 | 0.096963 | 39.5368 | 38.1606 | 110.0779 | 24.5017 | 98.33% | 3826.3169 | 99.25% | 99.45% | 85% |  |  | 99.36% | 0.86391
2021-09-09 | 156.4877 | 139.5756 | 139.5756 | 128.8838 | 116.6293 | 14.0374 | 14.0374 | 3423.1206 | 1020.3711 | 329.2847 | 604.0404 | 29.3626 | 12.9541 | 31.0898 | 70.8157 | 9389.4744 | 312.1309 |  |  | 29.4316 | 0.862 | 23.926 | 4027.1611 | 2073.4648 | 1953.6963 | 933.3252 | 16.9121 | 10.6918 | 11.9597 | 13.6712 | 10.9325 | 7.0561 | 3543.7181 | 7383.9493 | 11370.6083 | 2420.484 | 5002.2425 | 9092.1936 | 0.096629 | 0.098848 | 0.095616 | 16.8661 | 9.9127 | 11.2165 | 10.8482 | 28.0051 | 86.819 | 121.9566 | 95.3365 | 63.6122 | 99.46% | 99.38% | 99.22% | 99.55% | 99.44% | 99.05% | 124.186 | 121.3981 | 125.5017 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 102.6618 | 15 | 36 | 82 | 34 | 98.3% | 0.097177 | 0.097193 | 39.5636 | 37.9952 | 109.4476 | 24.8836 | 98.3% | 3831.8406 | 99.23% | 99.44% | 85% |  |  | 99.35% | 0.862
2021-09-08 | 156.0242 | 138.6933 | 138.6933 | 127.6651 | 115.0797 | 14.0713 | 14.0713 | 3466.2619 | 1033.2307 | 333.4347 | 613.0869 | 28.8715 | 12.7374 | 30.5698 | 69.6313 | 9078.5657 | 317.1861 |  |  | 29.2662 | 0.86672 | 23.5258 | 4079.3488 | 2099.5965 | 1979.7524 | 946.5216 | 17.3309 | 11.0283 | 12.3369 | 13.8435 | 11.0703 | 7.145 | 3438.5726 | 7158.7764 | 11014.2928 | 2349.2201 | 4852.0097 | 8811.3752 | 0.098668 | 0.101 | 0.097382 | 16.95 | 10.0195 | 11.3236 | 11.1898 | 28.9046 | 89.6865 | 121.6051 | 95.0007 | 63.5924 | 99.46% | 99.37% | 99.21% | 99.52% | 99.4% | 98.98% | 121.6205 | 118.8139 | 123.2259 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 101.0055 | 15 | 36 | 82 | 34 | 98.28% | 0.099208 | 0.099239 | 40.696 | 38.2932 | 109.359 | 25.6821 | 98.28% | 3716.8795 | 99.22% | 99.4% | 84.97% |  |  | 99.33% | 0.86672
2021-09-07 | 154.3207 | 136.7119 | 136.7119 | 125.4433 | 112.8885 | 14.3495 | 14.3495 | 3471.705 | 1034.8532 | 333.9583 | 615.3503 | 30.7696 | 13.5748 | 32.5796 | 74.209 | 8802.6262 | 315.5493 |  |  | 29.2657 | 0.86674 | 25.0725 | 4087.0553 | 2102.8935 | 1984.1618 | 949.3086 | 17.6088 | 11.2687 | 12.4429 | 13.8652 | 11.0877 | 7.1562 | 3210.4991 | 6674.7894 | 10257.0067 | 2194.4908 | 4527.4563 | 8210.9651 | 0.099928 | 0.10196 | 0.096715 | 17.1702 | 10.2003 | 11.3657 | 12.7866 | 33.0656 | 102.7349 | 120.2622 | 94.2537 | 64.1326 | 99.38% | 99.28% | 99.1% | 99.42% | 99.27% | 98.75% | 120.0867 | 117.6927 | 124.0756 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 98.5474 | 15 | 36 | 82 | 34 | 98.03% | 0.10006 | 0.10022 | 41.3203 | 38.7363 | 108.7029 | 29.3758 | 98.03% | 3468.6567 | 99.11% | 99.26% | 84.94% |  |  | 99.23% | 0.86674
2021-09-06 | 151.8267 | 134.6038 | 134.6038 | 123.547 | 111.1935 | 14.1618 | 14.1618 | 3422.8193 | 1020.2813 | 329.2557 | 605.9179 | 30.6648 | 13.5286 | 32.4687 | 73.9564 | 8593.1638 | 303.5467 |  |  | 29.0413 | 0.8732 | 24.9871 | 4028.7372 | 2073.2823 | 1955.4549 | 935.1736 | 17.2229 | 11.0568 | 12.2609 | 13.67 | 10.9316 | 7.0555 | 3216.3505 | 6689.989 | 10285.1408 | 2198.2156 | 4536.6124 | 8231.4382 | 0.10105 | 0.10331 | 0.098698 | 17.1617 | 10.2319 | 11.4573 | 12.6358 | 32.665 | 101.4425 | 118.1301 | 92.3929 | 62.4211 | 99.38% | 99.28% | 99.1% | 99.43% | 99.28% | 98.77% | 118.7576 | 116.1515 | 121.5834 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 96.9945 | 15 | 36 | 82 | 34 | 98.04% | 0.1014 | 0.1015 | 40.5406 | 38.8509 | 106.5502 | 29.0204 | 98.04% | 3475.6116 | 99.12% | 99.27% | 84.96% |  |  | 99.24% | 0.8732
2021-09-05 | 152.5411 | 135.056 | 135.056 | 123.8714 | 111.1743 | 13.9437 | 13.9437 | 3458.1452 | 1030.8113 | 332.6539 | 612.0797 | 30.4809 | 13.4474 | 32.2738 | 73.5126 | 8674.2917 | 308.3676 |  |  | 29.1413 | 0.87031 | 24.8372 | 4070.2249 | 2094.68 | 1975.5449 | 944.7336 | 17.4851 | 11.1846 | 12.4764 | 13.8111 | 11.0444 | 7.1283 | 3325.8268 | 6919.4657 | 10640.1131 | 2272.7885 | 4691.5535 | 8514.5975 | 0.10138 | 0.10423 | 0.10108 | 17.1574 | 10.1929 | 11.4825 | 12.2326 | 31.6159 | 98.1611 | 118.5582 | 92.2236 | 61.3737 | 99.41% | 99.31% | 99.14% | 99.46% | 99.33% | 98.85% | 118.3617 | 115.1349 | 118.7145 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 97.2699 | 15 | 36 | 82 | 34 | 98.12% | 0.10225 | 0.1022 | 41.1461 | 38.8329 | 106.6205 | 28.0892 | 98.12% | 3594.2056 | 99.15% | 99.32% | 84.96% |  |  | 99.26% | 0.87031
2021-09-04 | 152.7888 | 135.1934 | 135.1934 | 123.8722 | 111.3885 | 13.8782 | 13.8782 | 3473.507 | 1035.3904 | 334.1316 | 613.8169 | 34.8028 | 15.3542 | 36.85 | 83.9361 | 9305.4529 | 311.2622 |  |  | 29.1815 | 0.86915 | 28.3589 | 4087.3238 | 2103.985 | 1983.3388 | 947.9485 | 17.5954 | 11.3212 | 12.6426 | 13.8724 | 11.0935 | 7.16 | 3539.8755 | 7366.0317 | 11330.0452 | 2419.1427 | 4993.867 | 9065.3148 | 0.1021 | 0.10611 | 0.10575 | 17.1596 | 10.2593 | 11.5803 | 13.1629 | 34.0188 | 105.5978 | 118.094 | 90.8695 | 58.8452 | 99.37% | 99.26% | 99.07% | 99.46% | 99.32% | 98.84% | 117.533 | 113.0929 | 113.471 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 97.4975 | 15 | 36 | 82 | 34 | 97.98% | 0.10397 | 0.10365 | 41.5593 | 38.9992 | 105.4221 | 30.223 | 97.98% | 3825.9459 | 99.09% | 99.31% | 84.98% |  |  | 99.21% | 0.86915
2021-09-03
2021-09-02
2021-09-01
2021-08-31
2021-08-30
2021-08-29
2021-08-28
2021-08-27
2021-08-26
2021-08-25
2021-08-24
2021-08-23
2021-08-22
2021-08-21
2021-08-20
2021-08-19
2021-08-18
2021-08-17
2021-08-16
2021-08-15
2021-08-14
2021-08-13
2021-08-12
2021-08-11 | 162.0586 | 144.7678 | 144.7678 | 134.0594 | 121.5062 | 13.1677 | 13.1677 | 3468.1098 | 1033.7816 | 333.6124 | 611.9161 | 29.2001 | 12.8824 | 30.9177 | 70.4237 | 9627.1526 | 329.9776 |  |  | 29.3696 | 0.86377 | 23.7935 | 4080.0259 | 2100.7158 | 1979.3101 | 945.5285 | 17.2908 | 10.7084 | 11.9646 | 13.8509 | 11.0762 | 7.1488 | 3581.8896 | 7464.2996 | 11495.3899 | 2446.4489 | 5056.3668 | 9191.5222 | 0.093412 | 0.094615 | 0.08948 | 16.9098 | 9.7361 | 11.0048 | 10.8361 | 27.9713 | 86.7053 | 128.0776 | 101.1186 | 69.0096 | 99.47% | 99.39% | 99.23% | 99.56% | 99.45% | 99.06% | 128.4635 | 126.8303 | 134.1089 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 108.3894 | 15 | 36 | 82 | 34 | 98.33% | 0.093168 | 0.093392 | 39.9637 | 37.6507 | 115.5402 | 24.8539 | 98.33% | 3873.2564 | 99.25% | 99.44% | 85% |  |  | 99.35% | 0.86377
2021-08-10 | 161.7283 | 144.4406 | 144.4406 | 133.5535 | 121.1039 | 13.529 | 13.529 | 3466.2441 | 1033.2254 | 333.433 | 612.5554 | 29.257 | 12.9075 | 30.978 | 70.561 | 9419.3076 | 331.4375 |  |  | 29.2571 | 0.86698 | 23.8399 | 4078.7996 | 2099.5857 | 1979.2139 | 945.9884 | 17.2876 | 10.8871 | 12.2257 | 13.8434 | 11.0703 | 7.145 | 3543.9422 | 7380.8645 | 11360.0899 | 2420.9346 | 5001.5015 | 9086.2541 | 0.094122 | 0.095391 | 0.090141 | 16.9123 | 9.8968 | 11.2331 | 11.0066 | 28.4235 | 88.1607 | 127.5153 | 100.6154 | 68.7212 | 99.47% | 99.38% | 99.22% | 99.55% | 99.43% | 99.03% | 127.4936 | 125.7986 | 133.1247 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 107.5765 | 15 | 36 | 82 | 34 | 98.31% | 0.093891 | 0.094117 | 40.4004 | 38.0421 | 114.9909 | 25.2551 | 98.31% | 3831.3213 | 99.24% | 99.43% | 84.98% |  |  | 99.34% | 0.86698
2021-08-09 | 160.127 | 142.7295 | 142.7295 | 131.7196 | 119.1419 | 13.8811 | 13.8811 | 3463.7349 | 1032.4775 | 333.1916 | 612.7316 | 28.2508 | 12.4636 | 29.9126 | 68.1342 | 8809.7989 | 329.9401 |  |  | 29.0674 | 0.87244 | 23.02 | 4076.4665 | 2098.0658 | 1978.4007 | 945.9232 | 17.3974 | 11.01 | 12.3245 | 13.8334 | 11.0623 | 7.1398 | 3344.6522 | 6962.6986 | 10711.829 | 2285.1142 | 4719.3208 | 8569.7419 | 0.095645 | 0.096612 | 0.090222 | 17.0329 | 10.0129 | 11.3227 | 11.3224 | 29.2489 | 90.7617 | 126.1839 | 99.8964 | 69.0416 | 99.45% | 99.37% | 99.2% | 99.5% | 99.38% | 98.94% | 125.4641 | 124.2083 | 133.0051 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 105.2495 | 15 | 36 | 82 | 34 | 98.27% | 0.095087 | 0.095411 | 40.7319 | 38.3685 | 114.2553 | 25.9878 | 98.27% | 3615.2531 | 99.22% | 99.37% | 84.97% |  |  | 99.32% | 0.87244
2021-08-08 | 155.9522 | 139.6081 | 139.6081 | 129.2889 | 117.3405 | 13.9663 | 13.9663 | 3349.0683 | 998.2974 | 322.1613 | 593.1083 | 28.6825 | 12.654 | 30.3697 | 69.1754 | 8990.5848 | 308.1536 |  |  | 29.1489 | 0.87009 | 23.3718 | 3942.1766 | 2028.6095 | 1913.5671 | 915.2696 | 16.3441 | 10.3192 | 11.5362 | 13.3754 | 10.696 | 6.9035 | 3404.2622 | 7084.214 | 10894.6041 | 2326.0574 | 4802.6631 | 8717.7546 | 0.0952 | 0.09632 | 0.090865 | 16.8248 | 9.8638 | 11.1327 | 10.8898 | 28.1386 | 87.3495 | 122.2468 | 96.6207 | 66.1055 | 99.46% | 99.37% | 99.21% | 99.53% | 99.41% | 99% | 126.0506 | 124.5842 | 132.0647 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 103.3851 | 15 | 36 | 82 | 34 | 98.27% | 0.094865 | 0.095117 | 38.1995 | 37.8214 | 110.2435 | 25.001 | 98.27% | 3679.1342 | 99.22% | 99.41% | 84.95% |  |  | 99.35% | 0.87009
2021-08-07 | 162.6399 | 145.229 | 145.229 | 134.1535 | 121.9308 | 14.1986 | 14.1986 | 3468.963 | 1034.0359 | 333.6945 | 611.8279 | 28.6104 | 12.6222 | 30.2934 | 69.0016 | 9398.2015 | 337.169 |  |  | 29.0462 | 0.87306 | 23.3131 | 4080.7909 | 2101.2326 | 1979.5583 | 945.5224 | 17.4109 | 11.0756 | 12.228 | 13.8543 | 11.079 | 7.1506 | 3530.6077 | 7358.5982 | 11334.3867 | 2411.3093 | 4984.3215 | 9062.023 | 0.094687 | 0.096032 | 0.090636 | 17.023 | 10.0687 | 11.2481 | 10.8905 | 28.1085 | 87.1163 | 127.7424 | 100.7225 | 68.8784 | 99.48% | 99.39% | 99.24% | 99.55% | 99.44% | 99.04% | 126.7333 | 124.9589 | 132.3977 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 107.7502 | 15 | 36 | 82 | 34 | 98.34% | 0.094469 | 0.094698 | 40.7145 | 38.3398 | 115.2367 | 24.976 | 98.34% | 3818.0391 | 99.25% | 99.43% | 85.01% |  |  | 99.35% | 0.87306
2021-08-06 | 162.5496 | 145.2123 | 145.2123 | 134.271 | 122.0968 | 14.2141 | 14.2141 | 3460.2351 | 1031.4343 | 332.8549 | 611.5505 | 29.272 | 12.9141 | 30.9939 | 70.5971 | 9513.462 | 335.8737 |  |  | 29.0327 | 0.87345 | 23.8521 | 4071.7856 | 2095.9459 | 1975.8397 | 944.4055 | 17.3374 | 10.9413 | 12.2042 | 13.8194 | 11.0511 | 7.1326 | 3584.959 | 7466.4289 | 11491.8347 | 2448.9165 | 5059.4294 | 9191.6073 | 0.09468 | 0.096155 | 0.091128 | 17.0046 | 9.9713 | 11.2413 | 10.9485 | 28.2729 | 87.6923 | 127.4868 | 100.3853 | 68.3647 | 99.47% | 99.39% | 99.23% | 99.55% | 99.44% | 99.05% | 126.742 | 124.7989 | 131.6828 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 107.8265 | 15 | 36 | 82 | 34 | 98.32% | 0.094584 | 0.094778 | 40.4829 | 38.2173 | 114.8404 | 25.1214 | 98.32% | 3875.6723 | 99.24% | 99.44% | 84.98% |  |  | 99.34% | 0.87345
2021-08-05 | 161.7494 | 144.3682 | 144.3682 | 133.4592 | 121.1342 | 14.1164 | 14.1164 | 3468.7397 | 1033.9693 | 333.673 | 611.8651 | 27.9315 | 12.3227 | 29.5746 | 67.3643 | 9446.3444 | 333.0218 |  |  | 29.2292 | 0.86778 | 22.7599 | 4080.6047 | 2101.0973 | 1979.5074 | 945.5381 | 17.3813 | 10.909 | 12.1974 | 13.8534 | 11.0782 | 7.1501 | 3565.522 | 7432.1682 | 11448.4727 | 2435.0103 | 5033.8498 | 9152.9081 | 0.094787 | 0.096351 | 0.09158 | 16.995 | 9.9174 | 11.2194 | 10.4644 | 27.0057 | 83.691 | 126.829 | 99.7759 | 67.7526 | 99.49% | 99.41% | 99.26% | 99.57% | 99.46% | 99.09% | 126.5994 | 124.5443 | 131.033 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 107.0255 | 15 | 36 | 82 | 34 | 98.39% | 0.094775 | 0.094945 | 40.4877 | 38.1319 | 114.2608 | 23.9966 | 98.39% | 3855.9015 | 99.28% | 99.46% | 85.01% |  |  | 99.37% | 0.86778
2021-08-04 | 161.6064 | 144.518 | 144.518 | 133.6629 | 121.59 | 14.2182 | 14.2182 | 3447.345 | 1027.592 | 331.615 | 607.6434 | 29.551 | 13.0372 | 31.2893 | 71.2701 | 9625.9024 | 330.747 |  |  | 29.1858 | 0.86903 | 24.0795 | 4054.9884 | 2088.1381 | 1966.8503 | 939.2584 | 17.0884 | 10.8551 | 12.0601 | 13.7679 | 11.0099 | 7.106 | 3631.3492 | 7569.9808 | 11662.3232 | 2480.0012 | 5126.9636 | 9323.2084 | 0.094576 | 0.096263 | 0.091966 | 16.8682 | 9.9651 | 11.2063 | 10.8187 | 27.9197 | 86.5141 | 126.5092 | 99.3939 | 67.1485 | 99.47% | 99.39% | 99.24% | 99.56% | 99.46% | 99.07% | 126.8815 | 124.6583 | 130.4831 |  |  |  | 31 | 24.79 | 16 | 2418 | 1189.92 | 384 | 3991.92 | 107.3502 | 15 | 36 | 82 | 34 | 98.33% | 0.094698 | 0.094828 | 40.0036 | 38.0396 | 113.7019 | 24.8083 | 98.33% | 3927.291 | 99.25% | 99.45% | 85.01% |  |  | 99.35% | 0.86903
2021-08-03 | 161.9734 | 144.6089 | 144.6089 | 133.6663 | 121.409 | 14.2829 | 14.2829 | 3466.3994 | 1031.2414 | 329.9219 | 611.3307 | 29.9636 | 15.0685 | 36.6523 | 85.0668 | 9416.4873 | 331.6489 |  |  | 29.1076 | 0.87128 | 28.1519 | 4077.7301 | 2105.2361 | 1972.494 | 941.2526 | 17.3645 | 10.9426 | 12.2872 | 13.8807 | 11.049 | 7.0698 | 3569.2091 | 7439.4973 | 11408.5239 | 2434.7879 | 5038.9492 | 9142.8916 | 0.095296 | 0.096419 | 0.09063 | 17.0203 | 10.0059 | 11.3546 | 12.8741 | 33.481 | 105.0319 | 126.9097 | 99.8432 | 67.9656 | 99.38% | 99.27% | 99.07% | 99.47% | 99.34% | 98.85% | 125.9234 | 124.4564 | 132.4058 |  |  |  | 31.1432 | 24.79 | 15.862 | 2429.1719 | 1189.92 | 380.6875 | 3999.7794 | 107.096 | 14.4792 | 35.2188 | 81.7396 | 28.7917 | 98.27% | 0.094909 | 0.095186 | 40.5943 | 38.3808 | 114.3129 | 25.8819 | 98.27% | 3847.9746 | 99.22% | 99.33% | 85.01% |  |  | 99.32% | 0.87128
2021-08-02 | 160.6324 | 143.146 | 143.146 | 131.9929 | 119.6019 | 14.2958 | 14.2958 | 3471.8432 | 1027.3523 | 320.5654 | 611.8654 | 28.7761 | 26.2482 | 66.6948 | 162.7135 | 8849.6885 | 330.154 |  |  | 29.045 | 0.87309 | 50.817 | 4083.7086 | 2123.9255 | 1959.7831 | 932.4308 | 17.4864 | 11.1532 | 12.4358 | 14.0039 | 11.0073 | 6.8693 | 3385.4724 | 7042.1018 | 10646.3158 | 2304.2084 | 4775.2576 | 8597.3393 | 0.09688 | 0.096363 | 0.086508 | 17.1684 | 10.3126 | 11.5847 | 23.9565 | 64.1787 | 208.0219 | 126.2037 | 99.7309 | 69.3284 | 98.86% | 98.6% | 98.11% | 98.96% | 98.66% | 97.58% | 123.8643 | 124.5289 | 138.7154 |  |  |  | 31.5177 | 24.7735 | 15.4602 | 2458.3812 | 1189.13 | 371.045 | 4018.5562 | 105.278 | 12.9792 | 32.9792 | 80.4583 | 14.2292 | 98.24% | 0.095055 | 0.09577 | 41.0754 | 39.0656 | 114.1193 | 26.5437 | 98.24% | 3616.4791 | 99.2% | 98.64% | 85.02% |  |  | 99.31% | 0.87309
2021-08-01 | 160.1411 | 142.7937 | 142.7937 | 131.7257 | 119.3648 | 14.0081 | 14.0081 | 3461.1384 | 1035.1068 | 323.4709 | 611.9221 | 28.4061 | 13.6349 | 36.3598 | 62.4934 | 8940.2185 | 326.6153 |  |  | 28.9998 | 0.8744 | 24.9973 | 4073.0606 | 2102.5607 | 1970.4999 | 935.393 | 17.3473 | 11.068 | 12.3737 | 13.863 | 11.0904 | 6.9315 | 3407.5934 | 7138.2037 | 10878.5263 | 2324.4078 | 4821.3481 | 8747.2579 | 0.096277 | 0.097632 | 0.088982 | 17.0316 | 10.1616 | 11.4931 | 12.2305 | 34.9675 | 79.3562 | 125.9055 | 99.3267 | 68.1134 | 99.41% | 99.25% | 99.29% | 99.47% | 99.27% | 99.09% | 124.6404 | 122.9109 | 134.858 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 105.2991 | 12 | 32 | 55 | 25 | 98.28% | 0.095543 | 0.096 | 40.789 | 38.6863 | 113.7772 | 25.7693 | 98.28% | 3671.4227 | 99.23% | 99.35% | 84.98% |  |  | 99.33% | 0.8744
2021-07-31 | 161.3469 | 144.0842 | 144.0842 | 133.2257 | 120.832 | 14.2006 | 14.2006 | 3454.1018 | 1033.0024 | 322.8133 | 610.9168 | 29.3656 | 14.0955 | 37.588 | 64.6044 | 9299.7326 | 328.9637 |  |  | 28.9783 | 0.87502 | 25.8418 | 4065.0186 | 2098.2861 | 1966.7324 | 933.73 | 17.2628 | 10.8584 | 12.2417 | 13.8349 | 11.0679 | 6.9174 | 3532.6759 | 7399.3549 | 11275.095 | 2409.7975 | 4998.0672 | 9066.7446 | 0.09567 | 0.097184 | 0.089253 | 16.9984 | 9.9972 | 11.4 | 12.1795 | 34.8245 | 79.0415 | 126.5365 | 99.652 | 67.8176 | 99.42% | 99.25% | 99.29% | 99.49% | 99.3% | 99.13% | 125.4308 | 123.4765 | 134.45 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 106.6297 | 12 | 32 | 55 | 25 | 98.29% | 0.095128 | 0.095523 | 40.363 | 38.3956 | 114.0852 | 25.6638 | 98.29% | 3806.004 | 99.23% | 99.37% | 84.97% |  |  | 99.33% | 0.87502
2021-07-30 | 162.0428 | 144.7749 | 144.7749 | 133.8658 | 121.5282 | 14.2383 | 14.2383 | 3458.7369 | 1034.3886 | 323.2464 | 611.4722 | 29.9867 | 14.3936 | 38.383 | 65.9708 | 9512.6115 | 330.1311 |  |  | 29.0196 | 0.87382 | 26.3883 | 4070.2092 | 2101.1019 | 1969.1073 | 934.7187 | 17.268 | 10.9091 | 12.2215 | 13.8534 | 11.0827 | 6.9267 | 3603.501 | 7548.7709 | 11504.4509 | 2458.0222 | 5098.5883 | 9250.4573 | 0.095354 | 0.097056 | 0.089622 | 16.9715 | 10.0264 | 11.3641 | 12.1928 | 34.8589 | 79.1079 | 126.9524 | 99.7809 | 67.5362 | 99.41% | 99.25% | 99.29% | 99.5% | 99.32% | 99.14% | 125.8468 | 123.64 | 133.8962 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 107.313 | 12 | 32 | 55 | 25 | 98.29% | 0.094981 | 0.095327 | 40.3986 | 38.3621 | 114.2724 | 25.6893 | 98.29% | 3882.5312 | 99.23% | 99.39% | 84.98% |  |  | 99.33% | 0.87382
2021-07-29 | 161.7283 | 144.4246 | 144.4246 | 133.4929 | 121.0274 | 14.2708 | 14.2708 | 3467.4748 | 1046.4935 | 327.0292 | 613.3437 | 29.6442 | 14.2688 | 34.9114 | 72.2548 | 9426.1752 | 331.0039 |  |  | 29.1439 | 0.87023 | 25.9677 | 4080.8184 | 2093.9521 | 1986.8663 | 940.3729 | 17.3036 | 10.9317 | 12.2382 | 13.8063 | 11.2124 | 7.0078 | 3550.5424 | 7462.9105 | 11403.5402 | 2430.5142 | 5031.0831 | 9156.4262 | 0.09481 | 0.097861 | 0.090255 | 16.8875 | 9.9269 | 11.297 | 12.1323 | 32.3741 | 88.1938 | 126.7244 | 99.7071 | 67.5686 | 99.41% | 99.31% | 99.21% | 99.5% | 99.36% | 99.04% | 126.5694 | 122.6228 | 132.9565 |  |  |  | 29.5521 | 24 | 15 | 2305.0625 | 1152 | 360 | 3817.0625 | 106.8113 | 12.8958 | 31.5521 | 65.3021 | 26.7917 | 98.29% | 0.095057 | 0.095301 | 40.4735 | 38.1114 | 114.1077 | 25.5716 | 98.29% | 3849.7164 | 99.23% | 99.38% | 84.97% |  |  | 99.33% | 0.87023
2021-07-28 | 161.7901 | 144.4694 | 144.4694 | 133.5758 | 121.232 | 14.2682 | 14.2682 | 3471.6263 | 1059.7015 | 331.1567 | 612.0458 | 29.5021 | 14.2424 | 31.5368 | 79.3506 | 9483.1441 | 331.0597 |  |  | 29.11 | 0.87121 | 25.7321 | 4083.6721 | 2080.7681 | 2002.904 | 943.2025 | 17.3208 | 10.8935 | 12.2174 | 13.7193 | 11.3539 | 7.0962 | 3536.9119 | 7475.251 | 11476.9159 | 2431.0652 | 5023.8657 | 9191.8785 | 0.094279 | 0.099122 | 0.091491 | 16.8255 | 9.7974 | 11.2611 | 12.0443 | 29.6896 | 97.8088 | 126.7775 | 99.7928 | 67.5731 | 99.41% | 99.37% | 99.14% | 99.5% | 99.41% | 98.94% | 127.2817 | 121.0625 | 131.161 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.9836 | 14 | 31 | 78 | 29 | 98.31% | 0.095383 | 0.095491 | 40.4317 | 37.884 | 114.0795 | 25.3914 | 98.31% | 3867.4189 | 99.24% | 99.38% | 85.01% |  |  | 99.34% | 0.87121
2021-07-27 | 161.3172 | 144.0441 | 144.0441 | 133.084 | 120.5588 | 14.1728 | 14.1728 | 3471.2707 | 1059.593 | 331.1228 | 611.5152 | 28.969 | 13.985 | 30.9668 | 77.9166 | 9330.7131 | 328.9942 |  |  | 28.9733 | 0.87516 | 25.2671 | 4082.7858 | 2080.5549 | 2002.2309 | 942.638 | 17.2731 | 10.9601 | 12.2415 | 13.7179 | 11.3528 | 7.0955 | 3484.5699 | 7366.6685 | 11313.3766 | 2394.9119 | 4950.1199 | 9059.5397 | 0.094827 | 0.099559 | 0.091669 | 16.7857 | 9.8635 | 11.2954 | 12.0584 | 29.7186 | 97.8762 | 126.6032 | 99.7955 | 67.7404 | 99.42% | 99.37% | 99.14% | 99.5% | 99.4% | 98.92% | 126.5457 | 120.5314 | 130.9054 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.463 | 14 | 31 | 78 | 29 | 98.31% | 0.095836 | 0.09597 | 40.4748 | 37.9445 | 114.0343 | 25.4164 | 98.31% | 3810.6156 | 99.24% | 99.37% | 85.02% |  |  | 99.33% | 0.87516
2021-07-26 | 159.9541 | 142.5286 | 142.5286 | 131.421 | 118.8648 | 14.1317 | 14.1317 | 3471.3204 | 1059.6081 | 331.1275 | 613.6076 | 28.4301 | 13.7249 | 30.3908 | 76.4671 | 8918.6746 | 325.9412 |  |  | 28.7679 | 0.88114 | 24.797 | 4084.928 | 2080.5847 | 2004.3433 | 944.7351 | 17.4255 | 11.1075 | 12.4823 | 13.7181 | 11.3529 | 7.0956 | 3352.6499 | 7078.8719 | 10857.6534 | 2305.028 | 4760.0928 | 8700.4959 | 0.096199 | 0.10085 | 0.092092 | 16.9161 | 9.9748 | 11.4711 | 12.3797 | 30.5377 | 100.704 | 125.6531 | 99.1946 | 67.891 | 99.4% | 99.36% | 99.12% | 99.46% | 99.36% | 98.84% | 124.7421 | 118.9911 | 130.3043 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 104.7444 | 14 | 31 | 78 | 29 | 98.28% | 0.097029 | 0.097226 | 41.0154 | 38.3619 | 113.4565 | 26.1158 | 98.28% | 3664.4883 | 99.22% | 99.33% | 84.98% |  |  | 99.32% | 0.88114
2021-07-25 | 158.5041 | 141.3269 | 141.3269 | 130.3527 | 118.6189 | 14.0299 | 14.0299 | 3452.6889 | 1053.9209 | 329.3503 | 611.9244 | 28.2233 | 13.625 | 30.1697 | 75.9109 | 9035.7523 | 322.5134 |  |  | 28.9055 | 0.87713 | 24.6166 | 4064.6133 | 2069.4177 | 1995.1957 | 941.2747 | 17.1772 | 10.9742 | 12.2374 | 13.6445 | 11.292 | 7.0575 | 3398.8391 | 7170.651 | 10989.1857 | 2337.2017 | 4823.9783 | 8809.8599 | 0.096308 | 0.10123 | 0.092689 | 16.7967 | 9.9186 | 11.3019 | 12.0006 | 29.618 | 97.7535 | 124.2677 | 97.8409 | 66.7862 | 99.42% | 99.37% | 99.14% | 99.49% | 99.39% | 98.89% | 124.5997 | 118.5402 | 129.4649 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 104.1642 | 14 | 31 | 78 | 29 | 98.32% | 0.097305 | 0.097466 | 40.3888 | 38.0172 | 111.9708 | 25.3291 | 98.32% | 3713.7051 | 99.24% | 99.36% | 84.95% |  |  | 99.34% | 0.87713
2021-07-24 | 161.4977 | 144.1722 | 144.1722 | 133.1568 | 120.7469 | 14.2325 | 14.2325 | 3470.2747 | 1059.2889 | 331.0278 | 613.7409 | 28.0347 | 13.534 | 29.9681 | 75.4037 | 9361.2282 | 329.0298 |  |  | 28.9887 | 0.87472 | 24.4522 | 4084.0156 | 2079.9579 | 2004.0576 | 944.7687 | 17.3255 | 11.0155 | 12.2943 | 13.714 | 11.3495 | 7.0935 | 3498.6495 | 7387.7874 | 11331.8005 | 2405.201 | 4967.5741 | 9080.3 | 0.094721 | 0.099531 | 0.091658 | 16.8239 | 9.8933 | 11.2964 | 11.6103 | 28.6362 | 94.4277 | 126.6441 | 99.7439 | 67.6948 | 99.44% | 99.4% | 99.17% | 99.52% | 99.42% | 98.96% | 126.6876 | 120.5654 | 130.9217 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.4853 | 14 | 31 | 78 | 29 | 98.37% | 0.09577 | 0.095897 | 40.6352 | 38.0137 | 114.0385 | 24.4904 | 98.37% | 3824.0906 | 99.27% | 99.4% | 84.97% |  |  | 99.36% | 0.87472
2021-07-23 | 161.7444 | 144.4953 | 144.4953 | 133.5495 | 121.1291 | 14.3175 | 14.3175 | 3470.5879 | 1059.3845 | 331.0577 | 614.2057 | 28.1522 | 13.5907 | 30.0938 | 75.7198 | 9498.3511 | 330.3628 |  |  | 28.9298 | 0.87643 | 24.5547 | 4084.7936 | 2080.1457 | 2004.6479 | 945.2634 | 17.249 | 10.9458 | 12.2428 | 13.7152 | 11.3505 | 7.0941 | 3526.3661 | 7444.7415 | 11416.6535 | 2424.3749 | 5006.4642 | 9149.3692 | 0.094837 | 0.099655 | 0.091901 | 16.744 | 9.8254 | 11.2388 | 11.5904 | 28.5912 | 94.3 | 126.7484 | 99.8231 | 67.6535 | 99.44% | 99.4% | 99.17% | 99.52% | 99.43% | 98.97% | 126.5334 | 120.4149 | 130.575 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.7756 | 14 | 31 | 78 | 29 | 98.38% | 0.095909 | 0.096028 | 40.4376 | 37.8081 | 114.0694 | 24.4518 | 98.38% | 3854.0423 | 99.27% | 99.4% | 84.96% |  |  | 99.36% | 0.87643
2021-07-22 | 160.9684 | 143.7863 | 143.7863 | 132.9274 | 120.7121 | 14.2654 | 14.2654 | 3456.2763 | 1055.016 | 329.6925 | 611.9006 | 28.43 | 13.7248 | 30.3907 | 76.467 | 9552.6654 | 326.6347 |  |  | 29.0432 | 0.87314 | 24.797 | 4068.177 | 2071.5678 | 1996.6091 | 941.5931 | 17.1821 | 10.8589 | 12.1767 | 13.6587 | 11.3037 | 7.0648 | 3515.0853 | 7419.5407 | 11375.9939 | 2416.7676 | 4990.0402 | 9117.6485 | 0.094578 | 0.0994 | 0.091592 | 16.7808 | 9.8057 | 11.2427 | 11.6494 | 28.7408 | 94.8112 | 126.0967 | 99.2932 | 67.3484 | 99.43% | 99.39% | 99.16% | 99.52% | 99.42% | 98.96% | 126.8794 | 120.724 | 131.0152 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.4349 | 14 | 31 | 78 | 29 | 98.36% | 0.095643 | 0.095765 | 40.2177 | 37.8292 | 113.4749 | 24.5795 | 98.36% | 3841.4436 | 99.26% | 99.4% | 84.96% |  |  | 99.36% | 0.87314
2021-07-21 | 161.6982 | 144.4326 | 144.4326 | 133.5736 | 121.1865 | 14.3767 | 14.3767 | 3470.4698 | 1059.3485 | 331.0464 | 613.1031 | 27.3632 | 13.2098 | 29.2503 | 73.5976 | 9593.0636 | 330.2561 |  |  | 29.1506 | 0.87004 | 23.8665 | 4083.5729 | 2080.0749 | 2003.498 | 944.1495 | 17.2655 | 10.859 | 12.1224 | 13.7148 | 11.3502 | 7.0939 | 3523.3819 | 7443.8449 | 11423.4269 | 2421.8076 | 5003.8197 | 9151.2997 | 0.094219 | 0.098995 | 0.091281 | 16.7699 | 9.7587 | 11.152 | 11.195 | 27.6011 | 90.9673 | 126.6457 | 99.7536 | 67.6149 | 99.45% | 99.42% | 99.2% | 99.54% | 99.45% | 99.01% | 127.3627 | 121.218 | 131.4621 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 106.8432 | 14 | 31 | 78 | 29 | 98.42% | 0.095277 | 0.095397 | 40.2469 | 37.6805 | 114.028 | 23.6059 | 98.42% | 3851.8805 | 99.29% | 99.42% | 84.99% |  |  | 99.38% | 0.87004
2021-07-20 | 160.827 | 143.6129 | 143.6129 | 132.7175 | 120.28 | 14.2115 | 14.2115 | 3471.0941 | 1039.8389 | 324.9497 | 611.8893 | 26.0779 | 12.5894 | 27.8764 | 70.1407 | 9474.569 | 327.4899 |  |  | 29.1123 | 0.87115 | 22.5566 | 4082.9834 | 2106.3056 | 1976.6779 | 936.839 | 17.2141 | 10.8954 | 12.2998 | 13.8877 | 11.1411 | 6.9632 | 3527.2309 | 7411.3186 | 11309.9211 | 2406.329 | 4997.284 | 9087.6067 | 0.095988 | 0.097931 | 0.090268 | 16.8334 | 9.9639 | 11.4088 | 10.887 | 25.8868 | 85.8031 | 126.0397 | 99.1066 | 67.1999 | 99.48% | 99.44% | 99.23% | 99.55% | 99.48% | 99.06% | 125.0161 | 122.5358 | 132.9379 |  |  |  | 29.9167 | 24 | 15 | 2333.5 | 1152 | 360 | 3845.5 | 106.1076 | 14 | 31 | 78 | 29 | 98.48% | 0.095694 | 0.096034 | 40.4093 | 38.2061 | 113.5513 | 22.7895 | 98.48% | 3807.9777 | 99.32% | 99.45% | 85.01% |  |  | 99.4% | 0.87115
2021-07-19 | 158.7019 | 141.3962 | 141.3962 | 130.3204 | 117.7614 | 14.0691 | 14.0691 | 3472.3646 | 1017.8534 | 318.0792 | 611.853 | 24.6633 | 11.9064 | 26.3643 | 66.3359 | 8826.3968 | 322.77 |  |  | 29.0452 | 0.87308 | 21.1304 | 4084.2176 | 2136.432 | 1947.7856 | 929.9322 | 17.3058 | 11.0758 | 12.5003 | 14.0864 | 10.9056 | 6.816 | 3356.7886 | 7002.0909 | 10607.7275 | 2270.9639 | 4740.6501 | 8556.7214 | 0.098637 | 0.096942 | 0.088136 | 17.0396 | 10.3185 | 11.6732 | 11.0908 | 25.3184 | 84.5485 | 124.6847 | 98.2178 | 67.5199 | 99.48% | 99.44% | 99.22% | 99.51% | 99.47% | 99.01% | 121.6579 | 123.785 | 136.1537 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 103.7256 | 14 | 31 | 78 | 29 | 98.47% | 0.096415 | 0.097178 | 40.8818 | 39.0312 | 112.8814 | 23.045 | 98.47% | 3570.697 | 99.31% | 99.42% | 85.02% |  |  | 99.4% | 0.87308
2021-07-18 | 159.3179 | 141.9383 | 141.9383 | 130.8254 | 118.2515 | 13.915 | 13.915 | 3473.3031 | 1018.1285 | 318.1652 | 613.9201 | 25.0353 | 12.086 | 26.7618 | 67.3362 | 8961.388 | 323.6061 |  |  | 28.9544 | 0.87571 | 21.449 | 4087.2232 | 2137.0094 | 1950.2138 | 932.0853 | 17.3796 | 11.1129 | 12.488 | 14.0902 | 10.9085 | 6.8178 | 3405.2655 | 7095.6477 | 10738.0822 | 2304.4175 | 4806.8616 | 8666.7762 | 0.098513 | 0.096916 | 0.088286 | 17.0892 | 10.3284 | 11.6139 | 11.131 | 25.4294 | 85.0118 | 125.2515 | 98.5664 | 67.6263 | 99.48% | 99.44% | 99.22% | 99.52% | 99.47% | 99.02% | 121.8112 | 123.8179 | 135.9222 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 104.4309 | 14 | 31 | 78 | 29 | 98.47% | 0.096366 | 0.097108 | 40.9805 | 39.0315 | 113.325 | 23.1447 | 98.47% | 3620.7698 | 99.31% | 99.42% | 84.98% |  |  | 99.39% | 0.87571
2021-07-17 | 160.7081 | 143.5375 | 143.5375 | 132.6412 | 120.019 | 14.1173 | 14.1173 | 3470.6895 | 1017.3624 | 317.9258 | 612.2843 | 25.6435 | 12.3796 | 27.4121 | 68.9723 | 9306.9361 | 326.6205 |  |  | 28.8849 | 0.87773 | 21.9701 | 4082.9739 | 2135.4013 | 1947.5725 | 930.2101 | 17.1706 | 10.8963 | 12.2828 | 14.0796 | 10.9003 | 6.8127 | 3525.8774 | 7352.1176 | 11133.8566 | 2385.5641 | 4978.6487 | 8982.9079 | 0.097971 | 0.096432 | 0.088401 | 16.9127 | 10.151 | 11.4622 | 11.0308 | 25.1875 | 84.1434 | 126.1397 | 99.2159 | 67.6432 | 99.48% | 99.45% | 99.23% | 99.54% | 99.49% | 99.06% | 122.4847 | 124.4406 | 135.7452 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 105.8903 | 14 | 31 | 78 | 29 | 98.48% | 0.095947 | 0.096643 | 40.3498 | 38.5258 | 113.8924 | 22.9256 | 98.48% | 3750.0112 | 99.32% | 99.45% | 85% |  |  | 99.4% | 0.87773
2021-07-16 | 161.0339 | 143.7688 | 143.7688 | 132.8104 | 120.4238 | 14.0746 | 14.0746 | 3470.5669 | 1034.79 | 311.1362 | 612.3112 | 25.9526 | 12.5289 | 27.7425 | 69.8036 | 9447.8482 | 326.8073 |  |  | 28.8088 | 0.87995 | 22.1996 | 4082.8781 | 2124.6407 | 1958.2374 | 923.4474 | 17.2652 | 10.9584 | 12.2736 | 14.0086 | 11.087 | 6.6672 | 3571.5823 | 7542.713 | 11339.9531 | 2423.8694 | 5071.3992 | 9184.7004 | 0.097623 | 0.098549 | 0.087606 | 16.9612 | 10.188 | 11.529 | 10.9596 | 25.5179 | 81.7138 | 126.27 | 98.9967 | 66.968 | 99.48% | 99.45% | 99.24% | 99.55% | 99.5% | 99.11% | 122.9218 | 121.7668 | 136.9769 |  |  |  | 31.1667 | 24.6667 | 14.8333 | 2431 | 1184 | 356 | 3971 | 106.3745 | 14 | 31 | 78 | 29 | 98.49% | 0.096317 | 0.097001 | 40.4972 | 38.6782 | 113.8065 | 22.8373 | 98.49% | 3819.3696 | 99.32% | 99.46% | 85% |  |  | 99.4% | 0.87995
2021-07-15 | 160.2494 | 143.1671 | 143.1671 | 132.3134 | 119.9107 | 14.0851 | 14.0851 | 3455.8193 | 1112.2177 | 278.0544 | 609.8968 | 25.974 | 12.5392 | 27.7653 | 69.8611 | 9447.536 | 323.0684 |  |  | 28.7992 | 0.88023 | 22.0516 | 4065.7161 | 2065.5472 | 2000.1689 | 887.9512 | 17.0824 | 10.8537 | 12.218 | 13.619 | 11.9166 | 5.9583 | 3514.894 | 7882.7536 | 11444.683 | 2419.3645 | 5123.3538 | 9443.3959 | 0.095453 | 0.10684 | 0.08049 | 16.6789 | 10.057 | 11.9153 | 10.6867 | 27.1801 | 71.106 | 125.5891 | 98.1772 | 65.1593 | 99.48% | 99.46% | 99.26% | 99.56% | 99.47% | 99.25% | 125.7168 | 112.3166 | 149.0871 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 105.8596 | 14 | 31 | 78 | 29 | 98.5% | 0.096703 | 0.097914 | 40.1541 | 38.6512 | 112.8848 | 22.5571 | 98.5% | 3854.7659 | 99.33% | 99.48% | 85% |  |  | 99.41% | 0.88023
2021-07-14 | 160.7341 | 143.521 | 143.521 | 132.6165 | 120.1613 | 14.2936 | 14.2936 | 3467.7416 | 1116.0548 | 279.0137 | 612.8519 | 26.0051 | 12.5542 | 27.7986 | 69.9447 | 9407.3997 | 326.3985 |  |  | 28.8289 | 0.87936 | 22.078 | 4080.5935 | 2072.6731 | 2007.9203 | 891.8656 | 17.2132 | 10.9045 | 12.3131 | 13.666 | 11.9577 | 5.9789 | 3506.5211 | 7859.6938 | 11406.1407 | 2413.9071 | 5109.9428 | 9413.8112 | 0.095507 | 0.1069 | 0.080421 | 16.713 | 10.0431 | 11.9258 | 10.7502 | 27.3513 | 71.5909 | 125.8272 | 98.3644 | 65.376 | 99.48% | 99.46% | 99.26% | 99.55% | 99.46% | 99.24% | 125.6455 | 112.2542 | 149.2151 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 105.9008 | 14 | 31 | 78 | 29 | 98.5% | 0.096739 | 0.09796 | 40.4307 | 38.682 | 113.1515 | 22.6984 | 98.5% | 3844.8075 | 99.32% | 99.48% | 84.98% |  |  | 99.41% | 0.87936
2021-07-13 | 160.5722 | 143.3559 | 143.3559 | 132.307 | 119.8409 | 14.3678 | 14.3678 | 3472.7945 | 1117.681 | 279.4202 | 611.77 | 25.7704 | 12.4409 | 27.5477 | 69.3136 | 9190.3841 | 327.2658 |  |  | 28.73 | 0.88225 | 21.8788 | 4084.5645 | 2075.6933 | 2008.8712 | 891.1902 | 17.2163 | 11.0489 | 12.2891 | 13.6859 | 11.9752 | 5.9876 | 3424.6654 | 7685.1407 | 11163.599 | 2356.9761 | 4993.1704 | 9208.9122 | 0.095925 | 0.10711 | 0.080029 | 16.6958 | 10.1747 | 11.9234 | 10.9622 | 27.87 | 72.8676 | 125.8736 | 98.6356 | 66.0082 | 99.47% | 99.45% | 99.25% | 99.53% | 99.44% | 99.21% | 125.0983 | 112.032 | 149.9465 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 105.4743 | 14 | 31 | 78 | 29 | 98.48% | 0.096961 | 0.098246 | 40.5542 | 38.7939 | 113.4139 | 23.1303 | 98.48% | 3756.7117 | 99.31% | 99.45% | 85.02% |  |  | 99.39% | 0.88225
2021-07-12 | 159.1068 | 141.8288 | 141.8288 | 130.6747 | 118.1335 | 14.2644 | 14.2644 | 3469.121 | 1116.4987 | 279.1247 | 611.9494 | 24.5937 | 11.8728 | 26.2898 | 66.1486 | 8807.8372 | 323.3113 |  |  | 28.5381 | 0.88789 | 20.8798 | 4081.0703 | 2073.4976 | 2007.5727 | 891.074 | 17.278 | 11.1542 | 12.4731 | 13.6714 | 11.9625 | 5.9812 | 3297.7556 | 7396.8397 | 10740.5425 | 2269.8532 | 4807.1477 | 8861.7984 | 0.097177 | 0.10829 | 0.080268 | 16.7755 | 10.2792 | 12.1012 | 10.9211 | 27.7738 | 72.649 | 124.9135 | 98.083 | 66.1614 | 99.48% | 99.45% | 99.25% | 99.52% | 99.42% | 99.18% | 123.4864 | 110.8142 | 149.4984 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 103.8842 | 14 | 31 | 78 | 29 | 98.49% | 0.098027 | 0.099393 | 40.9053 | 39.1558 | 112.8085 | 23.0499 | 98.49% | 3616.8401 | 99.32% | 99.43% | 85.01% |  |  | 99.4% | 0.88789
2021-07-11 | 159.2141 | 142.1289 | 142.1289 | 131.1961 | 118.7021 | 14.2008 | 14.2008 | 3462.4064 | 1114.3377 | 278.5844 | 610.376 | 25.3511 | 12.2385 | 27.0995 | 68.1858 | 9106.8917 | 323.1332 |  |  | 28.6527 | 0.88451 | 21.5228 | 4072.7824 | 2069.4843 | 2003.2981 | 888.9604 | 17.0852 | 10.9328 | 12.228 | 13.645 | 11.9393 | 5.9697 | 3395.2533 | 7617.3318 | 11062.8711 | 2336.8391 | 4949.7788 | 9126.7969 | 0.096671 | 0.10793 | 0.08067 | 16.6398 | 10.1086 | 11.9072 | 10.8721 | 27.6449 | 72.2956 | 124.8477 | 97.8483 | 65.4552 | 99.48% | 99.45% | 99.25% | 99.53% | 99.44% | 99.21% | 124.1323 | 111.1858 | 148.7547 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 104.479 | 14 | 31 | 78 | 29 | 98.49% | 0.097713 | 0.099006 | 40.246 | 38.6556 | 112.4973 | 22.9433 | 98.49% | 3724.1036 | 99.32% | 99.45% | 85.01% |  |  | 99.4% | 0.88451
2021-07-10 | 160.1271 | 143.0835 | 143.0835 | 132.1102 | 119.7354 | 14.1596 | 14.1596 | 3468.6104 | 1116.3344 | 279.0836 | 612.7344 | 26.0471 | 12.5744 | 27.8434 | 70.0576 | 9470.2072 | 339.4745 |  |  | 28.7069 | 0.88293 | 22.1137 | 4081.3448 | 2073.1924 | 2008.1524 | 891.818 | 17.0436 | 10.9733 | 12.2037 | 13.6694 | 11.9607 | 5.9804 | 3523.6016 | 7899.4213 | 11465.48 | 2425.5571 | 5135.2401 | 9462.0468 | 0.096259 | 0.10787 | 0.081481 | 16.5444 | 10.1056 | 11.8218 | 10.7619 | 27.3778 | 71.648 | 125.3808 | 97.9002 | 64.8032 | 99.48% | 99.46% | 99.26% | 99.56% | 99.47% | 99.24% | 124.6631 | 111.2456 | 147.2739 |  |  |  | 32 | 28 | 14 | 2496 | 1344 | 336 | 4176 | 105.5399 | 14 | 31 | 78 | 29 | 98.5% | 0.09761 | 0.098807 | 40.2206 | 38.4718 | 112.6168 | 22.7207 | 98.5% | 3863.7933 | 99.33% | 99.48% | 84.99% |  |  | 99.41% | 0.88293
2021-07-09 | 161.9012 | 144.824 | 144.824 | 133.8675 | 121.4227 | 14.3513 | 14.3513 | 3468.8024 | 1112.6676 | 280.2898 | 613.0631 | 25.432 | 12.1737 | 26.8744 | 67.3995 | 9624.8763 | 349.9898 |  |  | 28.5508 | 0.88751 | 21.3516 | 4081.8655 | 2075.845 | 2006.0206 | 893.353 | 17.0772 | 10.9565 | 12.2684 | 13.6869 | 11.9214 | 6.0062 | 3610.7122 | 8074.368 | 11735.1198 | 2483.6013 | 5256.4562 | 9677.681 | 0.095909 | 0.10704 | 0.081704 | 16.5836 | 10.0932 | 11.8625 | 10.2413 | 25.8645 | 68.0365 | 126.6541 | 98.8465 | 65.2424 | 99.51% | 99.49% | 99.3% | 99.59% | 99.51% | 99.3% | 125.1185 | 112.1088 | 146.8711 |  |  |  | 32 | 27.8724 | 14.0425 | 2496 | 1337.8737 | 337.0211 | 4170.8947 | 107.064 | 13.8816 | 30.6447 | 76.8553 | 29 | 98.57% | 0.097198 | 0.098331 | 40.3021 | 38.5392 | 113.6394 | 21.7901 | 98.57% | 3954.3375 | 99.36% | 99.52% | 84.98% |  |  | 99.43% | 0.88751
2021-07-08 | 163.3385 | 146.1698 | 146.1698 | 135.153 | 122.7625 | 14.282 | 14.282 | 3473.3311 | 1027.6127 | 308.2838 | 614.3322 | 26.6856 | 10.1221 | 20.2442 | 45.0894 | 9800.9242 | 355.8837 |  |  | 28.4124 | 0.8916 | 16.2204 | 4087.6633 | 2137.4345 | 1950.2288 | 922.616 | 17.1686 | 11.0168 | 12.3057 | 14.093 | 11.0101 | 6.6061 | 3762.9998 | 7931.6931 | 11889.3438 | 2545.0223 | 5338.6962 | 9644.9745 | 0.098322 | 0.098376 | 0.088337 | 16.8799 | 10.2897 | 11.5457 | 8.5959 | 17.7986 | 50.4627 | 127.7976 | 99.7871 | 66.6763 | 99.6% | 99.62% | 99.53% | 99.66% | 99.67% | 99.48% | 122.0477 | 121.9808 | 135.843 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 108.5306 | 11 | 22 | 49 | 29 | 98.52% | 0.096742 | 0.097452 | 40.4912 | 38.7153 | 114.837 | 22.7271 | 98.52% | 4001.7263 | 99.33% | 99.63% | 84.97% |  |  | 99.41% | 0.8916
2021-07-07 | 161.8293 | 144.7387 | 144.7387 | 133.8441 | 121.3343 | 14.1417 | 14.1417 | 3463.7315 | 1024.7726 | 307.4318 | 611.9169 | 26.166 | 9.925 | 19.8501 | 44.2115 | 9497.8358 | 351.9341 |  |  | 28.2561 | 0.89625 | 15.9046 | 4075.6485 | 2131.5271 | 1944.1214 | 919.3487 | 17.0907 | 10.8946 | 12.3277 | 14.054 | 10.9797 | 6.5878 | 3657.5611 | 7712.4171 | 11564.9828 | 2473.4809 | 5189.9827 | 9379.9705 | 0.099318 | 0.0991 | 0.08843 | 16.8791 | 10.2255 | 11.6308 | 8.6934 | 17.9958 | 51.002 | 126.8245 | 99.2991 | 66.7687 | 99.6% | 99.62% | 99.53% | 99.65% | 99.65% | 99.46% | 120.8243 | 121.0894 | 135.7009 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.1499 | 11 | 22 | 49 | 29 | 98.5% | 0.097506 | 0.098287 | 40.3129 | 38.7354 | 114.1837 | 22.9794 | 98.5% | 3890.1817 | 99.33% | 99.62% | 84.99% |  |  | 99.4% | 0.89625
2021-07-06 | 159.313 | 141.9343 | 141.9343 | 130.5482 | 118.0092 | 14.0331 | 14.0331 | 3472.5545 | 1018.3282 | 317.6594 | 613.8992 | 24.5541 | 12.1116 | 24.2233 | 53.9518 | 8611.8917 | 341.1645 |  |  | 28.1071 | 0.90071 | 19.4908 | 4086.4537 | 2136.5668 | 1949.8869 | 931.5587 | 17.3787 | 11.3862 | 12.6533 | 14.0873 | 10.9107 | 6.807 | 3357.2594 | 7000.7496 | 10595.3391 | 2272.038 | 4740.6239 | 8551.1923 | 0.10127 | 0.099642 | 0.090483 | 17.093 | 10.5871 | 11.7739 | 11.6342 | 24.0097 | 70.8923 | 125.291 | 98.6262 | 67.7594 | 99.47% | 99.49% | 99.37% | 99.49% | 99.49% | 99.17% | 118.4926 | 120.4312 | 132.6211 |  |  |  | 31.0429 | 24.0429 | 15 | 2421.3482 | 1154.0604 | 360 | 3935.4086 | 103.9564 | 11 | 22 | 49 | 22.3005 | 98.47% | 0.099024 | 0.099807 | 41.4181 | 39.454 | 113.3997 | 23.6724 | 98.47% | 3570.3512 | 99.31% | 99.44% | 84.98% |  |  | 99.38% | 0.90071
2021-07-05 | 159.1112 | 141.9295 | 141.9295 | 130.7615 | 118.065 | 13.8889 | 13.8889 | 3468.6046 | 1016.7513 | 317.7348 | 612.0574 | 25.4298 | 12.7149 | 25.4298 | 56.6391 | 8737.0177 | 335.0292 |  |  | 28.0748 | 0.90168 | 20.4656 | 4080.662 | 2134.1186 | 1946.5435 | 929.7922 | 17.1817 | 11.168 | 12.596 | 14.0711 | 10.8938 | 6.8086 | 3396.6324 | 7083.1277 | 10730.7591 | 2298.4939 | 4796.3024 | 8655.8502 | 0.10134 | 0.099619 | 0.090912 | 16.9377 | 10.4119 | 11.7618 | 12.0722 | 24.9012 | 73.6202 | 125.2025 | 98.6022 | 67.5283 | 99.45% | 99.47% | 99.35% | 99.47% | 99.48% | 99.15% | 118.4173 | 120.4589 | 131.9952 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 104.1386 | 11 | 22 | 49 | 22 | 98.44% | 0.099119 | 0.099878 | 40.9458 | 39.1114 | 113.1988 | 24.2256 | 98.44% | 3613.0292 | 99.3% | 99.42% | 85% |  |  | 99.37% | 0.90168
2021-07-04 | 160.0851 | 142.8759 | 142.8759 | 131.8011 | 119.3324 | 14.0364 | 14.0364 | 3469.9763 | 1017.1534 | 317.8604 | 612.2816 | 25.3986 | 12.6993 | 25.3986 | 56.5695 | 9125.8821 | 337.822 |  |  | 28.2349 | 0.89688 | 20.4405 | 4082.2579 | 2134.9625 | 1947.2954 | 930.1421 | 17.2092 | 11.0748 | 12.406 | 14.0767 | 10.8981 | 6.8113 | 3521.1647 | 7343.9465 | 11127.1217 | 2382.5586 | 4972.4867 | 8975.0419 | 0.10052 | 0.099164 | 0.091263 | 16.9549 | 10.3191 | 11.5779 | 11.5747 | 23.8713 | 70.5656 | 125.5948 | 98.5666 | 66.938 | 99.47% | 99.49% | 99.37% | 99.51% | 99.52% | 99.21% | 119.376 | 121.0113 | 131.4887 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 105.2927 | 11 | 22 | 49 | 22 | 98.49% | 0.098606 | 0.099276 | 40.69 | 38.8519 | 113.2936 | 23.2243 | 98.49% | 3745.6352 | 99.32% | 99.47% | 85% |  |  | 99.39% | 0.89688
2021-07-03 | 161.3074 | 144.1702 | 144.1702 | 133.172 | 120.7033 | 14.1781 | 14.1781 | 3470.3813 | 1017.2721 | 317.8975 | 611.0494 | 26.2055 | 13.1028 | 26.2055 | 58.3669 | 9452.6282 | 339.393 |  |  | 28.2468 | 0.89653 | 21.0899 | 4081.4308 | 2135.2117 | 1946.2191 | 928.947 | 17.1372 | 10.9982 | 12.3565 | 14.0783 | 10.8993 | 6.8121 | 3629.6558 | 7575.7253 | 11486.6194 | 2455.4943 | 5127.3311 | 9261.4218 | 0.099895 | 0.098715 | 0.091502 | 16.8919 | 10.2598 | 11.559 | 11.5845 | 23.8792 | 70.5365 | 126.3488 | 98.9874 | 66.7443 | 99.47% | 99.49% | 99.37% | 99.53% | 99.53% | 99.24% | 120.1263 | 121.5619 | 131.145 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 106.5816 | 11 | 22 | 49 | 22 | 98.49% | 0.098174 | 0.09878 | 40.4919 | 38.7107 | 113.7212 | 23.2329 | 98.49% | 3862.133 | 99.32% | 99.48% | 85.03% |  |  | 99.39% | 0.89653
2021-07-02 | 161.9132 | 144.796 | 144.796 | 133.7812 | 121.3813 | 14.3484 | 14.3484 | 3471.811 | 1023.583 | 311.8831 | 612.4761 | 26.6184 | 11.8872 | 24.912 | 57.8645 | 9652.9645 | 340.7059 |  |  | 28.2713 | 0.8958 | 19.8575 | 4084.2872 | 2136.345 | 1947.9422 | 924.3592 | 17.1171 | 11.0148 | 12.3095 | 14.0858 | 10.967 | 6.6832 | 3689.9845 | 7748.4777 | 11664.6664 | 2495.9706 | 5226.4444 | 9441.0546 | 0.099679 | 0.099302 | 0.090276 | 16.853 | 10.2907 | 11.5506 | 10.3364 | 22.3899 | 67.2462 | 126.5858 | 98.9326 | 66.317 | 99.52% | 99.52% | 99.39% | 99.59% | 99.57% | 99.29% | 120.3859 | 120.8439 | 132.9264 |  |  |  | 31.6146 | 24.6146 | 15 | 2465.9375 | 1181.5 | 360 | 4007.4375 | 107.0614 | 12.8438 | 26.9167 | 62.5208 | 28.7604 | 98.49% | 0.098054 | 0.098723 | 40.4415 | 38.6943 | 113.8015 | 23.2123 | 98.49% | 3924.885 | 99.32% | 99.53% | 85% |  |  | 99.39% | 0.8958
2021-07-01 | 161.8881 | 144.8069 | 144.8069 | 133.8787 | 121.4566 | 14.1884 | 14.1884 | 3465.086 | 1025.1734 | 307.552 | 613.0141 | 26.6736 | 11.3161 | 24.2488 | 57.3887 | 9776.8382 | 338.8303 |  |  | 28.2514 | 0.89639 | 19.2316 | 4078.1001 | 2132.3606 | 1945.7395 | 920.5661 | 17.0812 | 10.9282 | 12.3022 | 14.0595 | 10.984 | 6.5904 | 3719.9802 | 7835.6711 | 11738.0715 | 2516.5226 | 5276.0852 | 9525.4343 | 0.099522 | 0.09956 | 0.089321 | 16.8527 | 10.2419 | 11.5805 | 9.7477 | 21.6367 | 65.2279 | 126.6331 | 98.8953 | 66.1391 | 99.55% | 99.54% | 99.4% | 99.61% | 99.59% | 99.32% | 120.5758 | 120.5309 | 134.3475 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.2649 | 14 | 30 | 71 | 33 | 98.5% | 0.097902 | 0.098628 | 40.3115 | 38.675 | 113.7922 | 23.0536 | 98.5% | 3955.054 | 99.33% | 99.56% | 84.97% |  |  | 99.4% | 0.89639
2021-06-30 | 162.2474 | 145.2536 | 145.2536 | 134.3957 | 121.9064 | 14.0808 | 14.0808 | 3463.0142 | 1024.5604 | 307.3681 | 612.2643 | 26.6439 | 11.3035 | 24.2217 | 57.3247 | 9836.2488 | 338.9758 |  |  | 28.1282 | 0.90008 | 19.2102 | 4075.2785 | 2131.0857 | 1944.1929 | 919.6324 | 16.9938 | 10.8579 | 12.2367 | 14.0511 | 10.9774 | 6.5865 | 3733.6729 | 7866.3642 | 11786.648 | 2525.618 | 5296.0522 | 9563.7293 | 0.099506 | 0.099417 | 0.089096 | 16.7848 | 10.1892 | 11.5378 | 9.7358 | 21.6066 | 65.1219 | 127.0981 | 99.3847 | 66.5382 | 99.55% | 99.54% | 99.4% | 99.61% | 99.59% | 99.32% | 120.5954 | 120.7038 | 134.6856 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.7889 | 14 | 30 | 71 | 33 | 98.51% | 0.097812 | 0.098556 | 40.0884 | 38.5118 | 114.2256 | 23.0219 | 98.51% | 3969.9575 | 99.33% | 99.56% | 84.98% |  |  | 99.4% | 0.90008
2021-06-29 | 161.9367 | 144.8389 | 144.8389 | 133.8334 | 121.3306 | 14.2218 | 14.2218 | 3467.9539 | 1026.0219 | 307.8066 | 612.2588 | 25.9506 | 11.0093 | 23.5915 | 55.8331 | 9555.0931 | 338.6441 |  |  | 27.9319 | 0.90598 | 18.7103 | 4080.2127 | 2134.1255 | 1946.0872 | 920.0654 | 17.0977 | 11.0055 | 12.3515 | 14.0712 | 10.9931 | 6.5959 | 3643.6419 | 7680.5843 | 11513.8464 | 2464.3839 | 5169.4993 | 9339.9679 | 0.10046 | 0.10021 | 0.089271 | 16.8587 | 10.3151 | 11.6412 | 9.7958 | 21.7321 | 65.4665 | 126.8991 | 99.3849 | 66.9396 | 99.55% | 99.54% | 99.4% | 99.6% | 99.58% | 99.3% | 119.451 | 119.7461 | 134.4228 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.0952 | 14 | 30 | 71 | 33 | 98.51% | 0.09859 | 0.099393 | 40.4547 | 38.815 | 114.2547 | 23.1563 | 98.51% | 3874.9728 | 99.33% | 99.55% | 84.99% |  |  | 99.39% | 0.90598
2021-06-28 | 159.7773 | 142.589 | 142.589 | 131.4008 | 118.798 | 14.112 | 14.112 | 3471.7697 | 1027.1508 | 308.1452 | 612.4493 | 25.0708 | 10.6361 | 22.7917 | 53.9403 | 9020.8045 | 333.2816 |  |  | 27.9857 | 0.90436 | 18.076 | 4084.219 | 2136.4736 | 1947.7453 | 920.5946 | 17.1883 | 11.1883 | 12.4972 | 14.0866 | 11.0052 | 6.6031 | 3457.7042 | 7290.1983 | 10931.0195 | 2338.5337 | 4906.1563 | 8866.1453 | 0.10156 | 0.10108 | 0.089226 | 16.9241 | 10.4744 | 11.7702 | 9.9661 | 22.1069 | 66.5808 | 125.4317 | 98.4661 | 66.9264 | 99.55% | 99.54% | 99.39% | 99.57% | 99.55% | 99.25% | 118.1519 | 118.7217 | 134.4898 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 104.6837 | 14 | 30 | 71 | 33 | 98.48% | 0.099434 | 0.10032 | 40.8737 | 39.1687 | 113.2881 | 23.5558 | 98.48% | 3677.5592 | 99.32% | 99.51% | 85% |  |  | 99.38% | 0.90436
2021-06-27 | 160.2244 | 143.0922 | 143.0922 | 131.8882 | 119.3912 | 13.9052 | 13.9052 | 3472.3989 | 1027.3369 | 308.2011 | 612.6875 | 25.2722 | 10.7215 | 22.9747 | 54.3735 | 9241.121 | 333.148 |  |  | 28.0002 | 0.90392 | 18.2212 | 4085.0864 | 2136.8609 | 1948.2256 | 920.8886 | 17.1322 | 11.204 | 12.5509 | 14.0892 | 11.0072 | 6.6043 | 3530.3959 | 7443.2506 | 11160.0879 | 2387.6851 | 5009.2368 | 9052.1244 | 0.10118 | 0.10085 | 0.089441 | 16.8632 | 10.4849 | 11.8147 | 9.8364 | 21.8193 | 65.7169 | 125.8683 | 98.6537 | 66.7458 | 99.55% | 99.54% | 99.4% | 99.59% | 99.56% | 99.27% | 118.5987 | 118.9836 | 134.1671 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 105.4768 | 14 | 30 | 71 | 33 | 98.5% | 0.099198 | 0.10004 | 40.8871 | 39.1628 | 113.4743 | 23.2495 | 98.5% | 3754.8104 | 99.33% | 99.53% | 85% |  |  | 99.39% | 0.90392
2021-06-26 | 161.5881 | 144.5497 | 144.5497 | 133.5256 | 121.1548 | 14.0152 | 14.0152 | 3462.8169 | 1024.502 | 307.3506 | 611.5928 | 26.3509 | 11.1792 | 23.9554 | 56.6944 | 9713.1053 | 334.6965 |  |  | 27.9057 | 0.90677 | 18.9989 | 4074.4097 | 2130.9642 | 1943.4455 | 918.9434 | 17.0384 | 11.0241 | 12.3158 | 14.0503 | 10.9768 | 6.5861 | 3692.5985 | 7782.657 | 11665.2719 | 2497.5951 | 5238.6256 | 9463.4918 | 0.10062 | 0.10059 | 0.090089 | 16.8356 | 10.353 | 11.6279 | 9.8087 | 21.7628 | 65.5687 | 126.6217 | 98.9491 | 66.2911 | 99.55% | 99.54% | 99.4% | 99.61% | 99.58% | 99.31% | 119.2627 | 119.2939 | 133.2018 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.1271 | 14 | 30 | 71 | 33 | 98.51% | 0.098925 | 0.099676 | 40.3784 | 38.8165 | 113.8193 | 23.1889 | 98.51% | 3926.8257 | 99.33% | 99.55% | 84.99% |  |  | 99.39% | 0.90677
2021-06-25 | 162.7684 | 145.675 | 145.675 | 134.5647 | 122.1741 | 14.3479 | 14.3479 | 3471.3534 | 1027.0276 | 308.1083 | 614.5857 | 26.7887 | 11.3649 | 24.3533 | 57.6362 | 9852.0157 | 339.7552 |  |  | 27.8495 | 0.90848 | 19.3145 | 4085.9392 | 2136.2175 | 1949.7217 | 922.694 | 17.0934 | 11.1103 | 12.4088 | 14.085 | 11.0039 | 6.6023 | 3747.6599 | 7891.9792 | 11819.5451 | 2535.4083 | 5314.7543 | 9592.796 | 0.10055 | 0.10065 | 0.090406 | 16.8153 | 10.3793 | 11.6387 | 9.8656 | 21.9023 | 66.0453 | 127.2535 | 99.3199 | 66.3456 | 99.55% | 99.54% | 99.4% | 99.61% | 99.59% | 99.31% | 119.3389 | 119.2226 | 132.7343 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.8434 | 14 | 30 | 71 | 33 | 98.51% | 0.098962 | 0.099682 | 40.6126 | 38.8333 | 114.2631 | 23.3363 | 98.51% | 3984.0954 | 99.33% | 99.56% | 84.96% |  |  | 99.39% | 0.90848
2021-06-24 | 162.2123 | 145.1765 | 145.1765 | 134.2468 | 121.8349 | 14.2457 | 14.2457 | 3469.0707 | 1026.3523 | 307.9057 | 612.3346 | 27.0494 | 11.4755 | 24.5903 | 58.1972 | 9884.2459 | 336.9432 |  |  | 27.8397 | 0.90877 | 19.5025 | 4081.4053 | 2134.8128 | 1946.5926 | 920.2403 | 17.0358 | 10.9296 | 12.3621 | 14.0757 | 10.9966 | 6.598 | 3758.2206 | 7922.3723 | 11876.786 | 2541.883 | 5332.138 | 9634.1752 | 0.10088 | 0.10102 | 0.090966 | 16.7905 | 10.2404 | 11.6483 | 9.933 | 22.0361 | 66.3798 | 126.7966 | 98.9282 | 65.9153 | 99.55% | 99.54% | 99.4% | 99.61% | 99.59% | 99.31% | 118.9496 | 118.7915 | 131.9168 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 107.5547 | 14 | 30 | 71 | 33 | 98.5% | 0.099339 | 0.10004 | 40.3275 | 38.6792 | 113.8025 | 23.4802 | 98.5% | 3996.8956 | 99.32% | 99.55% | 85% |  |  | 99.39% | 0.90877
2021-06-23 | 160.4929 | 143.7126 | 143.7126 | 132.9343 | 120.6115 | 14.1927 | 14.1927 | 3444.9466 | 1019.215 | 305.7645 | 607.1846 | 26.9208 | 11.421 | 24.4735 | 57.9206 | 9767.408 | 329.6675 |  |  | 27.8351 | 0.90891 | 19.4098 | 4052.1312 | 2119.9671 | 1932.1641 | 912.9491 | 16.7803 | 10.7782 | 12.1903 | 13.9778 | 10.9202 | 6.5521 | 3716.6822 | 7838.6583 | 11756.8625 | 2513.4802 | 5274.3393 | 9534.4819 | 0.10131 | 0.1014 | 0.091342 | 16.7203 | 10.2144 | 11.6277 | 9.9295 | 22.0209 | 66.301 | 125.3997 | 97.8814 | 65.1974 | 99.55% | 99.54% | 99.39% | 99.6% | 99.58% | 99.3% | 118.4449 | 118.3395 | 131.3738 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 106.4002 | 14 | 30 | 71 | 33 | 98.49% | 0.099747 | 0.10045 | 39.7489 | 38.5624 | 112.5418 | 23.4646 | 98.49% | 3953.4682 | 99.32% | 99.55% | 85.02% |  |  | 99.39% | 0.90891
2021-06-22 | 161.0994 | 144.0794 | 144.0794 | 133.1345 | 120.5157 | 14.3645 | 14.3645 | 3471.3635 | 984.4931 | 287.1438 | 611.9559 | 26.5874 | 11.2795 | 24.1704 | 57.2032 | 9549.646 | 338.1115 |  |  | 27.7333 | 0.91201 | 18.7341 | 4083.3195 | 2199.7267 | 1883.5928 | 899.0997 | 17.02 | 10.9449 | 12.3638 | 14.5037 | 10.5481 | 6.1531 | 3763.7236 | 7858.4463 | 11518.9691 | 2498.5057 | 5317.5796 | 9456.5379 | 0.10516 | 0.098388 | 0.085721 | 17.0332 | 10.7233 | 11.8997 | 10.2713 | 20.9073 | 62.21 | 125.7888 | 97.7754 | 65.464 | 99.55% | 99.55% | 99.4% | 99.59% | 99.61% | 99.34% | 114.1161 | 121.9656 | 139.9887 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 106.1981 | 14 | 30 | 71 | 33 | 98.47% | 0.099881 | 0.10163 | 40.3287 | 39.6562 | 113.3144 | 23.9145 | 98.47% | 3873.5604 | 99.31% | 99.56% | 85.01% |  |  | 99.37% | 0.91201
2021-06-21 | 158.4743 | 141.3689 | 141.3689 | 130.1241 | 117.6009 | 13.9982 | 13.9982 | 3471.111 | 984.4214 | 287.1229 | 612.4136 | 25.7728 | 10.9339 | 23.4298 | 55.4506 | 8975.5885 | 331.8284 |  |  | 27.5986 | 0.91612 | 18.1601 | 4083.5246 | 2199.5666 | 1883.9579 | 899.5365 | 17.1054 | 11.2448 | 12.5681 | 14.5026 | 10.5474 | 6.1526 | 3564.6449 | 7440.0273 | 10902.1994 | 2366.6491 | 5035.4927 | 8951.7038 | 0.10702 | 0.099937 | 0.086208 | 17.1162 | 11.0124 | 12.0855 | 10.5579 | 21.4971 | 63.9876 | 124.1449 | 96.688 | 65.3831 | 99.54% | 99.53% | 99.38% | 99.55% | 99.57% | 99.29% | 112.1271 | 120.0762 | 139.198 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 103.5709 | 14 | 30 | 71 | 33 | 98.44% | 0.10142 | 0.10329 | 40.9183 | 40.2141 | 112.1431 | 24.5879 | 98.44% | 3668.2459 | 99.3% | 99.52% | 85% |  |  | 99.36% | 0.91612
2021-06-20 | 158.4176 | 141.3413 | 141.3413 | 130.1432 | 117.5027 | 13.9307 | 13.9307 | 3472.8578 | 984.9168 | 287.2674 | 613.8014 | 25.7713 | 10.9333 | 23.4284 | 55.4473 | 9014.8615 | 332.0478 |  |  | 27.5927 | 0.9163 | 18.1591 | 4086.6593 | 2200.6736 | 1885.9857 | 901.0689 | 17.0763 | 11.1981 | 12.5323 | 14.5099 | 10.5527 | 6.1557 | 3576.8846 | 7461.0038 | 10926.9049 | 2375.1687 | 5051.4239 | 8974.6227 | 0.10711 | 0.10002 | 0.086383 | 17.065 | 10.9456 | 12.0163 | 10.5268 | 21.443 | 63.865 | 124.1275 | 96.6715 | 65.2963 | 99.54% | 99.54% | 99.38% | 99.56% | 99.58% | 99.29% | 112.0331 | 119.9718 | 138.9162 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 103.5616 | 14 | 30 | 71 | 33 | 98.44% | 0.10153 | 0.10339 | 40.8067 | 40.0269 | 112.1109 | 24.5247 | 98.44% | 3680.0586 | 99.3% | 99.52% | 84.98% |  |  | 99.36% | 0.9163
2021-06-19 | 159.0985 | 142.1597 | 142.1597 | 131.22 | 118.8068 | 13.9836 | 13.9836 | 3461.7827 | 981.7759 | 286.3513 | 610.3259 | 27.0412 | 11.472 | 24.5829 | 58.1796 | 9501.7141 | 334.0985 |  |  | 27.6438 | 0.91474 | 19.0539 | 4072.1085 | 2193.6555 | 1878.453 | 896.6772 | 16.9388 | 10.9396 | 12.3014 | 14.4637 | 10.519 | 6.1361 | 3737.7719 | 7803.3595 | 11437.2254 | 2481.4192 | 5280.646 | 9389.8653 | 0.10644 | 0.099788 | 0.087196 | 17.0219 | 10.762 | 11.8874 | 10.5209 | 21.4177 | 63.7355 | 124.2958 | 96.426 | 64.3714 | 99.54% | 99.53% | 99.38% | 99.58% | 99.59% | 99.32% | 112.736 | 120.255 | 137.6212 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 104.8036 | 14 | 30 | 71 | 33 | 98.44% | 0.10123 | 0.10296 | 40.1798 | 39.6712 | 111.8908 | 24.4978 | 98.44% | 3846.7435 | 99.3% | 99.54% | 85.01% |  |  | 99.36% | 0.91474
2021-06-18 | 159.7369 | 142.6539 | 142.6539 | 131.667 | 119.3269 | 14.0158 | 14.0158 | 3471.8861 | 985.9207 | 287.7384 | 612.9031 | 27.896 | 11.8646 | 25.4242 | 60.1705 | 9721.7386 | 341.038 |  |  | 27.582 | 0.91663 | 19.7186 | 4084.7892 | 2198.227 | 1886.5622 | 900.6415 | 17.083 | 10.9869 | 12.3351 | 14.4938 | 10.5634 | 6.1658 | 3789.2646 | 7909.4929 | 11594.4982 | 2517.3941 | 5352.9872 | 9518.2362 | 0.10658 | 0.10033 | 0.088046 | 17.0772 | 10.7383 | 11.8428 | 10.77 | 21.9889 | 65.4777 | 124.6519 | 96.5068 | 64.1908 | 99.53% | 99.53% | 99.37% | 99.57% | 99.59% | 99.31% | 112.5912 | 119.6026 | 136.2917 |  |  |  | 32.9583 | 24.0208 | 14.0208 | 2570.75 | 1153 | 336.5 | 4060.25 | 105.3227 | 14 | 30 | 71 | 32.9167 | 98.41% | 0.10162 | 0.10327 | 40.405 | 39.6582 | 112.1008 | 25.0333 | 98.41% | 3902.8315 | 99.29% | 99.54% | 85% |  |  | 99.34% | 0.91663
2021-06-17 | 160.565 | 143.638 | 143.638 | 132.7856 | 120.3643 | 14.2547 | 14.2547 | 3467.8924 | 1046.1214 | 313.8364 | 611.6327 | 27.1748 | 13.1189 | 28.1119 | 66.5315 | 9752.8096 | 341.104 |  |  | 27.6832 | 0.91353 | 22.4754 | 4079.5251 | 2107.9346 | 1971.5905 | 925.4691 | 16.927 | 10.8524 | 12.2641 | 13.8985 | 11.2084 | 6.7251 | 3575.2979 | 7584.9262 | 11442.7089 | 2436.9238 | 5086.7849 | 9250.9184 | 0.10099 | 0.10378 | 0.092526 | 16.5878 | 10.0093 | 11.505 | 11.7567 | 27.0565 | 80.974 | 125.7278 | 98.6637 | 66.3983 | 99.46% | 99.45% | 99.28% | 99.52% | 99.47% | 99.12% | 118.8285 | 115.6294 | 129.693 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 106.0801 | 14 | 30 | 71 | 29 | 98.43% | 0.10053 | 0.10106 | 40.0436 | 38.1021 | 113.0656 | 24.5903 | 98.43% | 3852.9296 | 99.29% | 99.44% | 85.01% |  |  | 99.36% | 0.91353
2021-06-16 | 160.4165 | 143.4293 | 143.4293 | 132.4579 | 120.0865 | 14.2151 | 14.2151 | 3470.0806 | 1046.7815 | 314.0344 | 612.7545 | 27.0397 | 13.0536 | 27.9721 | 66.2006 | 9710.3294 | 338.8578 |  |  | 27.7417 | 0.91175 | 22.3636 | 4082.8351 | 2109.2647 | 1973.5704 | 926.7889 | 16.9872 | 10.9714 | 12.3643 | 13.9072 | 11.2155 | 6.7293 | 3565.7708 | 7561.6127 | 11402.9841 | 2430.6779 | 5072.319 | 9220.7691 | 0.10094 | 0.10381 | 0.092563 | 16.6249 | 10.1018 | 11.5714 | 11.7127 | 26.963 | 80.7277 | 125.6196 | 98.5068 | 66.2843 | 99.46% | 99.45% | 99.28% | 99.52% | 99.47% | 99.12% | 118.8836 | 115.5984 | 129.6418 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 105.9308 | 14 | 30 | 71 | 29 | 98.44% | 0.10052 | 0.10105 | 40.3228 | 38.2981 | 112.9528 | 24.5049 | 98.44% | 3842.0409 | 99.3% | 99.44% | 84.99% |  |  | 99.36% | 0.91175
2021-06-15 | 159.361 | 142.3754 | 142.3754 | 131.2673 | 119.0087 | 14.2831 | 14.2831 | 3471.1312 | 1047.0984 | 314.1295 | 613.4084 | 26.7896 | 12.9329 | 27.7133 | 65.5883 | 9496.8824 | 335.4219 |  |  | 27.7451 | 0.91165 | 22.1567 | 4084.5395 | 2109.9033 | 1974.6363 | 927.5379 | 16.9856 | 11.1081 | 12.4889 | 13.9115 | 11.2189 | 6.7313 | 3503.8812 | 7428.1304 | 11198.5254 | 2388.6952 | 4983.6232 | 9056.8054 | 0.1017 | 0.10462 | 0.093122 | 16.612 | 10.218 | 11.6721 | 11.8106 | 27.1942 | 81.4443 | 124.7063 | 97.7587 | 65.8988 | 99.46% | 99.44% | 99.28% | 99.51% | 99.45% | 99.1% | 117.997 | 114.6991 | 128.8637 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 104.6547 | 14 | 30 | 71 | 29 | 98.42% | 0.10126 | 0.1018 | 40.5826 | 38.5021 | 112.1682 | 24.7145 | 98.42% | 3774.9278 | 99.29% | 99.42% | 84.98% |  |  | 99.35% | 0.91165
2021-06-14 | 157.7398 | 140.7453 | 140.7453 | 129.5647 | 117.0435 | 14.0147 | 14.0147 | 3469.237 | 1046.527 | 313.9581 | 612.3785 | 25.7919 | 12.4513 | 26.6813 | 63.1457 | 9016.0033 | 328.8964 |  |  | 27.4735 | 0.91996 | 21.3316 | 4081.6156 | 2108.7519 | 1972.8637 | 926.3366 | 16.9944 | 11.1806 | 12.6605 | 13.9039 | 11.2128 | 6.7277 | 3342.3043 | 7088.1229 | 10689.7327 | 2278.36 | 4754.5535 | 8643.6791 | 0.10324 | 0.1058 | 0.093229 | 16.64 | 10.3006 | 11.8582 | 12.0236 | 27.678 | 82.8631 | 123.8983 | 97.501 | 66.3868 | 99.45% | 99.44% | 99.27% | 99.47% | 99.42% | 99.04% | 116.2363 | 113.4245 | 128.7148 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 103.0331 | 14 | 30 | 71 | 29 | 98.41% | 0.10246 | 0.1031 | 40.8356 | 38.7988 | 111.7977 | 25.1545 | 98.41% | 3601.3734 | 99.28% | 99.39% | 85% |  |  | 99.34% | 0.91996
2021-06-13 | 157.6475 | 140.961 | 140.961 | 130.1128 | 117.5954 | 14.1052 | 14.1052 | 3442.3475 | 1038.4155 | 311.5247 | 606.8774 | 26.1303 | 12.6146 | 27.0313 | 63.9741 | 9281.3724 | 325.3019 |  |  | 27.3688 | 0.92319 | 21.6115 | 4049.2249 | 2092.4073 | 1956.8176 | 918.4021 | 16.6865 | 10.8482 | 12.2911 | 13.7961 | 11.1259 | 6.6755 | 3426.6264 | 7270.468 | 10969.7331 | 2335.5204 | 4875.5389 | 8867.9256 | 0.10306 | 0.10568 | 0.09376 | 16.5365 | 10.1196 | 11.6646 | 11.8325 | 27.2286 | 81.478 | 123.5846 | 97.1892 | 65.7292 | 99.46% | 99.45% | 99.28% | 99.49% | 99.44% | 99.08% | 116.439 | 113.5466 | 127.9862 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 103.5376 | 14 | 30 | 71 | 29 | 98.43% | 0.10241 | 0.10301 | 39.8257 | 38.3207 | 111.3166 | 24.7468 | 98.43% | 3692.9081 | 99.29% | 99.41% | 85.01% |  |  | 99.35% | 0.92319
2021-06-12 | 160.0592 | 143.2085 | 143.2085 | 132.3319 | 119.7872 | 14.2299 | 14.2299 | 3463.4049 | 1044.7677 | 313.4303 | 610.7483 | 27.0127 | 13.0406 | 27.9441 | 66.1345 | 9688.3722 | 332.5821 |  |  | 27.3156 | 0.92484 | 22.3413 | 4074.1532 | 2105.2069 | 1968.9463 | 924.1786 | 16.8507 | 10.8766 | 12.2791 | 13.8805 | 11.1939 | 6.7164 | 3561.6697 | 7556.4843 | 11400.4616 | 2427.5904 | 5067.5333 | 9216.4781 | 0.10243 | 0.10527 | 0.094003 | 16.5459 | 10.0521 | 11.5435 | 11.8612 | 27.2959 | 81.6852 | 125.3312 | 98.3423 | 66.0779 | 99.46% | 99.45% | 99.28% | 99.51% | 99.46% | 99.11% | 117.1578 | 113.9919 | 127.6553 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 105.5775 | 14 | 30 | 71 | 29 | 98.44% | 0.10199 | 0.10252 | 40.0064 | 38.1415 | 112.6821 | 24.8079 | 98.44% | 3838.3322 | 99.3% | 99.43% | 85.01% |  |  | 99.35% | 0.92484
2021-06-11 | 159.7267 | 142.7535 | 142.7535 | 131.905 | 119.3566 | 14.1974 | 14.1974 | 3467.2038 | 1045.9137 | 313.7741 | 612.5578 | 27.5722 | 13.3107 | 28.523 | 67.5044 | 9657.1015 | 332.294 |  |  | 27.1588 | 0.92971 | 22.8041 | 4079.7617 | 2107.5161 | 1972.2456 | 926.3319 | 16.9732 | 10.8485 | 12.351 | 13.8957 | 11.2062 | 6.7237 | 3554.4674 | 7535.5819 | 11360.9991 | 2423.2037 | 5055.6344 | 9187.998 | 0.10336 | 0.10632 | 0.094957 | 16.6294 | 9.9978 | 11.5663 | 12.2061 | 28.1047 | 84.1684 | 124.9932 | 97.9963 | 65.831 | 99.45% | 99.44% | 99.27% | 99.5% | 99.44% | 99.08% | 116.1024 | 112.872 | 126.3733 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 105.1133 | 14 | 30 | 71 | 29 | 98.4% | 0.10296 | 0.10349 | 40.1727 | 38.1935 | 112.3913 | 25.5419 | 98.4% | 3829.4991 | 99.28% | 99.41% | 84.99% |  |  | 99.33% | 0.92971
2021-06-10 | 158.4689 | 141.6031 | 141.6031 | 130.6633 | 118.0269 | 14.4297 | 14.4297 | 3458.6653 | 1043.3379 | 313.0014 | 611.4792 | 29.0307 | 14.0148 | 30.0318 | 71.0752 | 9541.8121 | 328.7863 |  |  | 27.0787 | 0.93221 | 24.0103 | 4070.1445 | 2102.326 | 1967.8185 | 924.4806 | 16.8657 | 10.9398 | 12.3762 | 13.8615 | 11.1786 | 6.7072 | 3548.7429 | 7519.8427 | 11332.6863 | 2419.7474 | 5046.4334 | 9167.0802 | 0.10456 | 0.10785 | 0.097035 | 16.5818 | 10.1149 | 11.6231 | 12.8729 | 29.6518 | 88.8422 | 123.5777 | 96.6215 | 64.4354 | 99.42% | 99.4% | 99.22% | 99.47% | 99.41% | 99.03% | 114.7624 | 111.2642 | 123.6672 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 103.7162 | 14 | 30 | 71 | 29 | 98.32% | 0.10441 | 0.10487 | 40.1818 | 38.3197 | 110.9334 | 26.9464 | 98.32% | 3822.7295 | 99.24% | 99.38% | 84.98% |  |  | 99.29% | 0.93221
2021-06-09 | 160.0914 | 143.041 | 143.041 | 131.8858 | 119.4567 | 14.1412 | 14.1412 | 3472.1627 | 1047.4096 | 314.2229 | 611.5817 | 22.9861 | 11.0968 | 23.7788 | 56.2764 | 9382.8679 | 332.0952 |  |  | 27.0198 | 0.93405 | 19.0111 | 4083.7444 | 2110.5303 | 1973.2141 | 925.8046 | 17.0505 | 11.1552 | 12.4925 | 13.9156 | 11.2222 | 6.7333 | 3532.4732 | 7502.0368 | 11327.5735 | 2406.6947 | 5028.1932 | 9153.5547 | 0.10361 | 0.10663 | 0.095229 | 16.6846 | 10.2781 | 11.716 | 10.3082 | 23.7018 | 70.8628 | 125.447 | 98.3001 | 66.0437 | 99.54% | 99.53% | 99.39% | 99.57% | 99.53% | 99.23% | 115.8166 | 112.5346 | 126.012 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 105.3363 | 14 | 30 | 71 | 29 | 98.66% | 0.10324 | 0.10377 | 40.6981 | 38.6787 | 112.8289 | 21.5441 | 98.66% | 3808.0692 | 99.4% | 99.5% | 85.02% |  |  | 99.44% | 0.93405
2021-06-08 | 160.8679 | 143.7867 | 143.7867 | 132.6397 | 120.1144 | 14.0527 | 14.0527 | 3472.7656 | 1048.1863 | 316.5315 | 612.9187 | 24.7778 | 12.1637 | 25.9041 | 60.5931 | 9428.559 | 333.9647 |  |  | 26.8612 | 0.93904 | 20.7251 | 4085.6843 | 2108.0478 | 1977.6365 | 929.4502 | 17.0812 | 11.1471 | 12.6415 | 13.8992 | 11.2306 | 6.7828 | 3467.7404 | 7349.2667 | 11113.3786 | 2365.4254 | 4931.5595 | 8973.3518 | 0.10317 | 0.10585 | 0.093997 | 16.6884 | 10.2279 | 11.7983 | 11.5443 | 26.4864 | 78.8211 | 126.5083 | 99.6322 | 67.7606 | 99.49% | 99.47% | 99.32% | 99.51% | 99.46% | 99.12% | 116.3128 | 113.3696 | 127.6631 |  |  |  | 31.25 | 25.25 | 15.25 | 2437.5 | 1212 | 366 | 4015.5 | 106.0166 | 13.5 | 28.75 | 67.25 | 27.5 | 98.53% | 0.10256 | 0.10314 | 40.8698 | 38.7146 | 114.0367 | 23.7621 | 98.53% | 3742.2541 | 99.34% | 99.43% | 85% |  |  | 99.38% | 0.93904
2021-06-07 | 158.9903 | 141.9721 | 141.9721 | 130.7312 | 117.9838 | 13.9845 | 13.9845 | 3469.9665 | 1049.0596 | 322.7876 | 612.4201 | 23.8212 | 12.4285 | 25.8927 | 57.9995 | 8946.0383 | 329.1638 |  |  | 26.6855 | 0.9446 | 20.7382 | 4082.3866 | 2098.1193 | 1984.2673 | 935.2077 | 17.0182 | 11.2408 | 12.6051 | 13.8338 | 11.2399 | 6.9169 | 3288.6389 | 6948.5912 | 10580.4078 | 2248.7987 | 4670.646 | 8511.4812 | 0.10428 | 0.10709 | 0.095934 | 16.6131 | 10.2484 | 11.7044 | 12.422 | 28.1427 | 81.594 | 125.3148 | 99.1433 | 68.1055 | 99.45% | 99.45% | 99.32% | 99.45% | 99.4% | 99.04% | 115.0791 | 112.0558 | 125.0854 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 103.9805 | 12 | 25 | 56 | 23 | 98.52% | 0.10384 | 0.10435 | 40.8642 | 38.566 | 113.2992 | 24.1129 | 98.52% | 3563.5602 | 99.33% | 99.37% | 85% |  |  | 99.37% | 0.9446
2021-06-06 | 157.8359 | 141.0465 | 141.0465 | 130.0285 | 117.5487 | 14.0312 | 14.0312 | 3446.3487 | 1041.9194 | 320.5906 | 607.809 | 24.6824 | 12.8778 | 26.8287 | 60.0962 | 9109.3867 | 322.9463 |  |  | 26.997 | 0.93476 | 21.4879 | 4054.1577 | 2083.8388 | 1970.319 | 928.3996 | 16.7894 | 11.018 | 12.4042 | 13.7396 | 11.1634 | 6.8698 | 3342.2206 | 7063.0011 | 10756.7033 | 2285.3912 | 4747.0972 | 8652.4052 | 0.10354 | 0.10658 | 0.096138 | 16.5621 | 10.1533 | 11.6466 | 12.4478 | 28.1984 | 81.7406 | 124.0474 | 97.9049 | 66.7958 | 99.44% | 99.43% | 99.31% | 99.46% | 99.41% | 99.06% | 115.9026 | 112.5866 | 124.8202 |  |  |  | 32 | 26 | 16 | 2496 | 1248 | 384 | 4128 | 103.4768 | 12 | 25 | 56 | 23 | 98.49% | 0.10333 | 0.10377 | 40.2116 | 38.362 | 111.9072 | 24.1606 | 98.49% | 3621.9083 | 99.32% | 99.38% | 85.01% |  |  | 99.37% | 0.93476
2021-06-05 | 159.4609 | 142.5066 | 142.5066 | 131.4557 | 118.9421 | 14.21 | 14.21 | 3467.1804 | 1028.7782 | 316.5471 | 611.8642 | 25.1391 | 14.3652 | 29.9275 | 59.8551 | 9377.8597 | 329.5223 |  |  | 26.8964 | 0.93793 | 23.136 | 4079.0446 | 2121.8551 | 1957.1896 | 928.4114 | 16.9543 | 11.0509 | 12.4107 | 13.9903 | 11.0226 | 6.7832 | 3475.5347 | 7293.6328 | 11036.0181 | 2360.1092 | 4921.3601 | 8907.9675 | 0.10494 | 0.10516 | 0.095315 | 16.676 | 10.2531 | 11.6065 | 13.7376 | 30.0604 | 78.3437 | 125.045 | 98.314 | 66.7483 | 99.39% | 99.39% | 99.33% | 99.42% | 99.39% | 99.12% | 114.3546 | 114.1151 | 125.8989 |  |  |  | 33 | 26 | 16 | 2574 | 1248 | 384 | 4206 | 104.6951 | 12 | 25 | 50 | 21 | 98.5% | 0.10347 | 0.10412 | 40.4158 | 38.5356 | 112.7152 | 24.1989 | 98.5% | 3717.8883 | 99.32% | 99.36% | 85% |  |  | 99.37% | 0.93793
2021-06-04 | 159.769 | 142.8205 | 142.8205 | 131.619 | 119.149 | 14.4263 | 14.4263 | 3473.2864 | 1030.59 | 317.1046 | 613.0757 | 25.3076 | 14.4615 | 30.1281 | 60.2563 | 9431.7994 | 331.2436 |  |  | 26.9226 | 0.9371 | 23.2911 | 4086.3622 | 2125.5918 | 1960.7703 | 930.1804 | 16.9485 | 11.2015 | 12.5538 | 14.0149 | 11.042 | 6.7951 | 3500.499 | 7345.4839 | 11113.6631 | 2377.1057 | 4956.5503 | 8970.9903 | 0.10502 | 0.10541 | 0.095893 | 16.6253 | 10.364 | 11.7063 | 13.7429 | 30.0734 | 78.3836 | 125.0552 | 98.1613 | 66.404 | 99.39% | 99.39% | 99.33% | 99.42% | 99.39% | 99.13% | 114.2634 | 113.8378 | 125.1392 |  |  |  | 33 | 26 | 16 | 2574 | 1248 | 384 | 4206 | 104.7473 | 12 | 25 | 50 | 21 | 98.5% | 0.10369 | 0.1043 | 40.7038 | 38.6956 | 112.5746 | 24.2094 | 98.5% | 3744.4853 | 99.32% | 99.37% | 85% |  |  | 99.37% | 0.9371
2021-06-03 | 159.1181 | 142.2788 | 142.2788 | 131.2155 | 118.7749 | 14.348 | 14.348 | 3462.5171 | 1020.1242 | 301.5043 | 610.8832 | 25.7525 | 13.8706 | 27.8662 | 61.6483 | 9528.1714 | 330.7842 |  |  | 26.8949 | 0.93797 | 22.1543 | 4073.4003 | 2140.8885 | 1932.5117 | 912.3875 | 16.8393 | 11.0633 | 12.3905 | 14.1157 | 10.9299 | 6.4608 | 3579.576 | 7550.6796 | 11246.9267 | 2415.1463 | 5080.1214 | 9154.6288 | 0.10648 | 0.10554 | 0.092971 | 16.6885 | 10.4857 | 11.7822 | 13.0792 | 26.8884 | 74.7892 | 124.3441 | 97.1379 | 65.1823 | 99.43% | 99.45% | 99.33% | 99.46% | 99.47% | 99.18% | 112.697 | 113.7008 | 129.0726 |  |  |  | 33 | 25.5521 | 15.1042 | 2574 | 1226.5 | 362.5 | 4163 | 104.4544 | 11.5521 | 23.2083 | 51.3438 | 21.4479 | 98.49% | 0.10402 | 0.10503 | 40.293 | 38.9563 | 111.8558 | 24.3044 | 98.49% | 3787.1507 | 99.32% | 99.42% | 85% |  |  | 99.36% | 0.93797
2021-06-02 | 158.6331 | 141.7335 | 141.7335 | 130.6811 | 118.1896 | 14.3302 | 14.3302 | 3469.5139 | 1012.9968 | 283.6391 | 611.8568 | 25.5796 | 12.7898 | 24.4169 | 61.6236 | 9402.2107 | 332.2233 |  |  | 26.8228 | 0.94025 | 20.1768 | 4081.3707 | 2172.878 | 1908.4926 | 895.4959 | 16.8996 | 11.0524 | 12.3072 | 14.3267 | 10.8535 | 6.078 | 3588.4855 | 7620.2069 | 11124.1473 | 2401.2503 | 5107.6917 | 9152.2937 | 0.10871 | 0.10579 | 0.088394 | 16.8156 | 10.7055 | 11.8889 | 12.3411 | 23.3257 | 70.5181 | 123.9108 | 96.4607 | 64.6518 | 99.47% | 99.52% | 99.33% | 99.49% | 99.54% | 99.23% | 110.383 | 113.4273 | 135.7562 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 103.8331 | 11 | 21 | 53 | 22 | 98.48% | 0.10453 | 0.1062 | 40.2592 | 39.41 | 111.6714 | 24.5324 | 98.48% | 3743.3623 | 99.32% | 99.46% | 85.01% |  |  | 99.36% | 0.94025
2021-06-01 | 155.1546 | 138.2617 | 138.2617 | 126.9265 | 114.0799 | 14.1009 | 14.1009 | 3468.5237 | 1012.7076 | 283.5581 | 613.6092 | 23.6765 | 11.8383 | 22.6003 | 57.0389 | 8522.0168 | 324.543 |  |  | 26.7395 | 0.94288 | 18.6757 | 4082.1328 | 2172.2579 | 1909.8749 | 897.1673 | 16.893 | 11.3352 | 12.6535 | 14.3226 | 10.8504 | 6.0762 | 3296.6114 | 6992.2611 | 10197.1328 | 2206.641 | 4689.8593 | 8394.114 | 0.11103 | 0.10751 | 0.088527 | 16.8 | 10.9615 | 12.1819 | 12.4616 | 23.573 | 71.3461 | 121.6333 | 95.1569 | 64.717 | 99.46% | 99.52% | 99.32% | 99.44% | 99.5% | 99.15% | 108.0824 | 111.6136 | 135.5522 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 99.9694 | 11 | 21 | 53 | 22 | 98.47% | 0.1063 | 0.10816 | 40.8816 | 39.9433 | 110.1099 | 24.7898 | 98.47% | 3437.5054 | 99.31% | 99.41% | 84.97% |  |  | 99.35% | 0.94288
2021-05-31 | 155.7433 | 138.8233 | 138.8233 | 127.6305 | 114.8705 | 13.9863 | 13.9863 | 3460.9563 | 1010.4982 | 282.9395 | 612.2948 | 25.0605 | 12.5302 | 23.9214 | 60.373 | 8759.8933 | 325.8316 |  |  | 26.5482 | 0.94897 | 19.7673 | 4073.2511 | 2167.5186 | 1905.7324 | 895.2343 | 16.9199 | 11.1928 | 12.5271 | 14.2913 | 10.8268 | 6.063 | 3363.9133 | 7133.9387 | 10402.6112 | 2251.8912 | 4785.2899 | 8563.7576 | 0.11107 | 0.10766 | 0.088862 | 16.8818 | 10.859 | 12.0992 | 12.98 | 24.5575 | 74.3359 | 122.1002 | 95.4338 | 64.7473 | 99.44% | 99.5% | 99.3% | 99.42% | 99.49% | 99.13% | 108.0371 | 111.4635 | 135.0405 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 100.8784 | 11 | 21 | 53 | 22 | 98.41% | 0.10643 | 0.10826 | 40.6398 | 39.84 | 110.4474 | 25.8243 | 98.41% | 3507.5762 | 99.29% | 99.4% | 84.97% |  |  | 99.32% | 0.94897
2021-05-30 | 157.1233 | 140.2557 | 140.2557 | 129.2134 | 116.431 | 14.0493 | 14.0493 | 3469.8898 | 1013.1065 | 283.6698 | 611.2874 | 24.0522 | 12.0261 | 22.9589 | 57.9438 | 8989.4855 | 333.1791 |  |  | 26.5446 | 0.94909 | 18.972 | 4081.1772 | 2173.1135 | 1908.0637 | 894.9572 | 16.8676 | 11.0423 | 12.6033 | 14.3282 | 10.8547 | 6.0786 | 3445.3843 | 7319.6271 | 10689.4341 | 2305.157 | 4904.9755 | 8792.8532 | 0.1104 | 0.10701 | 0.088622 | 16.7864 | 10.7012 | 12.1884 | 12.2028 | 23.0564 | 69.674 | 123.1746 | 96.2752 | 65.0984 | 99.48% | 99.53% | 99.34% | 99.47% | 99.53% | 99.21% | 108.6938 | 112.1429 | 135.4065 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 102.3722 | 11 | 21 | 53 | 22 | 98.51% | 0.10583 | 0.10763 | 40.5132 | 39.676 | 111.2778 | 24.2505 | 98.51% | 3594.6091 | 99.33% | 99.45% | 85.02% |  |  | 99.37% | 0.94909
2021-05-29 | 157.3091 | 140.7 | 140.7 | 129.8346 | 117.3263 | 14.1497 | 14.1497 | 3440.6681 | 1004.5746 | 281.2809 | 608.816 | 25.5004 | 12.7502 | 24.3413 | 61.4327 | 9398.7606 | 328.8961 |  |  | 26.5439 | 0.94911 | 20.1143 | 4049.484 | 2154.8126 | 1894.6715 | 890.0969 | 16.609 | 10.8654 | 12.3862 | 14.2076 | 10.7633 | 6.0274 | 3593.3173 | 7621.309 | 11114.0701 | 2405.2312 | 5111.8802 | 9149.1108 | 0.10973 | 0.10677 | 0.089396 | 16.7175 | 10.6335 | 12.0664 | 12.2951 | 23.2583 | 70.3964 | 122.8924 | 95.6799 | 63.9924 | 99.47% | 99.52% | 99.33% | 99.49% | 99.55% | 99.23% | 109.3634 | 112.3936 | 134.2336 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 103.2144 | 11 | 21 | 53 | 22 | 98.49% | 0.10553 | 0.1072 | 39.8606 | 39.4173 | 110.6073 | 24.459 | 98.49% | 3746.8182 | 99.32% | 99.47% | 84.97% |  |  | 99.36% | 0.94911
2021-05-28 | 158.7621 | 141.9915 | 141.9915 | 131.1114 | 118.467 | 14.3757 | 14.3757 | 3472.1089 | 1013.7544 | 283.8512 | 613.6161 | 26.1084 | 13.0542 | 24.9216 | 62.8974 | 9593.2387 | 335.1253 |  |  | 26.7069 | 0.94392 | 20.5939 | 4085.725 | 2174.5032 | 1911.2217 | 897.4673 | 16.7707 | 10.8801 | 12.3862 | 14.3374 | 10.8617 | 6.0825 | 3658.0096 | 7761.846 | 11323.2849 | 2448.2753 | 5204.889 | 9319.4681 | 0.10929 | 0.10649 | 0.089527 | 16.6577 | 10.5121 | 11.9209 | 12.4117 | 23.472 | 71.0137 | 123.825 | 96.2759 | 64.1307 | 99.47% | 99.52% | 99.33% | 99.49% | 99.55% | 99.24% | 109.7957 | 112.6856 | 134.0382 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 104.1022 | 11 | 21 | 53 | 22 | 98.48% | 0.10523 | 0.10686 | 40.0369 | 39.0908 | 111.3795 | 24.6846 | 98.48% | 3814.8585 | 99.32% | 99.47% | 84.98% |  |  | 99.35% | 0.94392
2021-05-27 | 155.4108 | 139.0904 | 139.0904 | 128.5195 | 116.4821 | 14.1744 | 14.1744 | 3404.0525 | 993.8839 | 278.2875 | 600.6875 | 26.6603 | 13.3302 | 25.4485 | 64.2272 | 9569.2504 | 317.1678 |  |  | 26.6511 | 0.94569 | 21.0293 | 4004.74 | 2131.881 | 1872.859 | 878.975 | 16.3204 | 10.5709 | 12.0527 | 14.0564 | 10.6488 | 5.9633 | 3653.3297 | 7755.486 | 11318.7051 | 2444.9185 | 5199.2783 | 9313.6436 | 0.10993 | 0.1074 | 0.090842 | 16.7068 | 10.5315 | 11.9714 | 12.4661 | 23.568 | 71.2717 | 120.9183 | 93.7615 | 62.0794 | 99.45% | 99.51% | 99.31% | 99.49% | 99.55% | 99.23% | 109.1569 | 111.7268 | 132.0968 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 102.3434 | 11 | 21 | 53 | 22 | 98.45% | 0.10607 | 0.10763 | 38.944 | 39.2097 | 108.5256 | 24.7862 | 98.45% | 3810.642 | 99.3% | 99.47% | 85% |  |  | 99.35% | 0.94569
2021-05-26 | 157.1687 | 140.4132 | 140.4132 | 129.5712 | 117.1855 | 14.1135 | 14.1135 | 3465.5256 | 1011.8323 | 283.313 | 611.2996 | 25.7987 | 12.8993 | 24.626 | 62.1514 | 9583.1421 | 327.4892 |  |  | 26.7294 | 0.9432 | 20.3496 | 4076.8251 | 2170.3802 | 1906.4449 | 894.6126 | 16.7555 | 10.842 | 12.2724 | 14.3102 | 10.8411 | 6.071 | 3651.3209 | 7753.2158 | 11317.7182 | 2443.3037 | 5197.0047 | 9311.8141 | 0.11016 | 0.10762 | 0.090868 | 16.6998 | 10.5182 | 11.8723 | 12.2569 | 23.1672 | 70.0428 | 122.5255 | 95.0169 | 63.0166 | 99.47% | 99.53% | 99.33% | 99.5% | 99.55% | 99.25% | 108.9322 | 111.5076 | 132.0597 |  |  |  | 33 | 25 | 14 | 2574 | 1200 | 336 | 4110 | 103.0634 | 11 | 21 | 53 | 22 | 98.5% | 0.10626 | 0.10784 | 39.8699 | 39.0902 | 110.1274 | 24.3657 | 98.5% | 3808.8172 | 99.32% | 99.48% | 85.01% |  |  | 99.36% | 0.9432
2021-05-25 | 156.4766 | 139.7029 | 139.7029 | 128.8507 | 116.2574 | 13.7509 | 13.7509 | 3471.3625 | 998.4947 | 285.527 | 613.1855 | 25.863 | 12.9315 | 24.6874 | 62.3062 | 9472.0073 | 324.6916 |  |  | 26.7403 | 0.94286 | 20.3741 | 4084.548 | 2187.3408 | 1897.2072 | 898.7125 | 16.7737 | 10.8522 | 12.5646 | 14.422 | 10.6982 | 6.1184 | 3642.7631 | 7662.5466 | 11201.5637 | 2428.4333 | 5163.4726 | 9209.1599 | 0.11122 | 0.10637 | 0.091468 | 16.7242 | 10.5571 | 12.0828 | 12.4547 | 23.0592 | 71.5287 | 122.2614 | 94.832 | 63.0689 | 99.47% | 99.52% | 99.32% | 99.49% | 99.55% | 99.22% | 107.8941 | 112.8186 | 131.1927 |  |  |  | 33 | 24.4792 | 14 | 2574 | 1175 | 336 | 4085 | 102.4926 | 11 | 21 | 53 | 22 | 98.48% | 0.10651 | 0.1082 | 40.1905 | 39.3642 | 109.9335 | 24.6917 | 98.48% | 3772.863 | 99.31% | 99.47% | 84.99% |  |  | 99.35% | 0.94286
2021-05-24 | 154.9406 | 138.0683 | 138.0683 | 126.9713 | 114.1842 | 13.7142 | 13.7142 | 3470.572 | 984.2686 | 287.0783 | 613.8556 | 24.8259 | 12.4129 | 23.6974 | 59.8077 | 8903.6636 | 321.2664 |  |  | 26.4675 | 0.95155 | 19.5336 | 4084.4276 | 2199.2251 | 1885.2025 | 900.934 | 16.8723 | 11.0969 | 12.4242 | 14.5004 | 10.5457 | 6.1517 | 3476.2391 | 7248.1341 | 10609.8573 | 2309.2833 | 4908.4155 | 8716.5321 | 0.11374 | 0.10632 | 0.092067 | 16.8739 | 10.8521 | 11.9137 | 12.7569 | 23.1645 | 73.6073 | 121.3059 | 94.3821 | 63.58 | 99.46% | 99.52% | 99.31% | 99.45% | 99.53% | 99.16% | 105.4998 | 112.8657 | 130.3395 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 100.4841 | 11 | 21 | 53 | 22 | 98.46% | 0.1079 | 0.10985 | 40.3935 | 39.6396 | 109.5669 | 25.2283 | 98.46% | 3576.4019 | 99.31% | 99.43% | 84.97% |  |  | 99.34% | 0.95155
2021-05-23 | 155.8124 | 138.9418 | 138.9418 | 127.9249 | 115.2182 | 14.0141 | 14.0141 | 3471.1631 | 984.4362 | 287.1272 | 613.3672 | 24.9016 | 12.4508 | 23.7697 | 59.9901 | 9084.4055 | 325.0688 |  |  | 26.2408 | 0.95885 | 19.5932 | 4084.5303 | 2199.5997 | 1884.9306 | 900.4944 | 16.8706 | 11.0169 | 12.4048 | 14.5029 | 10.5475 | 6.1527 | 3535.0881 | 7373.7227 | 10797.4009 | 2348.0796 | 4992.368 | 8868.9895 | 0.11428 | 0.10693 | 0.092888 | 16.8729 | 10.7779 | 11.906 | 12.6831 | 23.0235 | 73.1315 | 121.6849 | 94.5763 | 63.5125 | 99.47% | 99.52% | 99.32% | 99.46% | 99.54% | 99.18% | 105.0061 | 112.2181 | 129.1882 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 101.18 | 11 | 21 | 53 | 22 | 98.48% | 0.10851 | 0.11043 | 40.2924 | 39.5569 | 109.7976 | 25.0759 | 98.48% | 3637.4066 | 99.32% | 99.44% | 84.98% |  |  | 99.34% | 0.95885
2021-05-22 | 157.0881 | 140.2745 | 140.2745 | 129.326 | 116.8051 | 14.1305 | 14.1305 | 3466.6505 | 983.1564 | 286.754 | 612.7421 | 26.1128 | 13.0564 | 24.9259 | 62.9082 | 9518.4779 | 326.4211 |  |  | 26.0846 | 0.96392 | 20.5463 | 4079.3926 | 2196.7402 | 1882.6525 | 899.496 | 16.8135 | 10.9485 | 12.4975 | 14.484 | 10.5338 | 6.1447 | 3686.2588 | 7688.1252 | 11256.6107 | 2448.5897 | 5205.5828 | 9246.6966 | 0.11409 | 0.10714 | 0.093992 | 16.8472 | 10.73 | 12.0143 | 12.8048 | 23.2467 | 73.8488 | 122.3731 | 94.7665 | 63.0161 | 99.47% | 99.52% | 99.32% | 99.48% | 99.55% | 99.2% | 105.1816 | 111.9983 | 127.6707 |  |  |  | 33 | 24 | 14 | 2574 | 1152 | 336 | 4062 | 102.6392 | 11 | 21 | 53 | 22 | 98.47% | 0.10865 | 0.11046 | 40.2596 | 39.5915 | 110.0276 | 25.3186 | 98.47% | 3792.8093 | 99.31% | 99.46% | 84.98% |  |  | 99.34% | 0.96392
2021-05-21 | 156.2389 | 139.4506 | 139.4506 | 128.6135 | 116.2054 | 14.3069 | 14.3069 | 3465.8786 | 983.7329 | 286.9221 | 611.8111 | 27.4461 | 13.7231 | 26.1986 | 66.1202 | 9593.9714 | 325.292 |  |  | 26.289 | 0.95729 | 21.6017 | 4077.6897 | 2195.2236 | 1882.4661 | 898.7332 | 16.7883 | 10.837 | 12.3228 | 14.474 | 10.54 | 6.1483 | 3728.0202 | 7779.9498 | 11397.5174 | 2476.9962 | 5265.9621 | 9359.6213 | 0.1143 | 0.10788 | 0.095494 | 16.8299 | 10.6262 | 11.8663 | 13.2037 | 24.0016 | 76.2008 | 121.2215 | 93.5263 | 61.6351 | 99.45% | 99.5% | 99.29% | 99.47% | 99.54% | 99.19% | 104.9851 | 111.2321 | 125.663 |  |  |  | 32.9579 | 24 | 14 | 2570.7158 | 1152 | 336 | 4058.7158 | 101.8902 | 11 | 21 | 53 | 22 | 98.41% | 0.10924 | 0.11092 | 39.9482 | 39.3223 | 108.8009 | 26.1089 | 98.41% | 3838.3753 | 99.28% | 99.45% | 85% |  |  | 99.32% | 0.95729
2021-05-20 | 153.6072 | 136.8778 | 136.8778 | 126.1583 | 113.7179 | 14.0821 | 14.0821 | 3472.299 | 1024.0882 | 298.6924 | 613.1133 | 28.1284 | 14.0642 | 26.8498 | 67.7638 | 9561.0257 | 318.9518 |  |  | 26.4591 | 0.95182 | 22.4544 | 4085.4122 | 2149.5184 | 1935.8938 | 911.8056 | 16.7293 | 10.7195 | 12.1682 | 14.1726 | 10.9724 | 6.4006 | 3635.4373 | 7688.3973 | 11400.9662 | 2451.194 | 5165.2588 | 9302.1529 | 0.11338 | 0.11384 | 0.10207 | 16.5159 | 10.1449 | 11.5521 | 13.3132 | 25.9573 | 81.3334 | 118.9748 | 91.744 | 59.6841 | 99.43% | 99.48% | 99.27% | 99.46% | 99.5% | 99.13% | 105.8351 | 105.4151 | 117.5621 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 99.5971 | 11 | 21 | 53 | 22 | 98.37% | 0.11172 | 0.11254 | 39.617 | 38.2129 | 106.4567 | 26.6362 | 98.37% | 3840.9853 | 99.27% | 99.42% | 84.99% |  |  | 99.3% | 0.95182
2021-05-19 | 154.0053 | 137.5662 | 137.5662 | 126.9167 | 114.7406 | 13.4144 | 13.4144 | 3451.1931 | 1017.8634 | 296.8768 | 609.1428 | 29.1158 | 14.5579 | 27.7924 | 70.1427 | 9744.0946 | 313.9181 |  |  | 26.3789 | 0.9544 | 23.2426 | 4060.3359 | 2136.4529 | 1923.883 | 906.0196 | 16.4391 | 10.6495 | 12.0302 | 14.0865 | 10.9057 | 6.3616 | 3677.8041 | 7778.3923 | 11535.1481 | 2479.8057 | 5225.5703 | 9411.3158 | 0.11199 | 0.11211 | 0.10001 | 16.3805 | 10.1739 | 11.5315 | 13.5754 | 26.4684 | 82.93 | 120.0451 | 92.8382 | 60.7083 | 99.41% | 99.47% | 99.25% | 99.45% | 99.49% | 99.12% | 107.1504 | 107.0352 | 119.9863 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 101.1882 | 11 | 21 | 53 | 22 | 98.34% | 0.11011 | 0.111 | 39.1188 | 38.0859 | 107.3735 | 27.1603 | 98.34% | 3885.8754 | 99.25% | 99.41% | 85% |  |  | 99.29% | 0.9544
2021-05-18 | 154.5395 | 137.9664 | 137.9664 | 127.2551 | 114.5911 | 13.941 | 13.941 | 3453.5317 | 1018.5531 | 297.078 | 610.3372 | 26.001 | 13.0005 | 24.8192 | 62.6388 | 9325.5093 | 318.2178 |  |  | 26.4279 | 0.95282 | 20.7562 | 4063.8689 | 2137.9006 | 1925.9683 | 907.4152 | 16.5731 | 10.7112 | 12.2142 | 14.096 | 10.9131 | 6.366 | 3562.1189 | 7532.6581 | 11168.6453 | 2401.6291 | 5060.8866 | 9113.1993 | 0.11158 | 0.11122 | 0.098262 | 16.4909 | 10.214 | 11.6779 | 12.5055 | 24.3822 | 76.4063 | 120.3688 | 93.4894 | 61.7293 | 99.46% | 99.51% | 99.31% | 99.48% | 99.52% | 99.16% | 107.5441 | 107.891 | 122.123 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 100.6345 | 11 | 21 | 53 | 22 | 98.47% | 0.10934 | 0.11033 | 39.4985 | 38.3828 | 108.035 | 25.0206 | 98.47% | 3763.2656 | 99.31% | 99.44% | 84.98% |  |  | 99.35% | 0.95282
2021-05-17 | 153.5986 | 136.7712 | 136.7712 | 125.6511 | 113.0117 | 14.0692 | 14.0692 | 3464.6582 | 1021.8347 | 298.0351 | 611.924 | 25.0036 | 12.5018 | 23.8671 | 60.236 | 8831.3216 | 318.2206 |  |  | 26.2195 | 0.95954 | 19.96 | 4076.5821 | 2144.7884 | 1931.7938 | 909.9591 | 16.8273 | 11.1202 | 12.6295 | 14.1415 | 10.9482 | 6.3865 | 3389.2453 | 7168.3824 | 10630.3766 | 2284.9992 | 4815.6567 | 8673.1916 | 0.11331 | 0.11274 | 0.098526 | 16.6664 | 10.5571 | 12.0259 | 12.7697 | 24.8946 | 77.9977 | 119.7532 | 93.183 | 62.1973 | 99.45% | 99.5% | 99.31% | 99.44% | 99.48% | 99.1% | 105.9039 | 106.4418 | 121.7953 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 98.976 | 11 | 21 | 53 | 22 | 98.45% | 0.11076 | 0.11187 | 40.577 | 39.2494 | 107.7947 | 25.5465 | 98.45% | 3580.8902 | 99.3% | 99.4% | 84.99% |  |  | 99.33% | 0.95954
2021-05-16 | 152.8296 | 136.1999 | 136.1999 | 125.3385 | 112.7678 | 13.9414 | 13.9414 | 3445.5473 | 1016.1983 | 296.3912 | 609.6809 | 25.589 | 12.7945 | 24.4259 | 61.6463 | 9026.3636 | 313.165 |  |  | 26.1715 | 0.96109 | 20.4273 | 4055.2282 | 2132.9579 | 1922.2704 | 906.0721 | 16.6297 | 10.8614 | 12.4088 | 14.0635 | 10.8878 | 6.3512 | 3457.8976 | 7308.6816 | 10831.7657 | 2331.7029 | 4911.7587 | 8840.4002 | 0.1136 | 0.11326 | 0.099711 | 16.5984 | 10.3849 | 11.8875 | 12.7569 | 24.8814 | 78.0082 | 118.9788 | 92.3911 | 61.218 | 99.45% | 99.5% | 99.3% | 99.45% | 99.49% | 99.12% | 105.6316 | 105.951 | 120.3474 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 98.8248 | 11 | 21 | 53 | 22 | 98.45% | 0.11127 | 0.11231 | 39.9 | 38.8709 | 106.8906 | 25.5317 | 98.45% | 3652.529 | 99.3% | 99.41% | 84.97% |  |  | 99.33% | 0.96109
2021-05-15 | 154.3358 | 137.6425 | 137.6425 | 126.814 | 114.3415 | 14.0858 | 14.0858 | 3467.8443 | 1022.7744 | 298.3092 | 611.4697 | 26.5885 | 13.2943 | 25.38 | 64.0542 | 9463.4618 | 319.5153 |  |  | 26.3299 | 0.95597 | 21.2252 | 4079.314 | 2146.7607 | 1932.5533 | 909.7789 | 16.6933 | 10.8285 | 12.302 | 14.1545 | 10.9583 | 6.3923 | 3607.5623 | 7634.6552 | 11328.0185 | 2431.8062 | 5127.1868 | 9239.7017 | 0.11294 | 0.11309 | 0.10082 | 16.5192 | 10.2771 | 11.7214 | 12.7237 | 24.7945 | 77.6385 | 119.8108 | 92.6334 | 60.6137 | 99.45% | 99.5% | 99.31% | 99.48% | 99.52% | 99.16% | 106.2522 | 106.111 | 119.0273 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 100.2548 | 11 | 21 | 53 | 22 | 98.45% | 0.11105 | 0.11194 | 39.8238 | 38.5177 | 107.3079 | 25.4449 | 98.45% | 3812.3826 | 99.3% | 99.44% | 85.01% |  |  | 99.33% | 0.95597
2021-05-14 | 154.0755 | 137.2912 | 137.2912 | 126.4051 | 114.2355 | 14.292 | 14.292 | 3471.0595 | 1023.7226 | 298.5858 | 613.0421 | 27.5553 | 13.7777 | 26.3028 | 66.3833 | 9625.6528 | 318.9977 |  |  | 26.4764 | 0.95127 | 21.9969 | 4084.1016 | 2148.7511 | 1935.3505 | 911.6279 | 16.7843 | 10.8861 | 12.2738 | 14.1676 | 10.9685 | 6.3983 | 3667.3696 | 7756.1458 | 11501.4896 | 2472.608 | 5210.6922 | 9384.1446 | 0.11316 | 0.11387 | 0.1024 | 16.5779 | 10.3064 | 11.6552 | 12.9169 | 25.1831 | 78.9061 | 119.0972 | 91.6342 | 59.4395 | 99.44% | 99.5% | 99.29% | 99.48% | 99.52% | 99.16% | 106.0436 | 105.3879 | 117.1903 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 99.9566 | 11 | 21 | 53 | 22 | 98.42% | 0.11166 | 0.11244 | 39.9443 | 38.5396 | 106.4335 | 25.8422 | 98.42% | 3874.6944 | 99.29% | 99.44% | 84.99% |  |  | 99.32% | 0.95127
2021-05-13 | 153.3028 | 136.5396 | 136.5396 | 125.7444 | 113.501 | 14.2771 | 14.2771 | 3471.5491 | 1023.867 | 298.6279 | 612.2417 | 27.7122 | 13.8561 | 26.4526 | 66.7613 | 9607.8397 | 317.7213 |  |  | 26.3893 | 0.95406 | 22.1222 | 4083.7907 | 2149.0542 | 1934.7365 | 910.8695 | 16.7632 | 10.7953 | 12.3361 | 14.1696 | 10.97 | 6.3992 | 3648.4897 | 7719.8569 | 11452.7418 | 2459.6111 | 5184.9386 | 9342.1692 | 0.11416 | 0.11492 | 0.10353 | 16.5608 | 10.2279 | 11.7324 | 13.0992 | 25.5307 | 79.9573 | 118.4153 | 91.0725 | 58.9685 | 99.44% | 99.49% | 99.29% | 99.47% | 99.51% | 99.14% | 105.1129 | 104.4205 | 115.905 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 99.2389 | 11 | 21 | 53 | 22 | 98.4% | 0.1127 | 0.11347 | 39.8946 | 38.5211 | 105.8028 | 26.1996 | 98.4% | 3855.4423 | 99.28% | 99.43% | 85.01% |  |  | 99.31% | 0.95406
2021-05-12 | 152.2929 | 135.6006 | 135.6006 | 124.8224 | 112.4503 | 14.062 | 14.062 | 3470.7226 | 1023.6233 | 298.5568 | 613.4485 | 28.3753 | 14.1876 | 27.0855 | 68.3586 | 9615.1213 | 314.7347 |  |  | 26.4917 | 0.95078 | 22.6515 | 4084.1711 | 2148.5426 | 1935.6285 | 912.0053 | 16.6923 | 10.7782 | 12.1802 | 14.1662 | 10.9674 | 6.3976 | 3655.8687 | 7728.7694 | 11456.9841 | 2465.2173 | 5193.4526 | 9349.5314 | 0.1145 | 0.11545 | 0.10457 | 16.4856 | 10.2008 | 11.5574 | 13.3329 | 26.0026 | 81.5048 | 117.6296 | 90.3176 | 58.1684 | 99.42% | 99.48% | 99.27% | 99.46% | 99.5% | 99.13% | 104.8011 | 103.9375 | 114.7547 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 98.4306 | 11 | 21 | 53 | 22 | 98.37% | 0.11322 | 0.11393 | 39.6507 | 38.2438 | 105.0267 | 26.6819 | 98.37% | 3862.0572 | 99.27% | 99.42% | 84.98% |  |  | 99.3% | 0.95078
2021-05-11 | 150.794 | 133.9457 | 133.9457 | 123.0832 | 110.742 | 13.9138 | 13.9138 | 3471.7898 | 1033.5994 | 307.4225 | 613.331 | 28.2602 | 14.1301 | 26.9756 | 68.0814 | 9323.1477 | 311.4204 |  |  | 26.3375 | 0.95573 | 22.7317 | 4085.1209 | 2130.7679 | 1954.353 | 920.7536 | 16.8484 | 10.8625 | 12.328 | 14.049 | 11.0743 | 6.5876 | 3523.1811 | 7447.875 | 11146.8802 | 2388.3827 | 5004.8464 | 9050.1249 | 0.11517 | 0.11798 | 0.10839 | 16.5585 | 10.1336 | 11.5991 | 13.6634 | 27.2764 | 86.7999 | 116.5848 | 89.7113 | 58.0886 | 99.41% | 99.46% | 99.25% | 99.43% | 99.46% | 99.04% | 104.1939 | 101.7133 | 110.7155 |  |  |  | 30.4468 | 24 | 14.2766 | 2374.8511 | 1152 | 342.6383 | 3869.4894 | 96.8467 | 11 | 21 | 53 | 22 | 98.33% | 0.11498 | 0.11541 | 40.0389 | 38.2912 | 104.2077 | 27.4659 | 98.33% | 3757.2285 | 99.25% | 99.37% | 84.99% |  |  | 99.28% | 0.95573
2021-05-10 | 148.2035 | 131.381 | 131.381 | 120.5232 | 107.9731 | 13.8458 | 13.8458 | 3471.666 | 1059.7136 | 331.1605 | 613.5013 | 27.7766 | 13.8883 | 26.514 | 66.9163 | 8839.8197 | 306.406 |  |  | 26.039 | 0.9654 | 22.8005 | 4085.1673 | 2080.7919 | 2004.3755 | 944.6618 | 16.8226 | 10.8578 | 12.5134 | 13.7195 | 11.3541 | 7.0963 | 3273.537 | 6916.0199 | 10613.0824 | 2250.7763 | 4649.0027 | 8502.2778 | 0.11541 | 0.12317 | 0.11766 | 16.3296 | 9.7507 | 11.5017 | 14.0573 | 29.8903 | 98.814 | 114.762 | 88.9938 | 58.2255 | 99.38% | 99.43% | 99.21% | 99.38% | 99.36% | 98.84% | 103.9758 | 97.4273 | 101.9892 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 94.1065 | 11 | 21 | 53 | 22 | 98.28% | 0.11825 | 0.11799 | 40.1938 | 37.582 | 102.7149 | 28.6248 | 98.28% | 3579.154 | 99.22% | 99.28% | 84.98% |  |  | 99.25% | 0.9654
2021-05-09 | 147.6219 | 130.9613 | 130.9613 | 120.3878 | 107.9134 | 13.8843 | 13.8843 | 3471.9146 | 1059.7895 | 331.1842 | 612.3469 | 29.2207 | 14.6104 | 27.8925 | 70.3953 | 9190.8538 | 306.3526 |  |  | 26.121 | 0.96273 | 23.986 | 4084.2616 | 2080.9409 | 2003.3207 | 943.5312 | 16.6606 | 10.5735 | 12.2572 | 13.7205 | 11.3549 | 7.0968 | 3370.8281 | 7125.6676 | 10941.4699 | 2317.4024 | 4788.3809 | 8762.4911 | 0.11598 | 0.12424 | 0.12028 | 16.1803 | 9.5059 | 11.291 | 14.3243 | 30.4469 | 100.5928 | 113.8933 | 87.9878 | 56.8058 | 99.37% | 99.42% | 99.2% | 99.38% | 99.36% | 98.85% | 103.4674 | 96.5861 | 99.7712 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 94.0251 | 11 | 21 | 53 | 22 | 98.24% | 0.11931 | 0.11891 | 39.4913 | 36.9771 | 101.6202 | 29.1578 | 98.24% | 3686.4536 | 99.21% | 99.29% | 85.01% |  |  | 99.24% | 0.96273
2021-05-08 | 146.7579 | 130.096 | 130.096 | 119.5406 | 107.4938 | 13.9227 | 13.9227 | 3470.9773 | 1059.5034 | 331.0948 | 611.8755 | 31.8947 | 15.9473 | 30.4449 | 76.8372 | 9617.7384 | 303.9687 |  |  | 26.2243 | 0.95938 | 26.1809 | 4082.8528 | 2080.3791 | 2002.4737 | 942.9703 | 16.6619 | 10.5554 | 12.1844 | 13.7168 | 11.3518 | 7.0949 | 3510.4956 | 7420.6138 | 11394.4389 | 2413.6085 | 4986.6951 | 9125.2182 | 0.11696 | 0.12647 | 0.12523 | 16.1905 | 9.4965 | 11.2351 | 14.9556 | 31.7918 | 105.0382 | 112.516 | 86.1144 | 54.3526 | 99.34% | 99.39% | 99.16% | 99.38% | 99.36% | 98.85% | 102.6009 | 94.8855 | 95.8218 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 93.5678 | 11 | 21 | 53 | 22 | 98.16% | 0.12133 | 0.12065 | 39.4017 | 36.9221 | 99.8119 | 30.4448 | 98.16% | 3839.2511 | 99.17% | 99.29% | 85.01% |  |  | 99.2% | 0.95938
2021-05-07 | 150.871 | 132.9907 | 132.9907 | 122.2396 | 109.7581 | 13.7008 | 13.7008 | 3470.9272 | 1059.4881 | 331.09 | 611.6072 | 35.1143 | 17.5572 | 33.5182 | 84.5935 | 10053.7509 | 337.2607 |  |  | 26.2435 | 0.95876 | 28.8238 | 4082.5344 | 2080.349 | 2002.1854 | 942.6973 | 17.8803 | 10.7511 | 12.2988 | 13.7166 | 11.3517 | 7.0948 | 3549.8453 | 7501.8103 | 11517.0776 | 2441.142 | 5042.008 | 9224.308 | 0.11326 | 0.12246 | 0.12018 | 17.377 | 9.6753 | 11.3465 | 16.2688 | 34.5941 | 114.3233 | 116.112 | 88.8718 | 56.5994 | 99.28% | 99.34% | 99.08% | 99.33% | 99.31% | 98.76% | 105.9503 | 97.9886 | 99.849 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 96.144 | 11 | 21 | 53 | 22 | 97.99% | 0.11731 | 0.11673 | 40.9302 | 38.3988 | 103.4937 | 33.1262 | 97.99% | 3882.0899 | 99.1% | 99.24% | 85.02% |  |  | 99.13% | 0.95876
2021-05-06 | 152.9783 | 134.1148 | 134.1148 | 123.242 | 110.7609 | 13.6923 | 13.6923 | 3472.2287 | 1059.8854 | 331.2142 | 613.2311 | 43.0101 | 21.5051 | 41.0551 | 103.6153 | 10238.1321 | 362.7404 |  |  | 26.3052 | 0.95677 | 35.3051 | 4085.4598 | 2081.1291 | 2004.3306 | 944.4453 | 18.8635 | 10.8728 | 12.1996 | 13.7217 | 11.3559 | 7.0974 | 3534.0613 | 7454.0199 | 11424.0703 | 2432.3611 | 5015.3349 | 9158.2359 | 0.11145 | 0.12057 | 0.11701 | 18.3097 | 9.7655 | 11.2185 | 19.9649 | 42.5257 | 140.8 | 117.8 | 90.1148 | 58.0361 | 99.12% | 99.18% | 98.87% | 99.18% | 99.15% | 98.46% | 107.674 | 99.5286 | 102.5581 |  |  |  | 29 | 24 | 15 | 2262 | 1152 | 360 | 3774 | 97.0819 | 11 | 21 | 53 | 22 | 97.53% | 0.11526 | 0.11476 | 41.9359 | 39.2936 | 105.4426 | 40.7125 | 97.53% | 3862.3825 | 98.89% | 99.06% | 84.99% |  |  | 98.93% | 0.95677
2021-05-05
2021-05-04
2021-05-03 | 183.902 | 166.2098 | 166.2098 | 154.7149 | 142.1944 | 13.9338 | 13.9338 | 3472.2789 | 1054.9172 | 329.6616 | 613.0825 | 19.0441 | 9.522 | 18.1784 | 45.78 | 8660.2458 | 389.9711 |  |  | 25.9459 | 0.96844 | 15.5943 | 4085.3614 | 2087.7 | 1997.6614 | 942.7442 | 17.6922 | 11.4949 | 12.5119 | 13.7651 | 11.3027 | 7.0642 | 3295.045 | 6961.8119 | 10680.643 | 2259.5199 | 4679.6515 | 8557.5642 | 0.088947 | 0.088832 | 0.074392 | 17.2014 | 10.3683 | 11.5262 | 9.6628 | 20.3308 | 67.0723 | 149.8721 | 123.2212 | 91.9619 | 99.58% | 99.61% | 99.47% | 99.57% | 99.57% | 99.22% | 134.9117 | 135.086 | 161.3069 |  |  |  | 29.2286 | 24 | 15 | 2279.8286 | 1152 | 360 | 3791.8286 | 128.2371 | 11 | 21 | 52.8857 | 22 | 98.82% | 0.086582 | 0.08753 | 41.699 | 39.0959 | 137.9053 | 19.6165 | 98.82% | 3592.7257 | 99.47% | 99.51% | 84.99% |  |  | 99.49% | 0.96844
2021-05-02 | 185.5129 | 167.8818 | 167.8818 | 156.5532 | 143.9213 | 14.0016 | 14.0016 | 3471.5373 | 1017.6109 | 318.0034 | 613.1908 | 20.2167 | 10.1083 | 19.2977 | 47.7849 | 9071.6052 | 392.3739 |  |  | 25.8523 | 0.97151 | 16.2533 | 4084.7281 | 2135.9229 | 1948.8052 | 931.1942 | 17.6311 | 11.3286 | 12.452 | 14.083 | 10.903 | 6.8144 | 3449.7727 | 7198.6025 | 10907.0475 | 2333.506 | 4872.7263 | 8797.4705 | 0.090561 | 0.085458 | 0.07158 | 17.3533 | 10.5414 | 11.5987 | 10.1942 | 20.0578 | 65.9003 | 151.0787 | 123.9487 | 92.4872 | 99.57% | 99.6% | 99.46% | 99.56% | 99.59% | 99.25% | 132.5076 | 140.4203 | 167.6446 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 129.9173 | 11 | 21 | 52 | 22 | 98.78% | 0.085891 | 0.087326 | 41.4117 | 39.4935 | 139.053 | 20.4464 | 98.78% | 3669.946 | 99.45% | 99.52% | 84.99% |  |  | 99.46% | 0.97151
2021-05-01 | 185.597 | 167.9942 | 167.9942 | 156.7327 | 144.3782 | 14.0647 | 14.0647 | 3472.5098 | 1017.896 | 318.0925 | 611.9663 | 21.0986 | 10.5493 | 20.1396 | 49.8694 | 9504.8936 | 392.677 |  |  | 25.9303 | 0.96895 | 16.9623 | 4084.4761 | 2136.5213 | 1947.9548 | 930.0588 | 17.6028 | 11.2616 | 12.2383 | 14.087 | 10.906 | 6.8163 | 3591.6277 | 7500.4163 | 11373.1179 | 2428.9631 | 5074.8192 | 9169.6127 | 0.090611 | 0.085896 | 0.072665 | 17.3302 | 10.4899 | 11.4258 | 10.1967 | 20.0518 | 65.8286 | 150.6389 | 123.0254 | 90.892 | 99.57% | 99.6% | 99.46% | 99.58% | 99.6% | 99.28% | 132.4335 | 139.7031 | 165.1419 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 130.2601 | 11 | 21 | 52 | 22 | 98.77% | 0.086231 | 0.087585 | 41.1026 | 39.246 | 138.2352 | 20.4412 | 98.77% | 3822.0064 | 99.45% | 99.54% | 85.02% |  |  | 99.47% | 0.96895
2021-04-30 | 184.2831 | 166.7132 | 166.7132 | 155.4729 | 142.9537 | 14.2449 | 14.2449 | 3466.788 | 1016.2188 | 317.5684 | 612.6371 | 21.8196 | 10.9098 | 20.8278 | 51.5736 | 9541.0141 | 388.8851 |  |  | 26.2654 | 0.95805 | 17.542 | 4079.4251 | 2133.0009 | 1946.4242 | 930.2054 | 17.5699 | 11.2402 | 12.3664 | 14.0637 | 10.8881 | 6.805 | 3617.1349 | 7545.9818 | 11430.8055 | 2446.9471 | 5108.5704 | 9221.0376 | 0.090384 | 0.085919 | 0.073154 | 17.3262 | 10.4776 | 11.5363 | 10.3329 | 20.3348 | 66.8266 | 149.073 | 121.4094 | 89.121 | 99.55% | 99.59% | 99.44% | 99.58% | 99.6% | 99.28% | 132.7668 | 139.6668 | 164.0368 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 128.7414 | 11 | 21 | 52 | 22 | 98.74% | 0.086198 | 0.087497 | 41.1766 | 39.3401 | 136.5656 | 20.7282 | 98.74% | 3847.6755 | 99.43% | 99.54% | 84.98% |  |  | 99.46% | 0.95805
2021-04-29 | 191.9663 | 174.2095 | 174.2095 | 162.8761 | 150.3651 | 14.2872 | 14.2872 | 3471.6971 | 1017.6578 | 318.0181 | 612.6488 | 21.6373 | 10.8187 | 20.6538 | 51.1427 | 9760.9935 | 404.7338 |  |  | 25.9946 | 0.96685 | 17.3954 | 4084.3459 | 2136.0213 | 1948.3246 | 930.6668 | 17.7567 | 11.3335 | 12.5038 | 14.0837 | 10.9035 | 6.8147 | 3623.2738 | 7562.6365 | 11461.7559 | 2450.7408 | 5118.3846 | 9243.5374 | 0.086952 | 0.081869 | 0.068368 | 17.4807 | 10.5515 | 11.6591 | 10.3392 | 20.3398 | 66.8085 | 156.6011 | 128.767 | 96.3714 | 99.56% | 99.6% | 99.45% | 99.58% | 99.6% | 99.28% | 138.0071 | 146.5756 | 175.5195 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 136.0835 | 11 | 21 | 52 | 22 | 98.75% | 0.082352 | 0.08376 | 41.594 | 39.6913 | 144.0593 | 20.734 | 98.75% | 3854.9476 | 99.44% | 99.54% | 85% |  |  | 99.46% | 0.96685
2021-04-28 | 190.4059 | 172.6694 | 172.6694 | 161.2521 | 148.7827 | 13.9399 | 13.9399 | 3469.1793 | 1016.9197 | 317.7874 | 612.5883 | 20.2301 | 10.1151 | 19.3106 | 47.8166 | 9476.7423 | 400.2631 |  |  | 25.6847 | 0.97704 | 16.2641 | 4081.7676 | 2134.4721 | 1947.2954 | 930.3757 | 17.7365 | 11.4172 | 12.5686 | 14.0734 | 10.8956 | 6.8097 | 3607.4747 | 7529.4117 | 11410.5775 | 2439.9227 | 5095.9924 | 9202.6187 | 0.088455 | 0.083403 | 0.069812 | 17.4766 | 10.6368 | 11.7235 | 9.8049 | 19.2878 | 63.3564 | 155.4487 | 127.6375 | 95.3035 | 99.59% | 99.62% | 99.48% | 99.6% | 99.62% | 99.31% | 135.6616 | 143.8793 | 171.8893 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 134.8137 | 11 | 21 | 52 | 22 | 98.83% | 0.083856 | 0.085267 | 41.7224 | 39.8369 | 142.9219 | 19.6622 | 98.83% | 3837.9794 | 99.47% | 99.56% | 84.99% |  |  | 99.49% | 0.97704
2021-04-27 | 191.5653 | 173.8248 | 173.8248 | 162.2635 | 149.7579 | 13.8796 | 13.8796 | 3471.8129 | 1019.8754 | 317.7457 | 613.3871 | 20.2108 | 10.2394 | 19.694 | 48.2398 | 9446.2213 | 402.7362 |  |  | 25.284 | 0.9904 | 16.4946 | 4085.2001 | 2134.1919 | 1951.0082 | 931.1328 | 17.7405 | 11.5613 | 12.501 | 14.0716 | 10.9272 | 6.8088 | 3601.9948 | 7525.7104 | 11399.1761 | 2437.7201 | 5090.5502 | 9195.9202 | 0.08895 | 0.084017 | 0.069958 | 17.4495 | 10.746 | 11.6429 | 10.0688 | 20.0191 | 64.8297 | 156.6781 | 128.8103 | 96.3928 | 99.58% | 99.61% | 99.48% | 99.59% | 99.61% | 99.3% | 134.9078 | 142.8277 | 171.5314 |  |  |  | 31 | 24.0729 | 15 | 2418 | 1155.5 | 360 | 3933.5 | 135.8297 | 11.1458 | 21.4375 | 52.5104 | 22 | 98.83% | 0.084333 | 0.085763 | 41.8029 | 39.8383 | 144.135 | 19.9398 | 98.83% | 3835.533 | 99.47% | 99.55% | 84.99% |  |  | 99.48% | 0.9904
2021-04-26 | 189.5238 | 171.6822 | 171.6822 | 160.0952 | 147.4588 | 13.8423 | 13.8423 | 3471.068 | 1047.0793 | 314.1238 | 613.2665 | 19.6407 | 11.6058 | 24.1045 | 52.6727 | 8988.8681 | 397.5539 |  |  | 25.2083 | 0.99295 | 19.0926 | 4084.3345 | 2109.8649 | 1974.4696 | 927.3903 | 17.8416 | 11.587 | 12.7182 | 13.9112 | 11.2187 | 6.7312 | 3398.1298 | 7207.6072 | 10872.4663 | 2316.1771 | 4834.2887 | 8790.341 | 0.08898 | 0.087031 | 0.069444 | 17.4508 | 10.6603 | 11.8897 | 11.9051 | 26.5575 | 73.3974 | 155.2378 | 127.9955 | 96.2463 | 99.5% | 99.5% | 99.4% | 99.49% | 99.45% | 99.17% | 134.8618 | 137.882 | 172.8009 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 133.613 | 13 | 27 | 59 | 22 | 98.81% | 0.085231 | 0.086624 | 42.1468 | 40.0008 | 143.0736 | 20.3452 | 98.81% | 3661.6856 | 99.46% | 99.42% | 84.98% |  |  | 99.47% | 0.99295
2021-04-25 | 188.4553 | 170.8668 | 170.8668 | 159.4703 | 146.8522 | 13.9356 | 13.9356 | 3463.7537 | 1044.8729 | 313.4619 | 611.126 | 19.7778 | 11.6869 | 24.2727 | 53.0404 | 9141.5456 | 393.6006 |  |  | 25.5401 | 0.98183 | 19.2259 | 4074.8797 | 2105.4189 | 1969.4607 | 924.5878 | 17.5884 | 11.3966 | 12.4636 | 13.8819 | 11.1951 | 6.717 | 3447.722 | 7316.548 | 11042.1837 | 2349.6528 | 4905.9422 | 8925.2315 | 0.088484 | 0.086668 | 0.06952 | 17.2649 | 10.5276 | 11.708 | 11.6605 | 26.0025 | 71.8264 | 154.0356 | 126.8246 | 94.8647 | 99.5% | 99.51% | 99.41% | 99.5% | 99.47% | 99.2% | 135.6177 | 138.4588 | 172.6117 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 132.9005 | 13 | 27 | 59 | 22 | 98.82% | 0.084869 | 0.08622 | 41.4486 | 39.5005 | 141.7605 | 19.9205 | 98.82% | 3715.8558 | 99.47% | 99.44% | 85% |  |  | 99.48% | 0.98183
2021-04-24 | 190.0915 | 172.3597 | 172.3597 | 161.0609 | 148.2558 | 14.0709 | 14.0709 | 3469.633 | 1046.6465 | 313.9939 | 613.7257 | 20.3309 | 12.0137 | 24.9515 | 54.5237 | 9471.2089 | 398.0308 |  |  | 25.3874 | 0.98693 | 19.7636 | 4083.3587 | 2108.9926 | 1974.3661 | 927.7197 | 17.7319 | 11.2987 | 12.4981 | 13.9054 | 11.2141 | 6.7284 | 3560.3794 | 7549.0231 | 11383.3539 | 2426.9591 | 5064.31 | 9205.1741 | 0.088494 | 0.086843 | 0.070022 | 17.3481 | 10.3939 | 11.675 | 11.6849 | 26.0724 | 72.0834 | 155.0799 | 127.4426 | 94.8342 | 99.5% | 99.51% | 99.41% | 99.52% | 99.49% | 99.22% | 135.6018 | 138.1803 | 171.3742 |  |  |  | 31 | 25 | 15 | 2418 | 1200 | 360 | 3978 | 134.2669 | 13 | 27 | 59 | 22 | 98.82% | 0.08501 | 0.086325 | 41.5287 | 39.417 | 142.5182 | 19.9733 | 98.82% | 3835.9532 | 99.47% | 99.46% | 84.97% |  |  | 99.48% | 0.98693
2021-04-23 | 190.9014 | 173.1974 | 173.1974 | 161.8106 | 149.1773 | 13.9798 | 13.9798 | 3466.6997 | 1045.1285 | 313.6223 | 613.1219 | 20.9321 | 12.3309 | 25.6133 | 55.2441 | 9662.0591 | 398.8036 |  |  | 25.3559 | 0.98798 | 20.2175 | 4079.8216 | 2107.9489 | 1971.8727 | 926.7442 | 17.704 | 11.3868 | 12.5503 | 13.8986 | 11.1978 | 6.7205 | 3627.4565 | 7689.4069 | 11594.4118 | 2472.1739 | 5159.1806 | 9376.1187 | 0.088152 | 0.086529 | 0.069958 | 17.3467 | 10.4937 | 11.7418 | 11.7808 | 26.2616 | 71.6959 | 155.7704 | 127.8564 | 94.9098 | 99.5% | 99.5% | 99.41% | 99.52% | 99.49% | 99.24% | 136.1279 | 138.6825 | 171.531 |  |  |  | 30.98 | 24.96 | 14.98 | 2416.4393 | 1198.0792 | 359.5198 | 3974.0383 | 135.2233 | 12.96 | 26.92 | 58.0625 | 22 | 98.81% | 0.084722 | 0.086017 | 41.6411 | 39.5822 | 142.9632 | 20.1954 | 98.81% | 3906.8233 | 99.46% | 99.47% | 84.97% |  |  | 99.47% | 0.98798
2021-04-22 | 190.8505 | 173.2025 | 173.2025 | 161.928 | 149.2632 | 14.0796 | 14.0796 | 3468.6713 | 1013.0723 | 308.3263 | 612.3997 | 21.5286 | 10.7643 | 22.5072 | 13.7 | 9763.9596 | 399.0805 |  |  | 25.4792 | 0.98386 | 14.4549 | 4081.071 | 2147.2727 | 1933.7983 | 920.726 | 17.648 | 11.2744 | 12.4921 | 14.1578 | 10.8543 | 6.607 | 3730.4346 | 7810.2567 | 11735.6078 | 2513.683 | 5276.8758 | 9508.0021 | 0.089617 | 0.083947 | 0.06912 | 17.4509 | 10.6318 | 11.7645 | 10.2599 | 21.7789 | 17.1653 | 155.4323 | 127.2138 | 94.0445 | 99.57% | 99.57% | 99.86% | 99.59% | 99.59% | 99.82% | 133.9036 | 142.9482 | 173.6111 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 135.2019 | 11 | 23 | 14 | 22 | 98.79% | 0.084523 | 0.086139 | 41.4146 | 39.8473 | 142.6733 | 20.5091 | 98.79% | 3942.428 | 99.45% | 99.63% | 84.99% |  |  | 99.46% | 0.98386
2021-04-21 | 190.9247 | 173.2075 | 173.2075 | 161.8061 | 149.2341 | 14.0347 | 14.0347 | 3472.2691 | 1014.123 | 308.6461 | 612.1574 | 21.6882 | 10.8441 | 22.674 | 13.8016 | 9775.3666 | 398.8595 |  |  | 25.4494 | 0.98485 | 14.5621 | 4084.4264 | 2149.4999 | 1934.9265 | 920.8035 | 17.7172 | 11.4014 | 12.4881 | 14.1725 | 10.8656 | 6.6138 | 3733.6096 | 7820.6328 | 11756.7911 | 2515.5171 | 5282.4727 | 9522.7454 | 0.089757 | 0.084145 | 0.069338 | 17.4997 | 10.7447 | 11.7626 | 10.3496 | 21.962 | 17.3011 | 155.508 | 127.1731 | 93.9406 | 99.57% | 99.57% | 99.86% | 99.59% | 99.58% | 99.82% | 133.6948 | 142.6102 | 173.0647 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 135.2573 | 11 | 23 | 14 | 22 | 98.78% | 0.084694 | 0.086303 | 41.6067 | 40.0071 | 142.7191 | 20.682 | 98.78% | 3946.5085 | 99.45% | 99.62% | 85.01% |  |  | 99.46% | 0.98485
2021-04-20 | 188.8749 | 171.2613 | 171.2613 | 159.8338 | 147.3137 | 13.9214 | 13.9214 | 3472.0479 | 1014.0584 | 308.6265 | 611.8857 | 20.2125 | 10.1062 | 21.1312 | 12.8625 | 9519.9475 | 394.6225 |  |  | 25.6168 | 0.97929 | 13.5712 | 4083.9337 | 2149.363 | 1934.5707 | 920.5122 | 17.6136 | 11.4275 | 12.5641 | 14.1716 | 10.8649 | 6.6134 | 3646.1069 | 7639.4675 | 11486.2188 | 2456.2728 | 5159.2994 | 9302.8204 | 0.090167 | 0.084487 | 0.069488 | 17.4011 | 10.773 | 11.8408 | 9.8215 | 20.8365 | 16.4107 | 153.9159 | 125.9353 | 93.2026 | 99.59% | 99.59% | 99.86% | 99.6% | 99.6% | 99.82% | 133.0869 | 142.0342 | 172.6924 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 133.3215 | 11 | 23 | 14 | 22 | 98.83% | 0.08504 | 0.08667 | 41.6053 | 40.0149 | 141.3424 | 19.623 | 98.83% | 3854.3102 | 99.48% | 99.63% | 85.02% |  |  | 99.49% | 0.97929
2021-04-19 | 187.3874 | 169.6708 | 169.6708 | 158.1177 | 145.4646 | 13.8793 | 13.8793 | 3471.5334 | 1013.9082 | 308.5807 | 613.5514 | 18.4532 | 9.2266 | 19.292 | 11.743 | 9064.2811 | 391.2338 |  |  | 25.632 | 0.97878 | 12.39 | 4085.0848 | 2149.0445 | 1936.0403 | 922.1322 | 17.7167 | 11.553 | 12.6522 | 14.1695 | 10.8633 | 6.6124 | 3494.805 | 7316.2213 | 10989.95 | 2354.7802 | 4943.3568 | 8905.3202 | 0.090692 | 0.084795 | 0.069262 | 17.4915 | 10.8737 | 11.8855 | 9.347 | 19.8408 | 15.6408 | 152.9221 | 125.3947 | 93.444 | 99.61% | 99.61% | 99.87% | 99.6% | 99.6% | 99.82% | 132.3153 | 141.5183 | 173.2545 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 131.6036 | 11 | 23 | 14 | 22 | 98.89% | 0.085376 | 0.087065 | 41.9219 | 40.2507 | 140.7926 | 18.6848 | 98.89% | 3693.0791 | 99.5% | 99.64% | 84.98% |  |  | 99.51% | 0.97878
2021-04-18 | 188.363 | 170.5966 | 170.5966 | 159.0888 | 146.4786 | 13.9325 | 13.9325 | 3471.6001 | 1013.9277 | 308.5867 | 612.2639 | 18.1932 | 9.0966 | 19.0201 | 11.5775 | 9164.8192 | 392.5558 |  |  | 25.5961 | 0.97997 | 12.2154 | 4083.8641 | 2149.0858 | 1934.7783 | 920.8506 | 17.7664 | 11.5078 | 12.5524 | 14.1698 | 10.8635 | 6.6126 | 3523.0727 | 7381.3053 | 11095.7161 | 2373.273 | 4985.0926 | 8987.5623 | 0.090329 | 0.084438 | 0.068959 | 17.5514 | 10.8456 | 11.8214 | 9.1547 | 19.4214 | 15.2981 | 153.7264 | 126.0798 | 93.9712 | 99.62% | 99.62% | 99.87% | 99.61% | 99.61% | 99.83% | 132.8472 | 142.116 | 174.0171 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 132.5327 | 11 | 23 | 14 | 22 | 98.91% | 0.085025 | 0.086709 | 41.8267 | 40.2185 | 141.554 | 18.291 | 98.91% | 3724.027 | 99.51% | 99.65% | 85.01% |  |  | 99.52% | 0.97997
2021-04-17 | 189.6434 | 172.0493 | 172.0493 | 160.6935 | 147.9767 | 14.0401 | 14.0401 | 3471.2737 | 1013.8323 | 308.5577 | 612.0658 | 18.7891 | 9.3945 | 19.6431 | 11.9567 | 9546.4983 | 395.995 |  |  | 25.3493 | 0.98821 | 12.6155 | 4083.3395 | 2148.8837 | 1934.4558 | 920.6234 | 17.5941 | 11.3558 | 12.6168 | 14.1685 | 10.8625 | 6.6119 | 3650.6469 | 7649.2731 | 11499.4353 | 2459.1461 | 5165.8105 | 9314.1847 | 0.09059 | 0.084789 | 0.06967 | 17.3849 | 10.7054 | 11.887 | 9.2002 | 19.5166 | 15.3718 | 154.5575 | 126.6005 | 93.7839 | 99.62% | 99.62% | 99.87% | 99.63% | 99.62% | 99.83% | 132.4649 | 141.5271 | 172.2394 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 133.9117 | 11 | 23 | 14 | 22 | 98.92% | 0.085387 | 0.087036 | 41.5666 | 39.9773 | 141.9795 | 18.3808 | 98.92% | 3859.0007 | 99.51% | 99.66% | 85.01% |  |  | 99.52% | 0.98821
2021-04-16 | 188.2072 | 170.9132 | 170.9132 | 159.7704 | 147.2337 | 14.175 | 14.175 | 3434.0985 | 1002.9748 | 305.2532 | 605.6887 | 18.7269 | 9.3635 | 19.5781 | 11.9171 | 9644.8554 | 387.8835 |  |  | 25.3359 | 0.98865 | 12.5738 | 4039.7872 | 2125.8705 | 1913.9167 | 910.9419 | 17.2941 | 11.1428 | 12.3226 | 14.0167 | 10.7462 | 6.5411 | 3681.0438 | 7712.429 | 11593.3099 | 2479.6439 | 5208.6647 | 9390.6829 | 0.090553 | 0.084844 | 0.069963 | 17.3651 | 10.6736 | 11.7947 | 9.0007 | 19.094 | 15.0402 | 153.0338 | 125.2214 | 92.4332 | 99.62% | 99.62% | 99.87% | 99.64% | 99.63% | 99.84% | 132.5188 | 141.4366 | 171.5186 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 133.0739 | 11 | 23 | 14 | 22 | 98.93% | 0.085432 | 0.087055 | 40.7594 | 39.8334 | 140.4185 | 17.9829 | 98.93% | 3891.0058 | 99.52% | 99.67% | 85.01% |  |  | 99.53% | 0.98865
2021-04-15 | 190.5826 | 173.0116 | 173.0116 | 161.6394 | 148.8781 | 14.1004 | 14.1004 | 3470.9808 | 1013.7468 | 308.5316 | 613.5919 | 18.8688 | 9.4344 | 19.7265 | 12.0074 | 9773.5612 | 397.5313 |  |  | 25.1368 | 0.99536 | 12.669 | 4084.5727 | 2148.7024 | 1935.8703 | 922.1235 | 17.571 | 11.3722 | 12.591 | 14.1673 | 10.8616 | 6.6114 | 3730.6123 | 7810.2159 | 11731.3789 | 2513.5449 | 5277.0047 | 9506.3782 | 0.090875 | 0.085169 | 0.070242 | 17.3506 | 10.7045 | 11.8277 | 9.104 | 19.3237 | 15.2332 | 155.1762 | 126.9388 | 93.6865 | 99.62% | 99.63% | 99.87% | 99.64% | 99.63% | 99.84% | 132.0502 | 140.897 | 170.838 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 134.7606 | 11 | 23 | 14 | 22 | 98.94% | 0.085747 | 0.087374 | 41.5342 | 39.8828 | 142.367 | 18.1983 | 98.94% | 3942.2358 | 99.52% | 99.67% | 84.98% |  |  | 99.52% | 0.99536
2021-04-14 | 188.5955 | 171.1276 | 171.1276 | 159.8259 | 147.0536 | 13.8548 | 13.8548 | 3456.3081 | 1009.4614 | 307.2274 | 610.0569 | 18.3944 | 9.1972 | 19.2305 | 11.7055 | 9618.5702 | 390.7306 |  |  | 25.184 | 0.99377 | 12.3505 | 4066.365 | 2139.6193 | 1926.7457 | 917.2842 | 17.4679 | 11.3016 | 12.5569 | 14.1074 | 10.8157 | 6.5834 | 3680.8164 | 7710.3521 | 11587.4253 | 2479.5918 | 5207.8684 | 9387.1109 | 0.09124 | 0.085522 | 0.07057 | 17.367 | 10.7165 | 11.8927 | 8.9442 | 18.9768 | 14.9512 | 153.6548 | 125.6788 | 92.708 | 99.63% | 99.63% | 99.88% | 99.64% | 99.64% | 99.84% | 131.5214 | 140.3155 | 170.0437 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 133.2291 | 11 | 23 | 14 | 22 | 98.95% | 0.086103 | 0.087732 | 41.3265 | 39.9763 | 140.9902 | 17.8724 | 98.95% | 3890.4235 | 99.53% | 99.67% | 85% |  |  | 99.53% | 0.99377
2021-04-13 | 188.8135 | 171.1564 | 171.1564 | 159.7028 | 146.9126 | 13.8818 | 13.8818 | 3471.6015 | 1017.123 | 331.9033 | 614.2877 | 18.6604 | 9.44 | 19.319 | 18.2213 | 9558.7249 | 393.6781 |  |  | 25.344 | 0.98838 | 13.1739 | 4085.8893 | 2122.5752 | 1963.3141 | 946.1911 | 17.6572 | 11.4535 | 12.6021 | 13.995 | 10.8977 | 7.1122 | 3611.597 | 7473.1731 | 11501.1277 | 2452.2275 | 5082.4774 | 9199.5061 | 0.089886 | 0.085328 | 0.075167 | 17.3115 | 10.496 | 11.5574 | 9.1589 | 19.5761 | 25.5168 | 153.8892 | 126.2319 | 93.5194 | 99.62% | 99.62% | 99.8% | 99.63% | 99.61% | 99.72% | 133.5031 | 140.6336 | 159.6443 |  |  |  | 30.5 | 23.75 | 15.5 | 2379 | 1140 | 372 | 3891 | 133.039 | 10.75 | 22 | 20.75 | 21.25 | 98.93% | 0.086072 | 0.087143 | 41.7128 | 39.3649 | 141.2169 | 18.2177 | 98.93% | 3867.9234 | 99.52% | 99.64% | 84.97% |  |  | 99.52% | 0.98838
2021-04-12 | 186.4553 | 168.7916 | 168.7916 | 157.183 | 144.3676 | 13.876 | 13.876 | 3470.0926 | 1025.2546 | 394.3287 | 613.5516 | 17.5736 | 9.2493 | 17.5736 | 37.922 | 8967.5398 | 388.4331 |  |  | 25.1226 | 0.99584 | 14.967 | 4083.6442 | 2050.5092 | 2033.1349 | 1007.8803 | 17.6637 | 11.6086 | 12.8447 | 13.5198 | 10.9849 | 8.4499 | 3292.2357 | 6623.348 | 10855.7914 | 2280.1804 | 4575.9112 | 8393.8414 | 0.088348 | 0.086599 | 0.088465 | 17.0317 | 9.9555 | 11.1219 | 9.3937 | 20.0874 | 69.6713 | 152.3928 | 126.3196 | 95.1197 | 99.59% | 99.62% | 99.55% | 99.59% | 99.56% | 99.17% | 135.8262 | 138.5692 | 135.6468 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.4919 | 10 | 19 | 41 | 19 | 98.93% | 0.087807 | 0.087845 | 42.117 | 38.1092 | 140.0504 | 18.2943 | 98.93% | 3653.1987 | 99.52% | 99.51% | 84.98% |  |  | 99.52% | 0.99584
2021-04-11 | 186.4808 | 168.809 | 168.809 | 157.2481 | 144.4875 | 13.9706 | 13.9706 | 3472.348 | 1025.921 | 394.585 | 614.7198 | 17.8201 | 9.379 | 17.8201 | 38.4539 | 9129.4803 | 391.4366 |  |  | 25.267 | 0.99097 | 15.1769 | 4087.0678 | 2051.842 | 2035.2258 | 1009.3048 | 17.6718 | 11.561 | 12.6651 | 13.5286 | 10.992 | 8.4554 | 3344.6078 | 6726.1645 | 11018.9665 | 2316.6899 | 4647.9257 | 8522.2453 | 0.088121 | 0.086514 | 0.088688 | 17.0165 | 9.8975 | 10.9401 | 9.3356 | 19.9684 | 69.2886 | 152.1377 | 125.9074 | 94.4782 | 99.6% | 99.62% | 99.55% | 99.6% | 99.57% | 99.19% | 136.1771 | 138.706 | 135.3065 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.493 | 10 | 19 | 41 | 19 | 98.93% | 0.087697 | 0.08771 | 41.8978 | 37.8542 | 139.6904 | 18.1862 | 98.93% | 3710.6409 | 99.52% | 99.52% | 84.96% |  |  | 99.52% | 0.99097
2021-04-10 | 182.2638 | 165.4147 | 165.4147 | 154.3962 | 142.332 | 13.9208 | 13.9208 | 3386.8216 | 1000.6518 | 384.8661 | 597.4624 | 18.5985 | 9.7887 | 18.5985 | 40.1336 | 9481.0128 | 372.0166 |  |  | 25.4018 | 0.98645 | 15.8399 | 3984.2839 | 2001.3037 | 1982.9803 | 982.3284 | 16.8492 | 11.0185 | 12.1753 | 13.1954 | 10.7213 | 8.2471 | 3455.3434 | 6956.1939 | 11411.2982 | 2392.7205 | 4804.0531 | 8819.1965 | 0.087948 | 0.086647 | 0.089846 | 16.8607 | 9.8136 | 10.9619 | 9.1594 | 19.5769 | 67.848 | 148.0038 | 122.0574 | 90.548 | 99.59% | 99.61% | 99.54% | 99.62% | 99.59% | 99.23% | 136.445 | 138.4922 | 133.5622 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 128.3243 | 10 | 19 | 41 | 19 | 98.92% | 0.087835 | 0.087779 | 40.043 | 37.6363 | 135.2344 | 17.8289 | 98.92% | 3835.441 | 99.52% | 99.55% | 85% |  |  | 99.53% | 0.98645
2021-04-09 | 185.8224 | 168.4587 | 168.4587 | 157.2481 | 144.3371 | 13.8973 | 13.8973 | 3455.8069 | 1021.0339 | 392.7053 | 610.1941 | 18.7594 | 9.8734 | 18.7594 | 40.4808 | 9612.6246 | 389.3412 |  |  | 25.2979 | 0.98993 | 15.9769 | 4066.001 | 2042.0677 | 2023.9333 | 1002.8994 | 17.3637 | 11.2106 | 12.5186 | 13.4642 | 10.9396 | 8.4151 | 3475.8539 | 6995.4598 | 11471.5068 | 2407.1199 | 4831.9509 | 8867.4869 | 0.088119 | 0.086712 | 0.089805 | 16.8533 | 9.6819 | 10.9237 | 9.4035 | 20.1029 | 69.6938 | 151.257 | 124.8901 | 92.7603 | 99.59% | 99.61% | 99.54% | 99.61% | 99.58% | 99.21% | 136.1798 | 138.3891 | 133.6224 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.5421 | 10 | 19 | 41 | 19 | 98.92% | 0.087938 | 0.087895 | 41.0929 | 37.4589 | 138.4199 | 18.3081 | 98.92% | 3857.6798 | 99.51% | 99.54% | 84.99% |  |  | 99.52% | 0.98993
2021-04-08 | 187.6594 | 170.0898 | 170.0898 | 158.6456 | 145.9101 | 13.9066 | 13.9066 | 3468.7891 | 1024.8695 | 394.1806 | 613.5295 | 19.7442 | 10.3917 | 19.7442 | 42.606 | 9774.6766 | 400.5126 |  |  | 25.4038 | 0.98638 | 16.8157 | 4082.3186 | 2049.739 | 2032.5796 | 1007.7101 | 17.5697 | 11.4442 | 12.6161 | 13.5148 | 10.9807 | 8.4467 | 3448.303 | 6935.2438 | 11363.6274 | 2388.613 | 4792.1946 | 8787.9153 | 0.087085 | 0.085555 | 0.088031 | 16.9489 | 9.8181 | 10.926 | 9.9754 | 21.3372 | 74.0286 | 153.0769 | 126.5988 | 94.6447 | 99.56% | 99.59% | 99.52% | 99.58% | 99.55% | 99.16% | 137.7965 | 140.2603 | 136.3153 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 132.0503 | 10 | 19 | 41 | 19 | 98.85% | 0.086747 | 0.086741 | 41.63 | 37.6929 | 140.2992 | 19.4321 | 98.85% | 3825.9556 | 99.48% | 99.51% | 84.97% |  |  | 99.49% | 0.98638
2021-04-07 | 187.9134 | 170.3265 | 170.3265 | 158.8163 | 146.1271 | 13.8637 | 13.8637 | 3472.8366 | 1026.0654 | 394.6405 | 611.8975 | 18.9251 | 9.9606 | 18.9251 | 40.8385 | 9510.9392 | 400.6971 |  |  | 25.3319 | 0.98879 | 16.1181 | 4084.7341 | 2052.1307 | 2032.6034 | 1006.538 | 17.5869 | 11.5102 | 12.7209 | 13.5305 | 10.9936 | 8.4566 | 3402.5944 | 6851.9084 | 11244.677 | 2356.0799 | 4731.2971 | 8688.5609 | 0.087144 | 0.085495 | 0.087678 | 16.9554 | 9.8803 | 11.0453 | 9.7286 | 20.7901 | 72.028 | 153.5257 | 127.1458 | 95.3694 | 99.58% | 99.6% | 99.53% | 99.59% | 99.56% | 99.17% | 137.7032 | 140.3595 | 136.8649 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 132.3457 | 10 | 19 | 41 | 19 | 98.89% | 0.086702 | 0.086717 | 41.818 | 37.881 | 140.8437 | 18.9333 | 98.89% | 3777.4487 | 99.5% | 99.51% | 85.02% |  |  | 99.5% | 0.98879
2021-04-06 | 188.259 | 170.5698 | 170.5698 | 158.9281 | 146.3085 | 13.8268 | 13.8268 | 3470.1868 | 1025.2825 | 394.3394 | 613.139 | 19.0598 | 10.0315 | 19.0598 | 41.1291 | 9423.48 | 399.1393 |  |  | 25.0754 | 0.99744 | 16.2328 | 4083.3257 | 2050.5649 | 2032.7608 | 1007.4784 | 17.6892 | 11.6418 | 12.7412 | 13.5202 | 10.9852 | 8.4501 | 3381.8291 | 6804.025 | 11153.5714 | 2342.3005 | 4700.57 | 8623.3999 | 0.087611 | 0.085928 | 0.087907 | 17.0592 | 9.9878 | 11.0407 | 9.9342 | 21.2431 | 73.672 | 153.9263 | 127.5146 | 95.8801 | 99.57% | 99.59% | 99.52% | 99.58% | 99.55% | 99.15% | 136.9695 | 139.6521 | 136.5084 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 132.5017 | 10 | 19 | 41 | 19 | 98.87% | 0.08712 | 0.087147 | 42.0722 | 38.0877 | 141.3099 | 19.3463 | 98.87% | 3752.8233 | 99.49% | 99.5% | 84.98% |  |  | 99.49% | 0.99744
2021-04-05 | 186.5425 | 168.8728 | 168.8728 | 157.2172 | 144.43 | 13.8287 | 13.8287 | 3471.5459 | 1025.684 | 394.4938 | 612.9679 | 18.6665 | 9.8245 | 18.6665 | 40.2803 | 8937.4898 | 394.9057 |  |  | 25.0321 | 0.99891 | 15.8977 | 4084.5138 | 2051.368 | 2033.1458 | 1007.4618 | 17.6697 | 11.6556 | 12.7585 | 13.5255 | 10.9895 | 8.4534 | 3219.6446 | 6478.5197 | 10622.0413 | 2229.9503 | 4475.3861 | 8211.5857 | 0.088434 | 0.086483 | 0.087834 | 17.0338 | 9.9979 | 11.0575 | 10.2384 | 21.8922 | 75.9113 | 152.7784 | 126.9327 | 96.1384 | 99.56% | 99.58% | 99.51% | 99.54% | 99.51% | 99.08% | 135.6948 | 138.756 | 136.6212 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.5488 | 10 | 19 | 41 | 19 | 98.84% | 0.087713 | 0.087789 | 42.0838 | 38.0892 | 140.6688 | 19.9371 | 98.84% | 3573.1058 | 99.48% | 99.46% | 84.99% |  |  | 99.48% | 0.99891
2021-04-04 | 186.5054 | 168.8176 | 168.8176 | 157.1271 | 144.4311 | 13.8414 | 13.8414 | 3472.8304 | 1026.0635 | 394.6398 | 613.04 | 18.3478 | 9.6567 | 18.3478 | 39.5926 | 8976.2189 | 394.4961 |  |  | 25.0505 | 0.99828 | 15.6263 | 4085.8704 | 2052.127 | 2033.7434 | 1007.6799 | 17.6878 | 11.6905 | 12.8926 | 13.5305 | 10.9935 | 8.4566 | 3230.1525 | 6500.552 | 10659.7448 | 2237.1032 | 4490.2637 | 8240.0723 | 0.088466 | 0.086571 | 0.087997 | 17.0432 | 10.0238 | 11.1708 | 10.0288 | 21.4417 | 74.3383 | 152.6828 | 126.7713 | 95.9352 | 99.57% | 99.59% | 99.52% | 99.55% | 99.52% | 99.1% | 135.6448 | 138.6151 | 136.3676 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.5461 | 10 | 19 | 41 | 19 | 98.86% | 0.087785 | 0.087853 | 42.271 | 38.2377 | 140.5024 | 19.5269 | 98.86% | 3584.9653 | 99.49% | 99.47% | 85% |  |  | 99.49% | 0.99828
2021-04-03 | 186.7723 | 169.2368 | 169.2368 | 157.7436 | 144.8696 | 13.9435 | 13.9435 | 3467.7432 | 1024.5605 | 394.0617 | 612.4796 | 18.9998 | 9.9999 | 18.9998 | 40.9996 | 9307.6694 | 393.6948 |  |  | 25.0649 | 0.9978 | 16.1817 | 4080.2228 | 2049.121 | 2031.1018 | 1006.5413 | 17.5355 | 11.4933 | 12.7037 | 13.5107 | 10.9774 | 8.4442 | 3339.1772 | 6718.7925 | 11015.2009 | 2312.724 | 4641.4633 | 8515.8547 | 0.088372 | 0.086632 | 0.088701 | 16.9308 | 9.873 | 11.0244 | 10.026 | 21.4384 | 74.3417 | 152.5475 | 126.4344 | 94.9888 | 99.57% | 99.59% | 99.52% | 99.57% | 99.54% | 99.13% | 135.7896 | 138.5171 | 135.2863 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.9141 | 10 | 19 | 41 | 19 | 98.86% | 0.087868 | 0.087895 | 41.7325 | 37.8283 | 140.0747 | 19.524 | 98.86% | 3705.6618 | 99.49% | 99.49% | 84.99% |  |  | 99.49% | 0.9978
2021-04-02 | 186.6879 | 169.0379 | 169.0379 | 157.3858 | 145.1294 | 14.0086 | 14.0086 | 3470.7882 | 1025.4601 | 394.4077 | 614.1892 | 21.2264 | 11.1718 | 21.2264 | 45.8042 | 9709.9271 | 394.949 |  |  | 25.0412 | 0.9986 | 18.0779 | 4084.9774 | 2050.9203 | 2034.0571 | 1008.5969 | 17.6499 | 11.6521 | 12.6233 | 13.5226 | 10.9871 | 8.4516 | 3416.2402 | 6868.0169 | 11248.9691 | 2366.8426 | 4746.798 | 8701.1301 | 0.088795 | 0.087371 | 0.089811 | 17.0091 | 9.9848 | 10.9165 | 10.9633 | 23.4587 | 81.422 | 152.076 | 125.5755 | 93.9724 | 99.53% | 99.55% | 99.47% | 99.54% | 99.51% | 99.06% | 135.1424 | 137.3449 | 133.6139 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 130.9207 | 10 | 19 | 41 | 19 | 98.76% | 0.088502 | 0.08849 | 41.9254 | 37.9104 | 139.362 | 21.3636 | 98.76% | 3789.8167 | 99.44% | 99.45% | 84.96% |  |  | 99.44% | 0.9986
2021-04-01 | 186.2511 | 169.4042 | 169.4042 | 158.2435 | 145.7786 | 14.0176 | 14.0176 | 3390.9289 | 1001.8654 | 385.3328 | 598.2695 | 19.3478 | 10.183 | 19.3478 | 41.7505 | 9482.7798 | 382.5816 |  |  | 25.3092 | 0.98955 | 16.478 | 3989.1984 | 2003.7307 | 1985.4677 | 983.6024 | 16.8469 | 11.1607 | 12.2465 | 13.2114 | 10.7343 | 8.2571 | 3402.8612 | 6849.1979 | 11233.7318 | 2356.6164 | 4730.6764 | 8682.8197 | 0.085965 | 0.084136 | 0.086201 | 16.8272 | 9.9214 | 11.0043 | 9.7166 | 20.7718 | 72.0028 | 152.0779 | 126.2496 | 94.7881 | 99.57% | 99.59% | 99.52% | 99.59% | 99.56% | 99.17% | 139.5918 | 142.6266 | 139.2091 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 131.8425 | 10 | 19 | 41 | 19 | 98.86% | 0.085417 | 0.085451 | 40.2542 | 37.7529 | 139.4197 | 18.9167 | 98.86% | 3776.93 | 99.49% | 99.51% | 85% |  |  | 99.5% | 0.98955
2021-03-31 | 190.6211 | 172.9891 | 172.9891 | 161.3914 | 148.6801 | 13.9228 | 13.9228 | 3472.0775 | 1025.8411 | 394.5543 | 611.9725 | 18.357 | 9.6616 | 18.357 | 39.6124 | 9471.0032 | 401.6018 |  |  | 25.1581 | 0.99464 | 15.6342 | 4084.05 | 2051.6822 | 2032.3678 | 1006.5267 | 17.632 | 11.5976 | 12.7596 | 13.5276 | 10.9912 | 8.4547 | 3381.2447 | 6808.6633 | 11172.8429 | 2341.2717 | 4701.5333 | 8633.4174 | 0.086127 | 0.08419 | 0.085685 | 17.0027 | 9.9566 | 11.0783 | 9.5504 | 20.4092 | 70.7125 | 156.2242 | 129.8515 | 98.1439 | 99.59% | 99.61% | 99.54% | 99.59% | 99.57% | 99.18% | 139.3295 | 142.534 | 140.0484 |  |  |  | 32 | 26 | 20 | 2496 | 1248 | 480 | 4224 | 134.7078 | 10 | 19 | 41 | 19 | 98.91% | 0.085436 | 0.085504 | 41.9893 | 38.0376 | 143.595 | 18.5867 | 98.91% | 3753.6383 | 99.51% | 99.52% | 85.02% |  |  | 99.51% | 0.99464
2021-03-30 | 190.9324 | 173.1842 | 173.1842 | 161.4756 | 148.7632 | 13.8204 | 13.8204 | 3470.9733 | 1030.8445 | 364.6452 | 613.0093 | 18.409 | 9.689 | 18.409 | 39.7247 | 9348.1698 | 401.54 |  |  | 24.7488 | 1.0086 | 15.4341 | 4083.9826 | 2075.4835 | 2008.4991 | 977.6545 | 17.7482 | 11.7086 | 12.8224 | 13.6845 | 11.0448 | 7.8138 | 3391.832 | 6948.7885 | 11058.6069 | 2333.2819 | 4752.2953 | 8687.705 | 0.088124 | 0.085795 | 0.080369 | 17.2157 | 10.3193 | 11.4263 | 9.858 | 20.6325 | 66.041 | 156.62 | 129.8401 | 98.0591 | 99.58% | 99.61% | 99.54% | 99.58% | 99.57% | 99.24% | 136.1716 | 139.8688 | 149.3113 |  |  |  | 31.1042 | 25.1042 | 17.7604 | 2426.125 | 1205 | 426.25 | 4057.375 | 134.9386 | 10 | 19 | 41 | 19 | 98.9% | 0.086138 | 0.086618 | 42.2792 | 38.9613 | 144.1433 | 19.0693 | 98.9% | 3719.2726 | 99.51% | 99.52% | 84.99% |  |  | 99.5% | 1.0086
2021-03-29 | 189.7988 | 171.9609 | 171.9609 | 160.1393 | 147.3694 | 13.7963 | 13.7963 | 3473.0375 | 1038.6654 | 324.5829 | 612.4343 | 17.9455 | 9.445 | 17.9455 | 38.7244 | 8900.9977 | 398.7777 |  |  | 24.7119 | 1.0099 | 14.7236 | 4085.4718 | 2109.7891 | 1975.6827 | 937.0173 | 17.8379 | 11.8217 | 12.9141 | 13.9107 | 11.1286 | 6.9553 | 3297.4822 | 6932.7848 | 10586.5551 | 2247.2569 | 4673.0267 | 8503.4124 | 0.090111 | 0.087133 | 0.071941 | 17.437 | 10.8155 | 11.9702 | 10.1553 | 20.6352 | 58.6207 | 155.8945 | 128.9784 | 97.6346 | 99.58% | 99.62% | 99.54% | 99.55% | 99.56% | 99.31% | 133.1692 | 137.7209 | 166.8041 |  |  |  | 30 | 24 | 15 | 2340 | 1152 | 360 | 3852 | 133.5646 | 10 | 19 | 41 | 19 | 98.88% | 0.086251 | 0.087522 | 42.5737 | 40.2228 | 143.9347 | 19.4709 | 98.88% | 3557.4082 | 99.5% | 99.51% | 85.01% |  |  | 99.49% | 1.0099
2021-03-28 | 190.1935 | 172.4596 | 172.4596 | 160.679 | 147.7094 | 13.8876 | 13.8876 | 3472.5382 | 1037.0858 | 325.2146 | 613.3493 | 17.5334 | 9.2281 | 17.5334 | 37.8352 | 8867.0712 | 399.7787 |  |  | 24.746 | 1.0087 | 14.3876 | 4085.8874 | 2110.2378 | 1975.6497 | 938.5639 | 17.7339 | 11.7806 | 12.9961 | 13.9137 | 11.1116 | 6.9689 | 3289.9628 | 6905.9022 | 10547.5398 | 2241.9053 | 4659.0946 | 8471.1993 | 0.089806 | 0.086567 | 0.071626 | 17.3337 | 10.7696 | 12.0175 | 9.9364 | 20.1675 | 57.5374 | 156.2756 | 129.474 | 98.1399 | 99.59% | 99.62% | 99.55% | 99.56% | 99.57% | 99.32% | 133.6215 | 138.6216 | 167.5361 |  |  |  | 30.0521 | 24 | 15.0521 | 2344.0625 | 1152 | 361.25 | 3857.3125 | 133.7661 | 10 | 19 | 41 | 19 | 98.9% | 0.085861 | 0.087136 | 42.5106 | 40.1208 | 144.3172 | 19.0537 | 98.9% | 3547.2013 | 99.51% | 99.52% | 84.99% |  |  | 99.5% | 1.0087
2021-03-27 | 192.2095 | 174.5105 | 174.5105 | 162.7958 | 149.7146 | 13.9743 | 13.9743 | 3467.6196 | 1010.2928 | 336.7643 | 613.0732 | 17.9137 | 9.4282 | 17.9137 | 38.6558 | 9192.1232 | 404.2166 |  |  | 24.4385 | 1.0193 | 14.739 | 4080.6928 | 2120.5625 | 1960.1303 | 949.8375 | 17.699 | 11.7147 | 12.9801 | 13.9817 | 10.8246 | 7.2164 | 3424.8804 | 7048.6942 | 10899.3445 | 2325.1909 | 4808.2888 | 8696.0545 | 0.090312 | 0.084402 | 0.074305 | 17.3887 | 10.7328 | 11.8763 | 9.9398 | 19.6548 | 59.9241 | 157.8069 | 130.727 | 98.9939 | 99.59% | 99.63% | 99.56% | 99.57% | 99.59% | 99.31% | 132.8732 | 142.1763 | 161.496 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 135.7598 | 10 | 19 | 41 | 19 | 98.91% | 0.08586 | 0.087035 | 42.3937 | 39.9977 | 145.5529 | 19.0006 | 98.91% | 3667.3609 | 99.51% | 99.54% | 84.98% |  |  | 99.5% | 1.0193
2021-03-26 | 188.9001 | 171.921 | 171.921 | 160.764 | 147.9455 | 13.9372 | 13.9372 | 3392.7049 | 988.4664 | 329.4888 | 598.2586 | 18.4619 | 9.7168 | 18.4619 | 39.8388 | 9352.0928 | 386.6924 |  |  | 24.2071 | 1.0274 | 15.19 | 3990.9636 | 2074.7498 | 1916.2138 | 927.7474 | 16.979 | 11.157 | 12.3698 | 13.6797 | 10.5907 | 7.0605 | 3490.3739 | 7189.5148 | 11127.1733 | 2369.1378 | 4902.0476 | 8873.5149 | 0.090864 | 0.085016 | 0.075366 | 17.2506 | 10.5797 | 11.7309 | 9.9149 | 19.5938 | 59.6852 | 154.6763 | 127.9875 | 96.2492 | 99.59% | 99.62% | 99.55% | 99.58% | 99.6% | 99.33% | 132.0651 | 141.1504 | 159.2221 |  |  |  | 31 | 24 | 16 | 2418 | 1152 | 384 | 3954 | 134.0886 | 10 | 19 | 41 | 19 | 98.9% | 0.086513 | 0.087655 | 40.5058 | 39.5613 | 142.3215 | 18.9422 | 98.9% | 3738.787 | 99.51% | 99.55% | 85.01% |  |  | 99.5% | 1.0274
2021-03-25 | 190.4253 | 172.9124 | 172.9124 | 161.3184 | 148.634 | 13.8822 | 13.8822 | 3438.3296 | 1010.9721 | 349.8811 | 606.9356 | 18.1993 | 9.5786 | 18.1993 | 39.2721 | 9324.1174 | 395.2704 |  |  | 24.0464 | 1.0331 | 15.1349 | 4045.2652 | 2077.4764 | 1967.7888 | 956.8167 | 17.5129 | 11.594 | 12.8075 | 13.6976 | 10.8318 | 7.4975 | 3439.1443 | 7053.7134 | 11097.3388 | 2351.378 | 4820.994 | 8772.2057 | 0.090664 | 0.086597 | 0.079497 | 17.3251 | 10.5426 | 11.7089 | 9.915 | 20.1978 | 63.5477 | 156.0777 | 129.2192 | 97.4293 | 99.59% | 99.62% | 99.55% | 99.58% | 99.58% | 99.28% | 132.3571 | 138.5726 | 150.9484 |  |  |  | 29.2316 | 23.1158 | 16 | 2280.0632 | 1109.5579 | 384 | 3773.6211 | 134.7414 | 10 | 19 | 41 | 19 | 98.92% | 0.087576 | 0.088332 | 41.9144 | 39.5766 | 143.5974 | 19.0684 | 98.92% | 3730.8964 | 99.51% | 99.53% | 85% |  |  | 99.5% | 1.0331
2021-03-24 | 191.4066 | 173.8476 | 173.8476 | 162.1425 | 149.1249 | 13.7266 | 13.7266 | 3454.7586 | 1017.0809 | 353.7673 | 609.4617 | 17.2602 | 9.0843 | 17.2602 | 37.2456 | 9105.7245 | 398.5081 |  |  | 24.2845 | 1.0247 | 14.375 | 4064.2202 | 2083.9104 | 1980.3099 | 963.2289 | 17.5591 | 11.7051 | 12.9291 | 13.7401 | 10.8973 | 7.5807 | 3402.9569 | 6977.9405 | 11006.7267 | 2328.6374 | 4769.799 | 8688.415 | 0.089505 | 0.085562 | 0.078741 | 17.2353 | 10.5411 | 11.7195 | 9.4473 | 19.3202 | 61.0267 | 157.3028 | 130.5058 | 98.6513 | 99.61% | 99.64% | 99.57% | 99.59% | 99.59% | 99.3% | 134.0713 | 140.2489 | 152.3983 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 135.4594 | 10 | 19 | 41 | 19 | 98.96% | 0.086521 | 0.087242 | 42.1933 | 39.4959 | 144.8628 | 18.1811 | 98.96% | 3698.5566 | 99.53% | 99.55% | 85% |  |  | 99.52% | 1.0247
2021-03-23 | 192.0356 | 174.2467 | 174.2467 | 162.3625 | 149.267 | 13.8207 | 13.8207 | 3472.5681 | 1022.324 | 355.591 | 614.311 | 17.2069 | 9.0562 | 17.2069 | 37.1306 | 8941.247 | 402.5827 |  |  | 24.1586 | 1.0291 | 14.3306 | 4086.8791 | 2094.6531 | 1992.2261 | 969.902 | 17.7889 | 11.8842 | 13.0377 | 13.8109 | 10.9535 | 7.6198 | 3311.387 | 6783.6135 | 10688.7823 | 2266.617 | 4639.4727 | 8442.2855 | 0.089937 | 0.085804 | 0.078441 | 17.3121 | 10.6017 | 11.6892 | 9.7677 | 19.9895 | 63.2061 | 158.0327 | 131.3726 | 99.9683 | 99.6% | 99.63% | 99.56% | 99.57% | 99.57% | 99.25% | 133.4273 | 139.8533 | 152.9812 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 135.4049 | 10 | 19 | 41 | 19 | 98.94% | 0.086775 | 0.087543 | 42.7108 | 39.6031 | 145.8745 | 18.8106 | 98.94% | 3597.5742 | 99.52% | 99.52% | 84.97% |  |  | 99.51% | 1.0291
2021-03-22 | 190.4014 | 172.5318 | 172.5318 | 160.3934 | 147.397 | 13.7374 | 13.7374 | 3472.2976 | 1022.2444 | 355.5633 | 612.6886 | 16.2655 | 8.5608 | 16.2655 | 35.0992 | 8393.2994 | 398.8657 |  |  | 24.0973 | 1.0313 | 13.5466 | 4084.9862 | 2094.4899 | 1990.4963 | 968.2519 | 17.8696 | 12.1383 | 13.2963 | 13.8098 | 10.9526 | 7.6192 | 3114.9569 | 6386.4401 | 10072.3312 | 2131.6985 | 4365.8365 | 7951.4168 | 0.090646 | 0.086237 | 0.078125 | 17.4063 | 10.847 | 11.9581 | 9.8375 | 20.1208 | 63.5649 | 157.1135 | 130.9774 | 100.5762 | 99.6% | 99.63% | 99.56% | 99.54% | 99.54% | 99.2% | 132.3834 | 139.151 | 153.6008 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 133.6758 | 10 | 19 | 41 | 19 | 98.93% | 0.087232 | 0.088066 | 43.3043 | 40.2114 | 145.4526 | 18.9343 | 98.93% | 3385.3679 | 99.52% | 99.48% | 85% |  |  | 99.5% | 1.0313
2021-03-21 | 189.1451 | 171.6568 | 171.6568 | 159.955 | 146.8756 | 13.8427 | 13.8427 | 3437.8175 | 1012.0935 | 352.0325 | 607.3069 | 16.3075 | 8.5829 | 16.3075 | 35.1899 | 8542.33 | 391.1626 |  |  | 24.2238 | 1.0268 | 13.5816 | 4045.1244 | 2073.6915 | 1971.4329 | 959.3394 | 17.4883 | 11.7018 | 12.8489 | 13.6727 | 10.8439 | 7.5436 | 3171.503 | 6500.2026 | 10247.7223 | 2170.5624 | 4444.4358 | 8091.5864 | 0.090142 | 0.085769 | 0.078012 | 17.2857 | 10.607 | 11.7142 | 9.5488 | 19.5346 | 61.7357 | 155.7484 | 129.8226 | 99.2906 | 99.6% | 99.63% | 99.57% | 99.56% | 99.56% | 99.24% | 133.124 | 139.9115 | 153.8223 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 133.0104 | 10 | 19 | 41 | 19 | 98.95% | 0.086801 | 0.087612 | 42.039 | 39.6069 | 144.0415 | 18.3827 | 98.95% | 3446.3036 | 99.53% | 99.51% | 84.99% |  |  | 99.52% | 1.0268
2021-03-20 | 192.1602 | 174.5087 | 174.5087 | 162.8471 | 149.4909 | 14.006 | 14.006 | 3470.4532 | 1021.7014 | 355.3744 | 613.0654 | 16.9902 | 8.9422 | 16.9902 | 36.663 | 9000.6272 | 402.5375 |  |  | 24.2523 | 1.0258 | 14.1501 | 4083.5186 | 2093.3774 | 1990.1412 | 968.4398 | 17.6515 | 11.6616 | 12.9015 | 13.8025 | 10.9468 | 7.6152 | 3319.7247 | 6804.101 | 10726.9686 | 2271.9857 | 4652.1813 | 8469.9377 | 0.089605 | 0.085398 | 0.07812 | 17.2016 | 10.4219 | 11.5968 | 9.5853 | 19.6089 | 61.9698 | 158.0132 | 131.4959 | 99.9966 | 99.61% | 99.63% | 99.57% | 99.58% | 99.58% | 99.27% | 133.9204 | 140.5192 | 153.6089 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 135.4856 | 10 | 19 | 41 | 19 | 98.95% | 0.086421 | 0.087191 | 42.2146 | 39.2203 | 145.8799 | 18.4527 | 98.95% | 3607.3855 | 99.53% | 99.53% | 84.99% |  |  | 99.52% | 1.0258
2021-03-19 | 192.8458 | 175.0402 | 175.0402 | 163.1603 | 150.1797 | 14.1913 | 14.1913 | 3470.4937 | 1021.7134 | 355.3786 | 613.4002 | 17.3523 | 9.1328 | 17.3523 | 37.4444 | 9127.8637 | 404.4695 |  |  | 24.2223 | 1.0269 | 14.4517 | 4083.894 | 2093.4018 | 1990.4921 | 968.7788 | 17.8056 | 11.8799 | 13.0711 | 13.8026 | 10.9469 | 7.6153 | 3365.0892 | 6895.7483 | 10869.1641 | 2303.1682 | 4715.3526 | 8583.1868 | 0.089546 | 0.085536 | 0.078395 | 17.3486 | 10.6132 | 11.7418 | 9.6671 | 19.7791 | 62.5203 | 158.2816 | 131.419 | 99.75 | 99.6% | 99.63% | 99.56% | 99.58% | 99.58% | 99.27% | 134.0086 | 140.2913 | 153.0712 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 135.9842 | 10 | 19 | 41 | 19 | 98.95% | 0.086479 | 0.087224 | 42.7566 | 39.7036 | 145.9491 | 18.6127 | 98.95% | 3656.3892 | 99.53% | 99.53% | 84.98% |  |  | 99.51% | 1.0269
2021-03-18 | 192.5282 | 174.9632 | 174.9632 | 163.2318 | 150.4144 | 14.0485 | 14.0485 | 3448.0042 | 1015.0924 | 353.0756 | 607.8556 | 17.5065 | 9.214 | 17.5065 | 37.7773 | 9280.4488 | 400.3851 |  |  | 24.001 | 1.0347 | 14.5802 | 4055.8599 | 2079.8362 | 1976.0237 | 960.9313 | 17.565 | 11.7314 | 12.911 | 13.7132 | 10.876 | 7.5659 | 3413.5099 | 7000.923 | 11045.4971 | 2335.7598 | 4784.9953 | 8717.9499 | 0.089765 | 0.085763 | 0.078776 | 17.2954 | 10.6003 | 11.7467 | 9.6272 | 19.6855 | 62.1673 | 158.0645 | 131.2116 | 99.3737 | 99.61% | 99.63% | 99.57% | 99.59% | 99.59% | 99.29% | 133.682 | 139.9204 | 152.331 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 136.3088 | 10 | 19 | 41 | 19 | 98.95% | 0.086726 | 0.087462 | 42.2074 | 39.6424 | 145.587 | 18.5248 | 98.95% | 3710.351 | 99.53% | 99.54% | 85.01% |  |  | 99.52% | 1.0347
2021-03-17 | 194.4169 | 176.7489 | 176.7489 | 164.9777 | 151.9335 | 13.9897 | 13.9897 | 3460.3803 | 1018.736 | 354.3429 | 610.5523 | 17.6558 | 9.2925 | 17.6558 | 38.0995 | 9349.366 | 405.1097 |  |  | 23.8894 | 1.0386 | 14.7045 | 4070.9327 | 2087.3014 | 1983.6312 | 964.8953 | 17.668 | 11.7712 | 12.9851 | 13.7624 | 10.915 | 7.5931 | 3438.9349 | 7051.1198 | 11121.2283 | 2353.3355 | 4820.0487 | 8779.1937 | 0.089409 | 0.085327 | 0.078269 | 17.2992 | 10.5737 | 11.7393 | 9.7084 | 19.8555 | 62.7229 | 159.8729 | 132.8616 | 100.7604 | 99.61% | 99.63% | 99.57% | 99.59% | 99.59% | 99.29% | 134.2139 | 140.6346 | 153.3171 |  |  |  | 29 | 23 | 16 | 2262 | 1104 | 384 | 3750 | 137.98 | 10 | 19 | 41 | 19 | 98.95% | 0.086321 | 0.087067 | 42.4243 | 39.6122 | 147.3164 | 18.6847 | 98.95% | 3737.5438 | 99.53% | 99.54% | 85% |  |  | 99.51% | 1.0386
2021-03-16 | 195.3736 | 177.5233 | 177.5233 | 165.4563 | 152.1853 | 13.8534 | 13.8534 | 3471.8674 | 1016.8302 | 353.6801 | 613.1886 | 16.9865 | 9.437 | 16.7506 | 35.6245 | 8927.8272 | 409.1863 |  |  | 23.4574 | 1.0541 | 14.2467 | 4085.0559 | 2101.357 | 1983.6989 | 966.8687 | 17.8503 | 12.067 | 13.1958 | 13.8551 | 10.8946 | 7.5789 | 3317.4136 | 6788.6336 | 10683.6911 | 2266.0408 | 4645.7072 | 8443.7844 | 0.090541 | 0.085392 | 0.077621 | 17.4164 | 10.8281 | 11.8777 | 10.462 | 19.7991 | 61.773 | 161.312 | 134.4916 | 102.9266 | 99.58% | 99.64% | 99.58% | 99.54% | 99.57% | 99.27% | 132.5371 | 140.5283 | 154.5981 |  |  |  | 29.25 | 23 | 16 | 2281.5 | 1104 | 384 | 3769.5 | 138.4138 | 10 | 17.75 | 37.75 | 18 | 98.95% | 0.086826 | 0.087717 | 43.1131 | 40.1222 | 149.1095 | 19.0455 | 98.95% | 3592.3189 | 99.53% | 99.51% | 84.99% |  |  | 99.5% | 1.0541
2021-03-15 | 192.9557 | 175.2335 | 175.2335 | 163.1338 | 150.0491 | 13.807 | 13.807 | 3470.8822 | 1001.0068 | 348.1763 | 610.856 | 16.3917 | 10.9278 | 15.2989 | 30.5978 | 8571.7218 | 403.1754 |  |  | 23.5248 | 1.0517 | 14.1616 | 4081.7382 | 2121.6991 | 1960.0391 | 959.0323 | 17.7222 | 12.0997 | 13.1798 | 13.9892 | 10.7251 | 7.4609 | 3215.8478 | 6556.4767 | 10276.103 | 2183.7597 | 4496.1287 | 8139.5716 | 0.092286 | 0.084827 | 0.076748 | 17.4073 | 11.0337 | 11.9787 | 12.6635 | 18.3516 | 54.0579 | 159.4234 | 132.9725 | 102.2396 | 99.5% | 99.66% | 99.62% | 99.42% | 99.59% | 99.34% | 130.0301 | 141.4643 | 156.355 |  |  |  | 30 | 23 | 16 | 2340 | 1104 | 384 | 3828 | 136.1227 | 10 | 14 | 28 | 15 | 98.94% | 0.087413 | 0.088576 | 43.0017 | 40.4197 | 147.6259 | 19.0975 | 98.94% | 3448.098 | 99.52% | 99.46% | 85.03% |  |  | 99.5% | 1.0517
2021-03-14 | 191.6724 | 174.0977 | 174.0977 | 162.1758 | 148.8573 | 13.8246 | 13.8246 | 3465.411 | 999.4289 | 347.6274 | 612.0048 | 16.6399 | 11.0933 | 15.5306 | 31.0612 | 8758.8871 | 398.8415 |  |  | 23.9597 | 1.0361 | 14.3761 | 4077.4158 | 2118.3547 | 1959.0611 | 959.6322 | 17.5747 | 11.9219 | 13.0711 | 13.9672 | 10.7082 | 7.4492 | 3285.1163 | 6690.2941 | 10472.8333 | 2231.4643 | 4590.7324 | 8300.9318 | 0.091618 | 0.084415 | 0.07692 | 17.2852 | 10.8737 | 11.8601 | 12.3747 | 17.9471 | 52.9295 | 157.9586 | 131.4362 | 100.3426 | 99.5% | 99.66% | 99.63% | 99.45% | 99.61% | 99.36% | 130.9779 | 142.1553 | 156.0061 |  |  |  | 30 | 23 | 16 | 2340 | 1104 | 384 | 3828 | 135.0326 | 10 | 14 | 28 | 15 | 98.95% | 0.086962 | 0.088066 | 42.5677 | 40.019 | 145.9966 | 18.6762 | 98.95% | 3520.7296 | 99.53% | 99.48% | 84.99% |  |  | 99.51% | 1.0361
2021-03-13 | 190.7169 | 173.4774 | 173.4774 | 161.8619 | 148.9787 | 13.9667 | 13.9667 | 3416.2753 | 985.2581 | 342.6985 | 602.8484 | 17.3752 | 11.5835 | 16.2168 | 32.4337 | 9052.7178 | 390.7262 |  |  | 23.8259 | 1.0409 | 15.0113 | 4019.1236 | 2088.3187 | 1930.8049 | 945.5468 | 17.2395 | 11.6155 | 12.7317 | 13.7691 | 10.5563 | 7.3435 | 3382.1353 | 6889.4162 | 10787.3737 | 2297.2679 | 4726.7757 | 8549.0324 | 0.091462 | 0.084426 | 0.077312 | 17.3268 | 10.829 | 11.8132 | 12.4303 | 18.0251 | 53.1465 | 156.702 | 130.1501 | 98.8705 | 99.5% | 99.66% | 99.62% | 99.46% | 99.62% | 99.38% | 131.202 | 142.1359 | 155.2151 |  |  |  | 30 | 23 | 16 | 2340 | 1104 | 384 | 3828 | 135.0633 | 10 | 14 | 28 | 15 | 98.93% | 0.086947 | 0.088013 | 41.5868 | 39.9691 | 144.5143 | 18.7573 | 98.93% | 3625.0772 | 99.52% | 99.5% | 85% |  |  | 99.51% | 1.0409
2021-03-12 | 194.0967 | 176.3346 | 176.3346 | 164.3928 | 151.0892 | 13.9189 | 13.9189 | 3472.8353 | 1001.57 | 348.3722 | 613.9123 | 17.1727 | 11.4485 | 16.0278 | 32.0557 | 9016.7516 | 404.6694 |  |  | 23.6538 | 1.0471 | 14.8363 | 4086.7476 | 2122.893 | 1963.8546 | 962.2845 | 17.7621 | 11.9418 | 13.0604 | 13.9971 | 10.7311 | 7.4651 | 3377.6814 | 6876.5755 | 10760.5834 | 2294.5594 | 4719.4102 | 8530.6464 | 0.091667 | 0.084528 | 0.077139 | 17.4083 | 10.8503 | 11.799 | 12.5776 | 18.2457 | 53.8288 | 159.8812 | 132.9279 | 101.3291 | 99.5% | 99.66% | 99.62% | 99.45% | 99.61% | 99.37% | 130.9084 | 141.9644 | 155.5628 |  |  |  | 30 | 23 | 16 | 2340 | 1104 | 384 | 3828 | 137.2057 | 10 | 14 | 28 | 15 | 98.95% | 0.087058 | 0.088151 | 42.7643 | 40.0576 | 147.6824 | 18.9867 | 98.95% | 3619.453 | 99.53% | 99.49% | 84.98% |  |  | 99.5% | 1.0471
2021-03-11 | 190.5604 | 173.2783 | 173.2783 | 161.6011 | 148.7093 | 13.9181 | 13.9181 | 3420.6298 | 1016.6578 | 338.8859 | 602.8783 | 16.8663 | 8.877 | 17.754 | 39.9465 | 8817.7597 | 390.25 |  |  | 23.6062 | 1.0488 | 14.5935 | 4023.5081 | 2065.0861 | 1958.422 | 941.7642 | 17.2821 | 11.6771 | 12.7938 | 13.616 | 10.8928 | 7.2618 | 3263.2155 | 6766.7715 | 10548.0095 | 2231.7798 | 4596.5394 | 8379.4584 | 0.091021 | 0.087455 | 0.076513 | 17.2305 | 10.7525 | 11.9141 | 9.7697 | 21.0979 | 66.5385 | 156.8867 | 130.6277 | 99.5396 | 99.6% | 99.61% | 99.52% | 99.56% | 99.54% | 99.21% | 131.837 | 137.2134 | 156.8369 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 134.7745 | 10 | 20 | 45 | 19 | 98.94% | 0.087559 | 0.088524 | 41.7531 | 39.8971 | 144.8647 | 18.791 | 98.94% | 3543.6765 | 99.52% | 99.5% | 85.02% |  |  | 99.51% | 1.0488
2021-03-10 | 192.7053 | 175.1874 | 175.1874 | 163.3787 | 150.1519 | 14.0178 | 14.0178 | 3463.9645 | 1029.5374 | 343.1791 | 610.9888 | 17.4076 | 9.1619 | 18.3238 | 41.2285 | 9109.9252 | 400.1331 |  |  | 23.7838 | 1.0424 | 15.0618 | 4074.9533 | 2091.2479 | 1983.7054 | 954.1679 | 17.5179 | 11.8087 | 13.0209 | 13.7884 | 11.0308 | 7.3538 | 3352.0466 | 6949.0994 | 10829.1005 | 2292.7066 | 4721.1055 | 8604.0912 | 0.090676 | 0.087274 | 0.076708 | 17.1348 | 10.6651 | 11.888 | 9.8793 | 21.3387 | 67.3169 | 158.5108 | 131.7514 | 99.9332 | 99.6% | 99.61% | 99.52% | 99.57% | 99.55% | 99.22% | 132.3393 | 137.4975 | 156.4375 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 136.1609 | 10 | 20 | 45 | 19 | 98.94% | 0.087353 | 0.088281 | 42.3475 | 39.6879 | 146.1825 | 19.0053 | 98.94% | 3639.7364 | 99.52% | 99.51% | 85.01% |  |  | 99.5% | 1.0424
2021-03-09 | 191.3735 | 173.7861 | 173.7861 | 161.8503 | 148.6094 | 13.9755 | 13.9755 | 3471.6882 | 1031.833 | 343.9443 | 613.1384 | 17.4403 | 9.1791 | 18.3582 | 41.3059 | 8881.0287 | 398.5003 |  |  | 24.0323 | 1.0336 | 15.0901 | 4084.8267 | 2095.9108 | 1988.9158 | 957.0828 | 17.5875 | 11.9357 | 13.2036 | 13.8192 | 11.0554 | 7.3702 | 3285.2826 | 6807.361 | 10602.8275 | 2247.3761 | 4626.0781 | 8426.6106 | 0.090736 | 0.087355 | 0.076692 | 17.1388 | 10.7353 | 11.9966 | 10.0342 | 21.6811 | 68.4322 | 157.4133 | 130.8041 | 99.3278 | 99.59% | 99.6% | 99.51% | 99.55% | 99.53% | 99.19% | 132.2519 | 137.37 | 156.4706 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 134.6518 | 10 | 20 | 45 | 19 | 98.91% | 0.087407 | 0.08834 | 42.7268 | 39.8706 | 145.2372 | 19.31 | 98.91% | 3566.5429 | 99.51% | 99.49% | 84.99% |  |  | 99.49% | 1.0336
2021-03-08 | 188.9253 | 171.1743 | 171.1743 | 159.1464 | 145.969 | 13.8002 | 13.8002 | 3472.8424 | 1032.1761 | 344.0587 | 613.9502 | 16.6044 | 8.7392 | 17.4783 | 39.3262 | 8320.8426 | 393.64 |  |  | 24.1507 | 1.0294 | 14.3668 | 4086.7926 | 2096.6076 | 1990.1849 | 958.0089 | 17.7509 | 12.0279 | 13.2126 | 13.8238 | 11.059 | 7.3727 | 3094.4006 | 6409.5323 | 9979.4062 | 2117.0207 | 4356.6036 | 7932.759 | 0.091389 | 0.087796 | 0.076436 | 17.2843 | 10.8061 | 11.9848 | 10.1039 | 21.8375 | 68.9516 | 155.7082 | 129.6646 | 99.2904 | 99.59% | 99.6% | 99.5% | 99.52% | 99.5% | 99.13% | 131.3065 | 136.6803 | 156.994 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 132.137 | 10 | 20 | 45 | 19 | 98.9% | 0.087847 | 0.08884 | 42.9914 | 40.0752 | 144.1483 | 19.449 | 98.9% | 3358.8275 | 99.51% | 99.45% | 84.98% |  |  | 99.49% | 1.0294
2021-03-07 | 188.3729 | 170.9941 | 170.9941 | 159.2545 | 146.1975 | 13.916 | 13.916 | 3442.7698 | 1023.2381 | 341.0794 | 606.9662 | 16.9983 | 8.9465 | 17.893 | 40.2591 | 8604.8758 | 387.6372 |  |  | 24.0203 | 1.034 | 14.7077 | 4049.736 | 2078.4523 | 1971.2836 | 948.0455 | 17.3788 | 11.7396 | 12.9692 | 13.7041 | 10.9633 | 7.3088 | 3190.7263 | 6615.2073 | 10309.9422 | 2182.3689 | 4494.0592 | 8191.1069 | 0.091478 | 0.087993 | 0.077071 | 17.1584 | 10.7039 | 11.9568 | 9.9915 | 21.5802 | 68.0722 | 154.9004 | 128.8275 | 98.0558 | 99.59% | 99.6% | 99.51% | 99.54% | 99.52% | 99.17% | 131.1795 | 136.3742 | 155.6998 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 132.28 | 10 | 20 | 45 | 19 | 98.91% | 0.088058 | 0.089015 | 42.0875 | 39.819 | 143.0687 | 19.2203 | 98.91% | 3464.7277 | 99.51% | 99.48% | 85.01% |  |  | 99.5% | 1.034
2021-03-06 | 188.164 | 170.9994 | 170.9994 | 159.3817 | 146.6835 | 13.9522 | 13.9522 | 3420.3057 | 1016.5614 | 338.8538 | 604.3004 | 17.5829 | 9.2541 | 18.5083 | 41.6437 | 9024.0595 | 385.0409 |  |  | 24.1546 | 1.0293 | 15.2135 | 4024.6061 | 2064.8904 | 1959.7156 | 943.1542 | 17.1646 | 11.6177 | 12.7357 | 13.6147 | 10.8917 | 7.2612 | 3328.1703 | 6895.4288 | 10738.6024 | 2276.7749 | 4686.2305 | 8535.1132 | 0.090821 | 0.087649 | 0.077356 | 17.103 | 10.683 | 11.8277 | 9.7968 | 21.1698 | 66.8265 | 154.2919 | 127.8997 | 96.613 | 99.59% | 99.61% | 99.51% | 99.57% | 99.55% | 99.22% | 132.1281 | 136.909 | 155.1277 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 132.6898 | 10 | 20 | 45 | 19 | 98.92% | 0.087652 | 0.088544 | 41.518 | 39.6137 | 142.0743 | 18.8545 | 98.92% | 3612.919 | 99.51% | 99.51% | 84.98% |  |  | 99.51% | 1.0293
2021-03-05 | 191.4312 | 173.8816 | 173.8816 | 162.0321 | 148.8188 | 14.1016 | 14.1016 | 3471.0189 | 1031.6341 | 343.878 | 612.4994 | 17.6569 | 9.2931 | 18.5862 | 41.8191 | 9048.5425 | 398.5151 |  |  | 24.2046 | 1.0275 | 15.2775 | 4083.5184 | 2095.5068 | 1988.0116 | 956.3775 | 17.5496 | 11.8495 | 13.2038 | 13.8165 | 11.0532 | 7.3688 | 3333.7234 | 6909.7262 | 10765.603 | 2280.3341 | 4694.884 | 8554.5532 | 0.090308 | 0.087045 | 0.076664 | 17.1112 | 10.6665 | 12.0121 | 9.9513 | 21.4976 | 67.832 | 157.1996 | 130.4738 | 98.7602 | 99.59% | 99.6% | 99.51% | 99.56% | 99.54% | 99.21% | 132.8787 | 137.8597 | 156.5263 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 134.7319 | 10 | 20 | 45 | 19 | 98.92% | 0.087081 | 0.087986 | 42.6029 | 39.7898 | 144.8806 | 19.1466 | 98.92% | 3619.5657 | 99.51% | 99.5% | 85% |  |  | 99.5% | 1.0275
2021-03-04 | 189.249 | 172.2242 | 172.2242 | 160.7628 | 147.8742 | 14.0153 | 14.0153 | 3411.3605 | 1013.9028 | 337.9676 | 601.6275 | 18.1512 | 9.5533 | 19.1066 | 42.9898 | 9132.2597 | 386.2836 |  |  | 23.991 | 1.035 | 15.7053 | 4012.988 | 2059.4901 | 1953.4979 | 939.5951 | 17.0248 | 11.4614 | 12.5961 | 13.5791 | 10.8632 | 7.2422 | 3368.9939 | 6983.8064 | 10882.8486 | 2304.409 | 4744.8471 | 8646.9398 | 0.090531 | 0.087263 | 0.077052 | 17.0399 | 10.5927 | 11.769 | 10.022 | 21.6485 | 68.2975 | 155.2471 | 128.8496 | 97.2835 | 99.59% | 99.6% | 99.5% | 99.57% | 99.54% | 99.21% | 132.551 | 137.5157 | 155.7399 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 133.8261 | 10 | 20 | 45 | 19 | 98.9% | 0.087329 | 0.088224 | 41.0823 | 39.4016 | 142.9314 | 19.2809 | 98.9% | 3658.1027 | 99.5% | 99.5% | 85.01% |  |  | 99.5% | 1.035
2021-03-03 | 193.0978 | 175.5941 | 175.5941 | 163.687 | 150.553 | 14.0327 | 14.0327 | 3471.1732 | 1031.68 | 343.8933 | 613.7676 | 18.4744 | 9.7234 | 19.4467 | 43.7552 | 9402.7449 | 401.6234 |  |  | 23.8497 | 1.0401 | 15.9849 | 4084.9408 | 2095.5999 | 1989.3409 | 957.6609 | 17.5036 | 11.9071 | 13.0839 | 13.8171 | 11.0537 | 7.3691 | 3464.9926 | 7176.8499 | 11173.5154 | 2370.5727 | 4878.2695 | 8882.2177 | 0.090661 | 0.087549 | 0.077499 | 17.0548 | 10.7041 | 11.8741 | 10.1385 | 21.9128 | 69.1928 | 158.5091 | 131.3138 | 98.895 | 99.59% | 99.6% | 99.51% | 99.57% | 99.55% | 99.22% | 132.3618 | 137.0657 | 154.8404 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 136.5326 | 10 | 20 | 45 | 19 | 98.91% | 0.087559 | 0.088432 | 42.4947 | 39.633 | 145.7908 | 19.5161 | 98.91% | 3761.0109 | 99.51% | 99.51% | 84.97% |  |  | 99.49% | 1.0401
2021-03-02 | 191.3192 | 173.8526 | 173.8526 | 161.9589 | 148.6166 | 13.9242 | 13.9242 | 3471.9441 | 1031.9091 | 343.9697 | 613.1522 | 17.957 | 9.4511 | 18.9022 | 42.5299 | 8950.252 | 396.9836 |  |  | 24.0961 | 1.0313 | 15.5372 | 4085.0964 | 2096.0653 | 1989.031 | 957.1219 | 17.4666 | 11.8937 | 13.0707 | 13.8202 | 11.0562 | 7.3708 | 3319.9007 | 6878.8312 | 10713.8991 | 2271.1176 | 4674.7466 | 8514.9903 | 0.090579 | 0.087239 | 0.076783 | 17.0194 | 10.6966 | 11.8752 | 10.202 | 22.0447 | 69.5818 | 157.3533 | 130.7023 | 99.0012 | 99.58% | 99.6% | 99.5% | 99.55% | 99.53% | 99.18% | 132.4804 | 137.5527 | 156.2851 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 134.7017 | 10 | 20 | 45 | 19 | 98.89% | 0.087303 | 0.08822 | 42.431 | 39.5912 | 145.0804 | 19.6336 | 98.89% | 3604.0969 | 99.5% | 99.48% | 84.99% |  |  | 99.49% | 1.0313
2021-03-01 | 190.2171 | 172.6067 | 172.6067 | 160.5553 | 147.1987 | 13.8676 | 13.8676 | 3471.5395 | 1038.9889 | 335.4113 | 613.823 | 17.1828 | 9.0436 | 18.0871 | 40.696 | 8476.6709 | 394.8033 |  |  | 24.0416 | 1.0332 | 14.8084 | 4085.3625 | 2097.1394 | 1988.2231 | 949.2342 | 17.6104 | 12.0514 | 13.2003 | 13.8273 | 11.132 | 7.1874 | 3162.4292 | 6604.0837 | 10190.5157 | 2162.8421 | 4468.3694 | 8139.6344 | 0.09113 | 0.088164 | 0.074625 | 17.1618 | 10.8867 | 12.0761 | 10.2752 | 22.2613 | 68.0456 | 156.7753 | 130.4619 | 99.5147 | 99.58% | 99.6% | 99.5% | 99.52% | 99.5% | 99.16% | 131.6805 | 136.1103 | 160.8042 |  |  |  | 30.7812 | 24.7812 | 16 | 2400.9375 | 1189.5 | 384 | 3974.4375 | 133.3272 | 10 | 20 | 45 | 19 | 98.89% | 0.08754 | 0.088647 | 42.8622 | 40.1246 | 144.9736 | 19.7732 | 98.89% | 3430.3203 | 99.5% | 99.46% | 84.98% |  |  | 99.48% | 1.0332
2021-02-28 | 189.8736 | 172.4041 | 172.4041 | 160.4889 | 147.3607 | 13.9231 | 13.9231 | 3457.2059 | 1036.6434 | 331.7259 | 610.3681 | 17.3906 | 9.1529 | 18.3059 | 41.1882 | 8721.6039 | 393.5443 |  |  | 24.0442 | 1.0331 | 14.9713 | 4067.574 | 2088.8365 | 1978.7375 | 942.094 | 17.4696 | 11.9152 | 13.093 | 13.7725 | 11.1069 | 7.1084 | 3241.9389 | 6789.0987 | 10456.4868 | 2216.6567 | 4586.3457 | 8360.4299 | 0.091108 | 0.088485 | 0.07463 | 17.1399 | 10.8556 | 12.1008 | 10.1059 | 21.8995 | 66.3072 | 156.1782 | 129.6831 | 98.4055 | 99.59% | 99.6% | 99.51% | 99.54% | 99.52% | 99.21% | 131.7121 | 135.6158 | 160.7927 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 133.4084 | 10 | 20 | 45 | 19 | 98.9% | 0.087632 | 0.08874 | 42.4778 | 40.0962 | 144.1514 | 19.4384 | 98.9% | 3516.7156 | 99.51% | 99.48% | 84.99% |  |  | 99.49% | 1.0331
2021-02-27 | 190.6876 | 173.4004 | 173.4004 | 161.6494 | 148.579 | 14.084 | 14.084 | 3452.4637 | 1035.2215 | 331.2709 | 609.4843 | 18.5603 | 9.7686 | 19.5372 | 43.9587 | 9233.8075 | 396.8123 |  |  | 24.1014 | 1.0311 | 15.9783 | 4061.948 | 2085.9713 | 1975.9767 | 940.7552 | 17.2872 | 11.751 | 12.986 | 13.7537 | 11.0917 | 7.0987 | 3414.3093 | 7149.969 | 11012.2742 | 2334.5501 | 4830.1675 | 8804.8157 | 0.090713 | 0.088392 | 0.075285 | 16.9963 | 10.7286 | 12.0277 | 10.207 | 22.1189 | 66.9722 | 156.336 | 129.3877 | 97.2259 | 99.58% | 99.6% | 99.5% | 99.56% | 99.54% | 99.24% | 132.285 | 135.7582 | 159.3951 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 134.4189 | 10 | 20 | 45 | 19 | 98.89% | 0.087502 | 0.088537 | 42.0242 | 39.7526 | 143.7906 | 19.6331 | 98.89% | 3703.6963 | 99.5% | 99.5% | 85% |  |  | 99.49% | 1.0311
2021-02-26 | 191.3215 | 173.788 | 173.788 | 161.9311 | 148.9623 | 13.9961 | 13.9961 | 3472.1715 | 1041.1309 | 333.1619 | 613.1687 | 18.3986 | 9.6834 | 19.3669 | 43.5755 | 9737.6366 | 401.2623 |  |  | 24.2188 | 1.027 | 15.839 | 4085.3402 | 2097.8787 | 1987.4615 | 946.3306 | 17.5335 | 11.8569 | 12.9313 | 13.8322 | 11.155 | 7.1392 | 3475.1794 | 7277.1839 | 11207.5256 | 2376.1361 | 4916.204 | 8961.2208 | 0.090639 | 0.088547 | 0.075694 | 17.0902 | 10.731 | 11.8705 | 9.9576 | 21.5785 | 65.3392 | 156.7264 | 129.3792 | 96.8624 | 99.59% | 99.61% | 99.51% | 99.58% | 99.56% | 99.27% | 132.393 | 135.5218 | 158.533 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 135.0185 | 10 | 20 | 45 | 19 | 98.91% | 0.087578 | 0.088578 | 42.3217 | 39.6917 | 144.0433 | 19.1537 | 98.91% | 3769.6279 | 99.51% | 99.52% | 84.99% |  |  | 99.5% | 1.027
2021-02-25 | 188.2527 | 171.3496 | 171.3496 | 159.9194 | 147.0759 | 13.9396 | 13.9396 | 3418.2527 | 1004.6309 | 330.1911 | 602.827 | 18.2779 | 9.6199 | 19.2399 | 43.2897 | 10411.5314 | 388.0882 |  |  | 24.3643 | 1.0219 | 15.6996 | 4021.0797 | 2083.4307 | 1937.649 | 933.018 | 16.9031 | 11.4302 | 12.6709 | 13.7369 | 10.7639 | 7.0755 | 3544.6416 | 7340.6323 | 11337.662 | 2410.7091 | 4990.0494 | 9051.3708 | 0.09124 | 0.08672 | 0.076499 | 16.9511 | 10.6879 | 11.9012 | 9.6353 | 20.2783 | 63.3752 | 153.8561 | 126.8408 | 94.5176 | 99.6% | 99.61% | 99.52% | 99.6% | 99.59% | 99.3% | 131.5218 | 138.3761 | 156.865 |  |  |  | 29.4796 | 23.0995 | 15.1842 | 2299.4075 | 1108.775 | 364.42 | 3772.6026 | 133.1678 | 10 | 20 | 45 | 19 | 98.93% | 0.087435 | 0.088487 | 41.0042 | 39.5402 | 141.1174 | 18.441 | 98.93% | 3810.2464 | 99.52% | 99.55% | 85.01% |  |  | 99.52% | 1.0219
2021-02-24 | 191.0166 | 173.7199 | 173.7199 | 161.9831 | 148.897 | 14.0504 | 14.0504 | 3466.7581 | 1017.158 | 335.0638 | 611.9123 | 18.3305 | 9.6476 | 19.2953 | 43.4144 | 10496.0676 | 407.0707 |  |  | 24.296 | 1.0243 | 15.7419 | 4078.6705 | 2114.5363 | 1964.1341 | 946.9761 | 17.2967 | 11.7368 | 12.8144 | 13.942 | 10.8981 | 7.1799 | 3571.848 | 7387.686 | 11409.1766 | 2428.3215 | 5025.5711 | 9108.9607 | 0.091411 | 0.086688 | 0.076558 | 16.985 | 10.7467 | 11.7701 | 9.7589 | 20.4925 | 64.2377 | 156.2244 | 128.7697 | 96.0619 | 99.6% | 99.62% | 99.52% | 99.6% | 99.59% | 99.29% | 131.2751 | 138.4269 | 156.7433 |  |  |  | 29.36 | 22.95 | 15.12 | 2290.08 | 1101.6 | 362.88 | 3754.5601 | 134.8482 | 10 | 20 | 45 | 19 | 98.94% | 0.087523 | 0.08859 | 41.8478 | 39.5018 | 143.4045 | 18.6739 | 98.94% | 3836.0498 | 99.52% | 99.55% | 85% |  |  | 99.51% | 1.0243
2021-02-23 | 190.7212 | 173.221 | 173.221 | 161.2552 | 148.3132 | 13.9976 | 13.9976 | 3471.2732 | 1018.4827 | 335.5002 | 613.8135 | 17.6955 | 9.3134 | 18.6269 | 41.9105 | 10124.5176 | 406.8376 |  |  | 24.2005 | 1.0276 | 15.1966 | 4085.0867 | 2117.2902 | 1967.7965 | 949.3137 | 17.5002 | 11.9658 | 12.9724 | 13.9602 | 10.9123 | 7.1893 | 3466.0021 | 7164.5604 | 11057.6814 | 2356.7243 | 4875.3881 | 8831.2883 | 0.091822 | 0.086959 | 0.076291 | 17.142 | 10.9226 | 11.8668 | 9.7515 | 20.4853 | 64.2549 | 156.2365 | 128.9567 | 96.8398 | 99.6% | 99.62% | 99.53% | 99.59% | 99.58% | 99.27% | 130.6872 | 137.9965 | 157.2927 |  |  |  | 29.36 | 22.95 | 15.12 | 2290.08 | 1101.6 | 362.88 | 3754.5601 | 134.2345 | 10 | 20 | 45 | 19 | 98.94% | 0.087781 | 0.088894 | 42.4384 | 39.9314 | 143.7048 | 18.667 | 98.94% | 3721.478 | 99.52% | 99.53% | 84.97% |  |  | 99.51% | 1.0276
2021-02-22 | 189.7322 | 172.2556 | 172.2556 | 160.1724 | 147.015 | 13.9387 | 13.9387 | 3472.3424 | 1018.9003 | 335.6024 | 611.6567 | 16.6422 | 8.7451 | 17.472 | 39.2573 | 9533.001 | 402.4849 |  |  | 24.0755 | 1.032 | 14.2549 | 4083.9991 | 2117.8397 | 1966.1594 | 947.2591 | 17.4766 | 12.0832 | 13.1178 | 13.9638 | 10.9168 | 7.1915 | 3278.6223 | 6786.4135 | 10488.4272 | 2228.5853 | 4614.5627 | 8370.4941 | 0.092405 | 0.087142 | 0.075735 | 17.1305 | 11.0507 | 12.0485 | 9.7269 | 20.3967 | 63.792 | 155.956 | 129.2899 | 97.9988 | 99.61% | 99.62% | 99.53% | 99.56% | 99.56% | 99.24% | 129.8626 | 137.7065 | 158.4482 |  |  |  | 29.3563 | 22.9505 | 15.1187 | 2289.7875 | 1101.625 | 362.85 | 3754.2626 | 133.0777 | 9.9896 | 19.9583 | 44.8438 | 19.0104 | 98.95% | 0.088054 | 0.08925 | 42.6777 | 40.2297 | 143.9145 | 18.6336 | 98.95% | 3522.3265 | 99.53% | 99.51% | 85.02% |  |  | 99.51% | 1.032
2021-02-21 | 190.7242 | 173.2523 | 173.2523 | 161.2658 | 148.0286 | 13.928 | 13.928 | 3470.1348 | 1028.1881 | 335.2787 | 612.98 | 16.36 | 7.362 | 13.088 | 24.54 | 9687.6019 | 404.81 |  |  | 23.8896 | 1.0386 | 10.7183 | 4083.1148 | 2106.668 | 1976.4468 | 948.2587 | 17.4719 | 11.9865 | 13.2753 | 13.8901 | 11.0163 | 7.1845 | 3317.1652 | 6899.7453 | 10660.2433 | 2261.0159 | 4678.8285 | 8509.0437 | 0.092012 | 0.088013 | 0.075914 | 17.0859 | 10.8989 | 12.1659 | 8.0797 | 15.3034 | 39.4399 | 156.792 | 130.0024 | 98.2967 | 99.67% | 99.72% | 99.71% | 99.64% | 99.67% | 99.54% | 130.4181 | 136.3438 | 158.0738 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 134.0504 | 9 | 16 | 30 | 20 | 98.98% | 0.088156 | 0.089272 | 42.7337 | 40.1507 | 144.5658 | 18.1207 | 98.98% | 3581.079 | 99.54% | 99.64% | 84.99% |  |  | 99.53% | 1.0386
2021-02-20 | 191.8421 | 174.4215 | 174.4215 | 162.4688 | 149.3298 | 13.995 | 13.995 | 3472.2811 | 1028.824 | 335.4861 | 612.2045 | 17.1495 | 7.7173 | 13.7196 | 25.7242 | 10214.0903 | 406.906 |  |  | 23.8685 | 1.0394 | 11.2355 | 4084.4855 | 2107.971 | 1976.5146 | 947.6906 | 17.4206 | 11.9527 | 13.1074 | 13.8987 | 11.0231 | 7.189 | 3475.7651 | 7234.2025 | 11184.4257 | 2368.7228 | 4903.8931 | 8924.2636 | 0.091819 | 0.088133 | 0.076706 | 17.0297 | 10.8709 | 12.0275 | 8.0954 | 15.3262 | 39.4724 | 157.3317 | 129.9992 | 97.4116 | 99.67% | 99.72% | 99.71% | 99.66% | 99.69% | 99.56% | 130.6919 | 136.158 | 156.4406 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 135.3347 | 9 | 16 | 30 | 20 | 98.98% | 0.088221 | 0.089267 | 42.4807 | 39.9282 | 144.6438 | 18.148 | 98.98% | 3753.27 | 99.54% | 99.65% | 85.01% |  |  | 99.53% | 1.0394
2021-02-19 | 191.5855 | 174.1753 | 174.1753 | 162.4061 | 149.287 | 14.2418 | 14.2418 | 3470.9788 | 1028.4382 | 335.3603 | 612.5603 | 17.0503 | 7.6726 | 13.6402 | 25.5754 | 10213.8135 | 406.7518 |  |  | 23.865 | 1.0395 | 11.1705 | 4083.5391 | 2107.1803 | 1976.3588 | 947.9206 | 17.4102 | 11.7692 | 13.0622 | 13.8935 | 11.019 | 7.1863 | 3477.3646 | 7235.302 | 11182.4329 | 2369.9953 | 4905.4855 | 8924.2533 | 0.092091 | 0.088389 | 0.076924 | 17.0242 | 10.7037 | 11.9793 | 8.0422 | 15.2287 | 39.2342 | 156.827 | 129.5896 | 97.1113 | 99.68% | 99.72% | 99.71% | 99.66% | 99.69% | 99.56% | 130.3054 | 135.7633 | 155.9977 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 134.9016 | 9 | 16 | 30 | 20 | 98.99% | 0.08848 | 0.089529 | 42.2416 | 39.7072 | 144.1931 | 18.0324 | 98.99% | 3754.5133 | 99.55% | 99.65% | 85% |  |  | 99.53% | 1.0395
2021-02-18 | 192.1699 | 174.709 | 174.709 | 162.7831 | 149.4443 | 14.0713 | 14.0713 | 3468.8975 | 1027.8215 | 335.1592 | 613.9912 | 16.6768 | 7.5046 | 13.3414 | 25.0152 | 10163.9661 | 407.305 |  |  | 23.6966 | 1.0455 | 10.9259 | 4082.8887 | 2105.9168 | 1976.9719 | 949.1504 | 17.4609 | 11.9259 | 13.1894 | 13.8852 | 11.0124 | 7.182 | 3462.665 | 7197.8884 | 11113.3421 | 2360.5391 | 4882.7135 | 8873.934 | 0.092113 | 0.088344 | 0.07678 | 17.074 | 10.8359 | 12.0651 | 7.9385 | 15.0422 | 38.7925 | 157.603 | 130.3279 | 97.7978 | 99.68% | 99.73% | 99.72% | 99.66% | 99.69% | 99.56% | 130.2748 | 135.8324 | 156.2902 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 135.4162 | 9 | 16 | 30 | 20 | 99.01% | 0.088454 | 0.089515 | 42.5762 | 39.975 | 144.97 | 17.8112 | 99.01% | 3737.1636 | 99.55% | 99.66% | 84.96% |  |  | 99.53% | 1.0455
2021-02-17 | 190.8214 | 173.4481 | 173.4481 | 161.6165 | 148.5491 | 14.2269 | 14.2269 | 3470.3925 | 1029.1517 | 337.676 | 612.268 | 17.503 | 8.3274 | 14.8043 | 27.758 | 10313.2781 | 403.4208 |  |  | 23.9261 | 1.0373 | 12.1388 | 4082.6605 | 2103.5648 | 1979.0957 | 949.944 | 17.3732 | 11.8316 | 13.0259 | 13.8697 | 11.0266 | 7.2359 | 3494.3816 | 7264.0909 | 11255.0487 | 2383.9658 | 4927.5186 | 8970.1627 | 0.09221 | 0.088847 | 0.078071 | 16.9803 | 10.7342 | 11.9262 | 8.6443 | 16.4314 | 42.5677 | 156.0296 | 128.7418 | 96.1439 | 99.65% | 99.7% | 99.69% | 99.64% | 99.67% | 99.53% | 130.1382 | 135.0642 | 153.7063 |  |  |  | 29.2708 | 23.2708 | 15.2708 | 2283.125 | 1117 | 366.5 | 3766.625 | 134.2652 | 9 | 16 | 30 | 18.9167 | 98.97% | 0.088871 | 0.089837 | 42.2308 | 39.6407 | 143.2935 | 18.3491 | 98.97% | 3779.1112 | 99.54% | 99.63% | 85% |  |  | 99.52% | 1.0373
2021-02-16 | 188.9952 | 171.5879 | 171.5879 | 159.706 | 146.3286 | 14.0885 | 14.0885 | 3470.72 | 1031.5453 | 343.8484 | 612.7582 | 16.8958 | 9.5039 | 16.8958 | 31.6796 | 9768.8701 | 399.0691 |  |  | 24.037 | 1.0334 | 13.8978 | 4083.4782 | 2095.3263 | 1988.1519 | 956.6066 | 17.4073 | 11.8819 | 13.1294 | 13.8153 | 11.0523 | 7.3682 | 3317.6235 | 6876.9235 | 10718.1225 | 2269.5257 | 4672.38 | 8515.2769 | 0.092166 | 0.089035 | 0.078896 | 16.9721 | 10.6936 | 11.9389 | 10.2834 | 19.7477 | 51.915 | 154.9029 | 128.281 | 96.5108 | 99.58% | 99.64% | 99.63% | 99.55% | 99.58% | 99.39% | 130.1997 | 134.7792 | 152.0994 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 132.277 | 9 | 16 | 30 | 16 | 98.96% | 0.089041 | 0.089921 | 42.4186 | 39.6046 | 142.6088 | 18.5125 | 98.96% | 3602.4609 | 99.53% | 99.53% | 84.99% |  |  | 99.52% | 1.0334
2021-02-15 | 187.9258 | 170.4886 | 170.4886 | 158.5297 | 145.2241 | 14.0268 | 14.0268 | 3467.2898 | 1030.5258 | 343.5086 | 611.2833 | 16.35 | 9.1969 | 16.35 | 30.6562 | 9400.7396 | 395.4733 |  |  | 23.6588 | 1.0469 | 13.4489 | 4078.5731 | 2093.2555 | 1985.3177 | 954.7919 | 17.4372 | 11.9588 | 13.3212 | 13.8017 | 11.0413 | 7.3609 | 3208.8074 | 6654.4898 | 10376.7305 | 2194.8144 | 4520.0624 | 8241.795 | 0.09367 | 0.09033 | 0.079612 | 17.0338 | 10.7884 | 12.1514 | 10.4138 | 19.9917 | 52.5301 | 154.2523 | 127.9638 | 96.7944 | 99.58% | 99.64% | 99.63% | 99.53% | 99.56% | 99.36% | 128.1097 | 132.8457 | 150.7308 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 131.1796 | 9 | 16 | 30 | 16 | 98.96% | 0.090352 | 0.091285 | 42.7172 | 39.9736 | 142.2337 | 18.7414 | 98.96% | 3484.9914 | 99.53% | 99.51% | 85.01% |  |  | 99.51% | 1.0469
2021-02-14 | 187.7729 | 170.4675 | 170.4675 | 158.6207 | 145.3475 | 13.9906 | 13.9906 | 3459.8531 | 1028.3155 | 342.7718 | 611.0383 | 16.3508 | 9.1973 | 16.3508 | 30.6578 | 9637.2016 | 393.291 |  |  | 23.8969 | 1.0384 | 13.4496 | 4070.8914 | 2088.7658 | 1982.1256 | 953.8101 | 17.3053 | 11.8468 | 13.0643 | 13.7721 | 11.0177 | 7.3451 | 3284.1682 | 6807.246 | 10608.6831 | 2246.6191 | 4625.1647 | 8428.6894 | 0.092895 | 0.089722 | 0.079445 | 16.9505 | 10.7101 | 11.9312 | 10.0699 | 19.3379 | 50.8409 | 153.9425 | 127.5094 | 96.0033 | 99.59% | 99.65% | 99.64% | 99.55% | 99.58% | 99.4% | 129.1777 | 133.7462 | 151.0485 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 131.341 | 9 | 16 | 30 | 16 | 98.98% | 0.089728 | 0.09062 | 42.2165 | 39.5919 | 141.7561 | 18.1286 | 98.98% | 3566.0204 | 99.54% | 99.54% | 84.99% |  |  | 99.53% | 1.0384
2021-02-13 | 188.6365 | 171.4068 | 171.4068 | 159.6248 | 146.4795 | 14.0733 | 14.0733 | 3454.7104 | 1026.787 | 342.2623 | 609.6546 | 17.1577 | 9.6512 | 17.1577 | 32.1707 | 10145.2932 | 395.2511 |  |  | 23.8427 | 1.0403 | 14.1133 | 4064.365 | 2085.6611 | 1978.7039 | 951.9169 | 17.2298 | 11.7819 | 13.0165 | 13.7516 | 11.0013 | 7.3342 | 3428.1374 | 7107.3973 | 11079.4559 | 2344.9645 | 4828.4394 | 8801.4405 | 0.092731 | 0.089842 | 0.080201 | 16.9182 | 10.6805 | 11.9249 | 10.1273 | 19.4451 | 51.1092 | 154.2718 | 127.3861 | 95.1325 | 99.59% | 99.64% | 99.63% | 99.57% | 99.6% | 99.42% | 129.4063 | 133.5676 | 149.6233 |  |  |  | 30 | 24 | 16 | 2340 | 1152 | 384 | 3876 | 132.4275 | 9 | 16 | 30 | 16 | 98.97% | 0.089802 | 0.090631 | 42.0282 | 39.5236 | 141.6401 | 18.229 | 98.97% | 3722.738 | 99.54% | 99.55% | 85% |  |  | 99.52% | 1.0403
2021-02-12 | 189.1039 | 171.7056 | 171.7056 | 159.8005 | 146.8342 | 13.913 | 13.913 | 3471.0465 | 1044.3237 | 342.975 | 613.3374 | 17.0561 | 7.9755 | 15.9991 | 36.8028 | 10237.395 | 397.9437 |  |  | 24.0116 | 1.0343 | 13.238 | 4084.3839 | 2083.7478 | 2000.6361 | 956.3123 | 17.3983 | 11.9051 | 13.1265 | 13.739 | 11.1892 | 7.3495 | 3450.7941 | 7201.7004 | 11208.2725 | 2367.7985 | 4874.4564 | 8911.525 | 0.091861 | 0.090734 | 0.07999 | 16.9073 | 10.6484 | 11.9329 | 8.2329 | 18.1622 | 57.5323 | 154.6927 | 127.5478 | 95.0308 | 99.66% | 99.67% | 99.59% | 99.65% | 99.63% | 99.35% | 130.6321 | 132.2543 | 150.0181 |  |  |  | 28.625 | 23.3125 | 15.3125 | 2232.75 | 1119 | 367.5 | 3719.25 | 132.832 | 10.375 | 20.8125 | 47.875 | 22.1875 | 98.99% | 0.089601 | 0.090349 | 42.4299 | 39.4886 | 141.9024 | 17.8817 | 98.99% | 3768.5566 | 99.55% | 99.6% | 84.98% |  |  | 99.53% | 1.0343
2021-02-11 | 189.1095 | 171.7815 | 171.7815 | 160.0588 | 146.7806 | 13.9835 | 13.9835 | 3466.6153 | 1049.1073 | 342.1002 | 611.4572 | 17.3086 | 7.6158 | 15.9239 | 38.7713 | 9943.7829 | 397.2592 |  |  | 23.9812 | 1.0354 | 13.2046 | 4078.0725 | 2075.4078 | 2002.6647 | 953.5574 | 17.328 | 11.7227 | 13.1948 | 13.684 | 11.2404 | 7.3307 | 3465.825 | 7261.4184 | 11302.3697 | 2381.3431 | 4904.1041 | 8985.847 | 0.091648 | 0.091282 | 0.080148 | 16.8568 | 10.489 | 12.0484 | 7.7937 | 18.0687 | 60.0175 | 154.5934 | 127.4958 | 94.7008 | 99.68% | 99.68% | 99.57% | 99.67% | 99.63% | 99.33% | 130.9364 | 131.4605 | 149.7235 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 132.8635 | 11 | 23 | 56 | 25 | 98.99% | 0.089691 | 0.090402 | 42.2455 | 39.3942 | 141.7172 | 18.0083 | 98.99% | 3796.5705 | 99.54% | 99.61% | 85.01% |  |  | 99.53% | 1.0354
2021-02-10 | 189.4859 | 172.138 | 172.138 | 160.2951 | 147.191 | 14.017 | 14.017 | 3467.4511 | 1049.3602 | 342.1827 | 612.7836 | 17.4506 | 7.6783 | 16.0545 | 39.0893 | 9658.3618 | 398.2 |  |  | 24.0333 | 1.0335 | 13.313 | 4080.2348 | 2075.9082 | 2004.3265 | 954.9663 | 17.3478 | 11.8429 | 13.0897 | 13.6873 | 11.2431 | 7.3325 | 3505.1441 | 7339.1136 | 11415.4985 | 2408.7504 | 4958.3514 | 9079.1184 | 0.09139 | 0.091147 | 0.080172 | 16.8602 | 10.5801 | 11.9212 | 7.7562 | 17.9898 | 59.7958 | 154.7896 | 127.4882 | 94.526 | 99.68% | 99.68% | 99.57% | 99.68% | 99.64% | 99.34% | 131.3052 | 131.6558 | 149.678 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 133.201 | 11 | 23 | 56 | 25 | 98.99% | 0.089517 | 0.090209 | 42.2805 | 39.3615 | 141.7987 | 17.9295 | 98.99% | 3838.6002 | 99.55% | 99.61% | 84.98% |  |  | 99.53% | 1.0335
2021-02-09 | 189.1135 | 171.8316 | 171.8316 | 159.9906 | 147.0151 | 14.0295 | 14.0295 | 3454.8307 | 1045.5409 | 340.9372 | 609.4295 | 17.53 | 7.7132 | 16.1276 | 39.2672 | 9519.5012 | 395.0052 |  |  | 23.8388 | 1.0404 | 13.3735 | 4064.2602 | 2068.3526 | 1995.9076 | 950.3667 | 17.2819 | 11.8411 | 12.9828 | 13.6375 | 11.2022 | 7.3058 | 3463.2983 | 7255.6847 | 11292.8139 | 2379.665 | 4900.3985 | 8978.5191 | 0.091789 | 0.091442 | 0.080201 | 16.8976 | 10.6486 | 11.9144 | 7.9106 | 18.3406 | 60.9244 | 154.5833 | 127.4603 | 94.7771 | 99.68% | 99.67% | 99.56% | 99.67% | 99.63% | 99.32% | 130.7352 | 131.2305 | 149.6235 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 133.0007 | 11 | 23 | 56 | 25 | 98.97% | 0.089824 | 0.09054 | 42.1057 | 39.4606 | 141.7263 | 18.2792 | 98.97% | 3793.7213 | 99.54% | 99.6% | 85.01% |  |  | 99.52% | 1.0404
2021-02-08 | 187.2004 | 169.9134 | 169.9134 | 158.0518 | 144.7873 | 13.9717 | 13.9717 | 3457.9452 | 1046.4834 | 341.2446 | 609.6952 | 16.4931 | 7.2569 | 15.1736 | 36.9445 | 8919.4312 | 391.7873 |  |  | 23.6631 | 1.0467 | 12.5825 | 4067.6403 | 2070.2172 | 1997.4232 | 950.9398 | 17.287 | 11.8616 | 13.0202 | 13.6498 | 11.2123 | 7.3124 | 3268.9991 | 6849.7456 | 10662.8502 | 2246.0606 | 4625.8072 | 8476.8704 | 0.093145 | 0.092442 | 0.080359 | 16.8822 | 10.6558 | 11.939 | 7.9402 | 18.4072 | 61.1349 | 153.3911 | 126.9577 | 95.2482 | 99.68% | 99.67% | 99.56% | 99.65% | 99.6% | 99.28% | 128.8312 | 129.8106 | 149.3291 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 130.7527 | 11 | 23 | 56 | 25 | 98.97% | 0.090875 | 0.091671 | 42.1688 | 39.477 | 141.1348 | 18.3456 | 98.97% | 3581.1296 | 99.54% | 99.57% | 85.01% |  |  | 99.52% | 1.0467
2021-02-07 | 187.4354 | 170.0596 | 170.0596 | 158.1495 | 145.189 | 14.0686 | 14.0686 | 3457.7239 | 1046.4164 | 341.2228 | 610.2886 | 16.6351 | 7.3194 | 15.3043 | 37.2625 | 9249.8673 | 392.5798 |  |  | 23.8246 | 1.0409 | 12.6908 | 4068.0125 | 2070.0847 | 1997.9278 | 951.5114 | 17.3758 | 11.9102 | 12.9945 | 13.6489 | 11.2116 | 7.3119 | 3369.7587 | 7058.7911 | 10984.6473 | 2315.4339 | 4767.77 | 8734.2405 | 0.092778 | 0.092424 | 0.080872 | 16.9652 | 10.6936 | 11.9022 | 7.7252 | 17.9122 | 59.5099 | 153.1383 | 126.2736 | 94.1157 | 99.68% | 99.68% | 99.57% | 99.67% | 99.62% | 99.32% | 129.3416 | 129.8366 | 148.3826 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 131.0998 | 11 | 23 | 56 | 25 | 99% | 0.09076 | 0.091496 | 42.2805 | 39.561 | 140.5852 | 17.8523 | 99% | 3691.0231 | 99.55% | 99.6% | 85% |  |  | 99.53% | 1.0409
2021-02-06 | 188.8369 | 171.4162 | 171.4162 | 159.5912 | 146.519 | 13.9097 | 13.9097 | 3470.2345 | 1050.2026 | 342.4574 | 612.3844 | 17.1447 | 7.5437 | 15.7732 | 38.4042 | 9675.9887 | 396.2576 |  |  | 23.9663 | 1.0359 | 13.0796 | 4082.6189 | 2077.5746 | 2005.0443 | 954.8418 | 17.4207 | 11.825 | 13.0519 | 13.6983 | 11.2522 | 7.3384 | 3506.2999 | 7345.4283 | 11431.6593 | 2409.1874 | 4961.1412 | 9089.2654 | 0.092019 | 0.091877 | 0.080965 | 16.9181 | 10.561 | 11.8927 | 7.6425 | 17.7194 | 58.8643 | 154.2087 | 126.8672 | 93.8911 | 99.69% | 99.68% | 99.58% | 99.68% | 99.64% | 99.35% | 130.4077 | 130.6092 | 148.2128 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 132.6231 | 11 | 23 | 56 | 25 | 99.01% | 0.090205 | 0.090885 | 42.2976 | 39.3717 | 141.2412 | 17.6602 | 99.01% | 3840.7075 | 99.55% | 99.62% | 85% |  |  | 99.54% | 1.0359
2021-02-05 | 188.5765 | 171.1008 | 171.1008 | 159.2606 | 146.2037 | 13.9108 | 13.9108 | 3470.4195 | 1050.2585 | 342.4756 | 614.431 | 17.2 | 7.568 | 15.824 | 38.5281 | 9638.8343 | 396.5156 |  |  | 23.9228 | 1.0374 | 13.1218 | 4084.8505 | 2077.6854 | 2007.1652 | 956.9066 | 17.4756 | 11.8403 | 13.0019 | 13.699 | 11.2528 | 7.3388 | 3490.8246 | 7304.8321 | 11354.9727 | 2399.2585 | 4936.8198 | 9034.0543 | 0.092304 | 0.092166 | 0.081131 | 16.9532 | 10.5522 | 11.8007 | 7.7108 | 17.8917 | 59.5067 | 153.9694 | 126.6649 | 93.8437 | 99.68% | 99.68% | 99.57% | 99.68% | 99.64% | 99.34% | 130.0047 | 130.2001 | 147.9096 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 132.2703 | 11 | 23 | 56 | 25 | 99% | 0.090472 | 0.09116 | 42.3178 | 39.3061 | 141.087 | 17.8316 | 99% | 3821.9543 | 99.55% | 99.61% | 84.96% |  |  | 99.53% | 1.0374
2021-02-04 | 188.6735 | 171.3453 | 171.3453 | 159.6235 | 146.5814 | 14.129 | 14.129 | 3469.6537 | 1050.0268 | 342.4 | 613.56 | 19.4686 | 8.5662 | 17.9111 | 43.6097 | 9636.6407 | 395.6751 |  |  | 23.957 | 1.0362 | 14.8525 | 4083.2138 | 2077.2269 | 2005.9869 | 955.9601 | 17.3281 | 11.7219 | 13.0694 | 13.696 | 11.2503 | 7.3371 | 3515.5679 | 7357.3951 | 11438.8873 | 2416.3887 | 4972.0456 | 9099.8742 | 0.092253 | 0.092096 | 0.081149 | 16.8218 | 10.4579 | 11.8825 | 8.6539 | 20.08 | 66.775 | 153.8413 | 126.5847 | 93.6921 | 99.65% | 99.64% | 99.52% | 99.64% | 99.6% | 99.27% | 130.0775 | 130.2989 | 147.8765 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 132.3416 | 11 | 23 | 56 | 25 | 98.88% | 0.090426 | 0.091109 | 42.1193 | 39.1622 | 140.842 | 20.0118 | 98.88% | 3849.3657 | 99.49% | 99.57% | 84.97% |  |  | 99.48% | 1.0362
2021-02-03 | 188.704 | 171.3344 | 171.3344 | 159.6398 | 146.5919 | 13.9867 | 13.9867 | 3470.4563 | 1050.2697 | 342.4792 | 613.8586 | 21.4457 | 9.4361 | 19.7301 | 48.0385 | 9630.419 | 394.5068 |  |  | 23.8669 | 1.0394 | 16.3608 | 4084.3149 | 2077.7074 | 2006.6075 | 956.3378 | 17.3696 | 11.6946 | 12.9652 | 13.6992 | 11.2529 | 7.3388 | 3538.373 | 7402.6182 | 11505.8286 | 2432.4401 | 5003.5559 | 9154.5657 | 0.092513 | 0.092404 | 0.081502 | 16.855 | 10.4283 | 11.7802 | 9.5013 | 22.053 | 73.3599 | 153.9174 | 126.5812 | 93.5965 | 99.61% | 99.61% | 99.48% | 99.61% | 99.56% | 99.2% | 129.7109 | 129.8638 | 147.2363 |  |  |  | 28 | 23 | 15 | 2184 | 1104 | 360 | 3648 | 132.6137 | 11 | 23 | 56 | 25 | 98.77% | 0.090717 | 0.091394 | 42.0295 | 39.0635 | 140.8823 | 21.9773 | 98.77% | 3873.9086 | 99.45% | 99.53% | 84.97% |  |  | 99.42% | 1.0394
2021-02-02 | 187.8277 | 170.5133 | 170.5133 | 158.7557 | 145.634 | 13.9383 | 13.9383 | 3470.5599 | 1035.0854 | 337.5279 | 612.2967 | 21.1927 | 9.3248 | 19.4973 | 47.4716 | 9401.4245 | 393.0527 |  |  | 24.0081 | 1.0344 | 16.0687 | 4082.8567 | 2097.9466 | 1984.9101 | 949.8246 | 17.3144 | 11.7576 | 13.1535 | 13.8326 | 11.0902 | 7.2327 | 3499.1354 | 7291.1226 | 11284.1766 | 2391.4445 | 4939.331 | 8998.8281 | 0.093325 | 0.090977 | 0.080019 | 16.8976 | 10.636 | 12.044 | 9.5967 | 21.6521 | 72.3322 | 153.3216 | 126.097 | 93.4998 | 99.61% | 99.61% | 99.47% | 99.6% | 99.56% | 99.2% | 128.5823 | 131.9009 | 149.965 |  |  |  | 28.6875 | 23 | 15 | 2237.625 | 1104 | 360 | 3701.625 | 131.7378 | 11 | 23 | 56 | 25 | 98.76% | 0.090445 | 0.091331 | 42.2254 | 39.5777 | 140.4865 | 22.0694 | 98.76% | 3793.9434 | 99.44% | 99.52% | 85% |  |  | 99.42% | 1.0344
2021-02-01 | 186.7938 | 169.4761 | 169.4761 | 157.6372 | 144.1496 | 14.0113 | 14.0113 | 3469.851 | 1028.104 | 335.2513 | 613.6953 | 20.0636 | 8.828 | 18.4585 | 44.9424 | 8791.518 | 390.9247 |  |  | 23.8141 | 1.0413 | 15.1708 | 4083.5464 | 2106.4957 | 1977.0507 | 948.9466 | 17.3177 | 11.8389 | 13.2395 | 13.889 | 11.0154 | 7.184 | 3325.7801 | 6908.9852 | 10658.6948 | 2267.727 | 4688.3918 | 8514.5766 | 0.094634 | 0.090895 | 0.079134 | 16.9309 | 10.7576 | 12.1168 | 9.6842 | 21.593 | 72.3642 | 152.8292 | 126.1957 | 94.5339 | 99.61% | 99.61% | 99.47% | 99.57% | 99.54% | 99.15% | 126.8037 | 132.0202 | 151.6422 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 130.1603 | 11 | 23 | 56 | 25 | 98.76% | 0.090958 | 0.092029 | 42.3962 | 39.8052 | 140.5743 | 22.2324 | 98.76% | 3588.5213 | 99.44% | 99.49% | 84.97% |  |  | 99.42% | 1.0413
2021-01-31 | 187.6671 | 170.2857 | 170.2857 | 158.4697 | 145.0305 | 14.0015 | 14.0015 | 3467.8165 | 1027.5012 | 335.0547 | 612.7928 | 19.671 | 8.6552 | 18.0973 | 44.063 | 8895.4579 | 392.9805 |  |  | 23.5625 | 1.0503 | 14.8739 | 4080.6093 | 2105.2606 | 1975.3487 | 947.8475 | 17.3815 | 11.816 | 13.2335 | 13.8808 | 11.0089 | 7.1797 | 3356.7175 | 6975.9031 | 10766.0029 | 2288.5382 | 4732.7946 | 8598.5547 | 0.094935 | 0.091191 | 0.079401 | 17.0127 | 10.7522 | 12.1346 | 9.4843 | 21.1412 | 70.8226 | 153.5755 | 126.8027 | 94.9761 | 99.62% | 99.62% | 99.49% | 99.59% | 99.55% | 99.18% | 126.4021 | 131.5925 | 151.131 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 131.0283 | 11 | 23 | 56 | 25 | 98.79% | 0.091251 | 0.092325 | 42.4309 | 39.8995 | 141.2468 | 21.7677 | 98.79% | 3622.4257 | 99.46% | 99.51% | 84.98% |  |  | 99.43% | 1.0503
2021-01-30 | 189.3684 | 171.9085 | 171.9085 | 159.9677 | 146.5995 | 13.9398 | 13.9398 | 3468.8697 | 1027.8132 | 335.1565 | 614.0367 | 19.8652 | 8.7407 | 18.2759 | 44.498 | 9114.4448 | 396.3651 |  |  | 23.2495 | 1.0617 | 15.0208 | 4082.9064 | 2105.9 | 1977.0064 | 949.1932 | 17.4598 | 11.9408 | 13.2113 | 13.8851 | 11.0123 | 7.1819 | 3425.0554 | 7114.0126 | 10972.7295 | 2335.4516 | 4827.9812 | 8766.4103 | 0.095069 | 0.091379 | 0.079649 | 17.0727 | 10.849 | 12.0841 | 9.49 | 21.1618 | 70.9328 | 155.0651 | 127.9498 | 95.7342 | 99.63% | 99.62% | 99.49% | 99.59% | 99.56% | 99.19% | 126.2238 | 131.3219 | 150.6611 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 132.6977 | 11 | 23 | 56 | 25 | 98.81% | 0.091421 | 0.092486 | 42.6119 | 40.0059 | 142.5264 | 21.7887 | 98.81% | 3695.3275 | 99.46% | 99.52% | 84.96% |  |  | 99.43% | 1.0617
2021-01-29 | 188.1037 | 170.7083 | 170.7083 | 158.9242 | 145.4646 | 13.8707 | 13.8707 | 3461.189 | 1025.5375 | 334.4144 | 611.0934 | 18.7847 | 8.2653 | 17.2819 | 42.0777 | 8902.9257 | 390.9453 |  |  | 23.1513 | 1.0653 | 14.2038 | 4072.2824 | 2101.2371 | 1971.0453 | 945.5078 | 17.3954 | 11.7842 | 13.157 | 13.8543 | 10.9879 | 7.166 | 3359.86 | 6985.3606 | 10784.9984 | 2290.3429 | 4738.0981 | 8611.842 | 0.095761 | 0.091922 | 0.079958 | 17.0797 | 10.7599 | 12.1114 | 9.1612 | 20.4142 | 68.3581 | 154.1249 | 127.3414 | 95.4748 | 99.64% | 99.64% | 99.51% | 99.6% | 99.57% | 99.21% | 125.3126 | 130.5455 | 150.0782 |  |  |  | 29 | 23 | 15 | 2262 | 1104 | 360 | 3726 | 131.6874 | 11 | 23 | 56 | 25 | 98.85% | 0.092004 | 0.093096 | 42.3365 | 39.951 | 141.8174 | 21.0198 | 98.85% | 3626.3766 | 99.48% | 99.53% | 84.99% |  |  | 99.45% | 1.0653
2021-01-28 | 187.6202 | 170.4103 | 170.4103 | 158.7499 | 145.3886 | 13.861 | 13.861 | 3464.3184 | 1007.4132 | 314.2012 | 612.5186 | 20.8281 | 9.1644 | 19.1618 | 46.6549 | 9336.1482 | 390.5779 |  |  | 23.6526 | 1.0471 | 15.4719 | 4076.837 | 2142.704 | 1934.1329 | 926.7198 | 17.2099 | 11.6605 | 13.0105 | 14.1277 | 10.7937 | 6.7329 | 3616.3742 | 7526.8109 | 11363.8761 | 2437.9414 | 5102.2624 | 9183.3669 | 0.096681 | 0.090198 | 0.076196 | 17.0343 | 10.9594 | 12.1798 | 9.5649 | 20.295 | 65.6399 | 153.0104 | 125.3036 | 92.5247 | 99.62% | 99.62% | 99.49% | 99.61% | 99.6% | 99.29% | 124.1196 | 133.0406 | 157.4882 |  |  |  | 30.9666 | 23.6588 | 14.7578 | 2415.3919 | 1135.62 | 354.1875 | 3905.1994 | 131.5229 | 11 | 23 | 56 | 25 | 98.79% | 0.091329 | 0.092938 | 41.8809 | 40.1734 | 140.2622 | 21.741 | 98.79% | 3824.5035 | 99.46% | 99.55% | 84.98% |  |  | 99.43% | 1.0471
2021-01-27 | 188.1967 | 170.8508 | 170.8508 | 159.1119 | 145.8667 | 14.0131 | 14.0131 | 3469.446 | 1039.0096 | 332.1315 | 612.5554 | 20.8114 | 10.3469 | 19.8316 | 43.6608 | 9346.6123 | 393.2095 |  |  | 23.5933 | 1.0492 | 16.3765 | 4082.0014 | 2098.305 | 1983.6964 | 944.6869 | 17.3459 | 11.7389 | 13.0875 | 13.835 | 11.1322 | 7.1171 | 3535.4069 | 7401.9966 | 11391.7332 | 2416.0665 | 5001.0181 | 9111.9415 | 0.094579 | 0.092656 | 0.08018 | 16.937 | 10.6537 | 12.04 | 10.6928 | 22.1468 | 65.5753 | 153.4821 | 126.0623 | 93.1348 | 99.57% | 99.6% | 99.52% | 99.56% | 99.56% | 99.28% | 126.8778 | 129.5117 | 149.6632 |  |  |  | 31.0013 | 24.945 | 15.9479 | 2418.0975 | 1197.36 | 382.75 | 3998.2075 | 131.8466 | 11 | 21.0833 | 46.4167 | 22.125 | 98.79% | 0.09166 | 0.092625 | 42.1723 | 39.6307 | 140.5652 | 21.762 | 98.79% | 3831.1916 | 99.46% | 99.51% | 84.99% |  |  | 99.43% | 1.0492
2021-01-26 | 188.7243 | 171.1926 | 171.1926 | 159.2953 | 146.0691 | 14.1176 | 14.1176 | 3473.3647 | 1041.4887 | 333.2764 | 612.4851 | 20.3339 | 10.1669 | 19.4096 | 42.5163 | 9095.8441 | 394.7884 |  |  | 23.2398 | 1.0621 | 16.0424 | 4085.8498 | 2098.5997 | 1987.2502 | 945.7615 | 17.5318 | 11.8973 | 13.27 | 13.8369 | 11.1588 | 7.1416 | 3450.1212 | 7228.0791 | 11138.0163 | 2358.9223 | 4881.7538 | 8903.0219 | 0.095367 | 0.093455 | 0.080466 | 17.0872 | 10.7718 | 12.1961 | 10.8945 | 22.5302 | 66.3818 | 154.0971 | 126.8146 | 94.262 | 99.57% | 99.6% | 99.52% | 99.54% | 99.54% | 99.25% | 125.83 | 128.4047 | 149.1312 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 131.9525 | 11 | 21 | 46 | 22 | 98.79% | 0.092371 | 0.093364 | 42.699 | 40.0552 | 141.3855 | 22.0528 | 98.79% | 3743.3131 | 99.46% | 99.49% | 85.01% |  |  | 99.42% | 1.0621
2021-01-25 | 187.0243 | 169.5146 | 169.5146 | 157.4848 | 144.0691 | 14.1644 | 14.1644 | 3471.0129 | 1040.7835 | 333.0507 | 612.6108 | 19.4448 | 9.7224 | 18.561 | 40.6574 | 8562.8192 | 391.5418 |  |  | 23.0818 | 1.0679 | 15.3409 | 4083.6237 | 2097.1787 | 1986.445 | 945.6616 | 17.5097 | 12.0298 | 13.2968 | 13.8276 | 11.1513 | 7.1368 | 3252.3334 | 6811.3835 | 10492.342 | 2223.9189 | 4601.204 | 8388.4411 | 0.096487 | 0.094192 | 0.080329 | 17.0785 | 10.8969 | 12.2204 | 11.1033 | 22.9679 | 67.6951 | 153.0341 | 126.4221 | 94.8736 | 99.56% | 99.6% | 99.52% | 99.5% | 99.5% | 99.19% | 124.3685 | 127.3992 | 149.3858 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 129.9076 | 11 | 21 | 46 | 22 | 98.77% | 0.093168 | 0.094249 | 42.8363 | 40.1958 | 140.8986 | 22.4809 | 98.77% | 3528.2464 | 99.45% | 99.45% | 85% |  |  | 99.41% | 1.0679
2021-01-24 | 182.8753 | 165.6796 | 165.6796 | 153.9931 | 140.7442 | 13.8893 | 13.8893 | 3447.7447 | 1033.8065 | 330.8181 | 609.5928 | 20.1102 | 10.0551 | 19.1961 | 42.0485 | 8753.0091 | 378.3176 |  |  | 23.7428 | 1.0439 | 15.8658 | 4057.3376 | 2083.1201 | 1974.2174 | 940.4109 | 17.1956 | 11.6865 | 13.0179 | 13.7349 | 11.0765 | 7.089 | 3322.6476 | 6954.1767 | 10705.2985 | 2272.4062 | 4699.3557 | 8561.6963 | 0.096175 | 0.094351 | 0.081424 | 16.9331 | 10.6813 | 12.06 | 10.9121 | 22.5828 | 66.6042 | 149.0764 | 122.5463 | 90.8812 | 99.56% | 99.59% | 99.51% | 99.52% | 99.52% | 99.22% | 124.7727 | 127.184 | 147.3758 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 126.845 | 11 | 21 | 46 | 22 | 98.76% | 0.093231 | 0.094213 | 41.9 | 39.6743 | 136.8039 | 22.1034 | 98.76% | 3603.5973 | 99.44% | 99.47% | 84.98% |  |  | 99.42% | 1.0439
2021-01-23 | 183.2774 | 166.1077 | 166.1077 | 154.469 | 141.4166 | 14.0034 | 14.0034 | 3456.467 | 1036.4219 | 331.655 | 611.2833 | 21.7303 | 10.8651 | 20.7425 | 45.436 | 9242.882 | 380.4586 |  |  | 23.8534 | 1.0399 | 17.144 | 4067.7503 | 2088.3901 | 1979.3602 | 942.9383 | 17.1697 | 11.6388 | 13.0686 | 13.7696 | 11.1045 | 7.1069 | 3493.6733 | 7310.9129 | 11252.836 | 2389.5419 | 4940.884 | 9000.2922 | 0.096235 | 0.0949 | 0.082887 | 16.8423 | 10.5958 | 12.0577 | 11.199 | 23.1799 | 68.3763 | 148.7958 | 121.6842 | 89.1651 | 99.55% | 99.58% | 99.5% | 99.53% | 99.53% | 99.24% | 124.6953 | 126.449 | 144.7758 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 127.3612 | 11 | 21 | 46 | 22 | 98.73% | 0.093672 | 0.094554 | 41.8771 | 39.4959 | 135.9791 | 22.6874 | 98.73% | 3788.8769 | 99.43% | 99.48% | 84.97% |  |  | 99.41% | 1.0399
2021-01-22 | 182.2301 | 165.0535 | 165.0535 | 153.4589 | 140.447 | 14.0825 | 14.0825 | 3470.07 | 1040.5007 | 332.9602 | 611.6579 | 22.6074 | 11.3037 | 21.5798 | 47.27 | 9436.4453 | 378.833 |  |  | 24.2504 | 1.0259 | 17.836 | 4081.7278 | 2096.609 | 1985.1189 | 944.6181 | 17.1766 | 11.5946 | 13.0184 | 13.8238 | 11.1482 | 7.1349 | 3534.5548 | 7404.1111 | 11408.859 | 2416.9232 | 5000.9688 | 9119.6926 | 0.096126 | 0.095087 | 0.083644 | 16.7669 | 10.5154 | 11.9876 | 11.4083 | 23.5968 | 69.5299 | 147.5312 | 120.2768 | 87.5084 | 99.53% | 99.57% | 99.48% | 99.53% | 99.53% | 99.24% | 124.8357 | 126.1997 | 143.4651 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 126.3671 | 11 | 21 | 46 | 22 | 98.69% | 0.093797 | 0.094617 | 41.7895 | 39.2699 | 134.5946 | 23.0957 | 98.69% | 3834.8938 | 99.41% | 99.48% | 85.01% |  |  | 99.4% | 1.0259
2021-01-21 | 182.0185 | 164.8014 | 164.8014 | 153.2512 | 140.191 | 14.057 | 14.057 | 3465.8458 | 1039.2341 | 332.5549 | 612.2246 | 23.4348 | 11.7174 | 22.3696 | 49.0001 | 9542.0467 | 377.5776 |  |  | 24.4649 | 1.0184 | 18.4888 | 4078.0704 | 2094.0568 | 1984.0137 | 944.7795 | 17.2172 | 11.5502 | 12.986 | 13.807 | 11.1347 | 7.1262 | 3530.4971 | 7389.3505 | 11376.5629 | 2414.7758 | 4993.371 | 9097.9675 | 0.095434 | 0.094406 | 0.083017 | 16.8264 | 10.4802 | 11.9493 | 11.7357 | 24.2892 | 71.6322 | 147.3376 | 120.1142 | 87.4192 | 99.51% | 99.55% | 99.46% | 99.51% | 99.51% | 99.21% | 125.7416 | 127.1105 | 144.5486 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 126.1755 | 11 | 21 | 46 | 22 | 98.64% | 0.093118 | 0.093934 | 41.7534 | 39.2559 | 134.4481 | 23.7725 | 98.64% | 3829.2335 | 99.39% | 99.47% | 84.99% |  |  | 99.38% | 1.0184
2021-01-20 | 184.2869 | 166.981 | 166.981 | 155.3353 | 142.3856 | 13.9567 | 13.9567 | 3469.7249 | 1040.3973 | 332.9271 | 613.1789 | 23.1832 | 11.5916 | 22.1294 | 48.4739 | 9725.8234 | 382.6474 |  |  | 24.1111 | 1.0308 | 18.2903 | 4082.9038 | 2096.4005 | 1986.5033 | 946.106 | 17.306 | 11.6457 | 12.9696 | 13.8224 | 11.1471 | 7.1342 | 3601.3181 | 7537.2175 | 11603.2508 | 2463.1656 | 5093.4295 | 9279.6665 | 0.095355 | 0.094303 | 0.082862 | 16.8826 | 10.5462 | 11.9081 | 11.5329 | 23.8696 | 70.3992 | 149.4193 | 121.8449 | 88.7477 | 99.53% | 99.57% | 99.48% | 99.53% | 99.53% | 99.24% | 125.845 | 127.25 | 144.8198 |  |  |  | 31 | 25 | 16 | 2418 | 1200 | 384 | 4002 | 128.3941 | 11 | 21 | 46 | 22 | 98.68% | 0.093019 | 0.093841 | 41.9213 | 39.3369 | 136.3158 | 23.3621 | 98.68% | 3905.9075 | 99.41% | 99.49% | 84.98% |  |  | 99.39% | 1.0308
2021-01-19 | 182.7464 | 165.4581 | 165.4581 | 153.6809 | 140.512 | 13.9694 | 13.9694 | 3470.249 | 1033.8161 | 328.6168 | 613.0374 | 21.6927 | 11.3101 | 21.873 | 47.0438 | 9249.1992 | 379.2096 |  |  | 24.0198 | 1.034 | 17.8407 | 4083.2864 | 2107.8162 | 1975.4702 | 941.6541 | 17.2883 | 11.7772 | 13.027 | 13.8977 | 11.0766 | 7.0418 | 3440.8192 | 7194.3856 | 11025.6955 | 2346.0902 | 4864.3776 | 8839.0708 | 0.096797 | 0.094353 | 0.081659 | 16.9098 | 10.7504 | 12.0139 | 11.9159 | 24.6245 | 71.0206 | 148.4589 | 121.3875 | 89.1669 | 99.52% | 99.55% | 99.47% | 99.49% | 99.49% | 99.2% | 123.9711 | 127.1817 | 146.9527 |  |  |  | 31 | 24.7073 | 15.7073 | 2418 | 1185.9512 | 376.9756 | 3980.9268 | 126.5608 | 10.7073 | 20.7073 | 44.5366 | 20.5366 | 98.7% | 0.093593 | 0.094635 | 42.0925 | 39.6741 | 135.8906 | 23.0827 | 98.7% | 3711.1646 | 99.42% | 99.45% | 84.99% |  |  | 99.4% | 1.034
2021-01-18 | 180.6831 | 163.3944 | 163.3944 | 151.6795 | 138.4448 | 14.0452 | 14.0452 | 3468.1207 | 1016.6094 | 317.6904 | 612.9861 | 18.3139 | 10.7729 | 21.5457 | 44.1688 | 8829.2022 | 375.4169 |  |  | 24.3425 | 1.0227 | 16.9899 | 4081.1068 | 2133.8208 | 1947.286 | 930.6765 | 17.2888 | 11.7149 | 13.0035 | 14.0691 | 10.8922 | 6.8077 | 3374.1502 | 7036.3133 | 10660.1109 | 2282.8567 | 4764.5763 | 8598.7442 | 0.098122 | 0.092999 | 0.078894 | 17.0382 | 10.9125 | 12.121 | 11.6786 | 24.0847 | 65.5377 | 146.6331 | 119.7766 | 88.244 | 99.53% | 99.55% | 99.49% | 99.49% | 99.49% | 99.24% | 122.2963 | 129.0338 | 152.1027 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 124.4488 | 10 | 20 | 41 | 17 | 98.87% | 0.093406 | 0.094859 | 42.0072 | 40.0716 | 134.5111 | 19.918 | 98.87% | 3588.8772 | 99.49% | 99.45% | 84.98% |  |  | 99.48% | 1.0227
2021-01-17 | 180.5298 | 163.3826 | 163.3826 | 151.7858 | 138.7418 | 14.0837 | 14.0837 | 3464.1802 | 1015.4543 | 317.3295 | 611.41 | 19.3043 | 11.3555 | 22.7109 | 46.5574 | 9141.9796 | 374.6086 |  |  | 24.5447 | 1.0156 | 17.9087 | 4075.5902 | 2131.3963 | 1944.1938 | 928.7395 | 17.1472 | 11.5968 | 12.9574 | 14.0532 | 10.8799 | 6.7999 | 3472.6232 | 7244.6479 | 10980.5473 | 2349.2824 | 4904.5155 | 8855.1445 | 0.097637 | 0.092785 | 0.079257 | 16.9349 | 10.8308 | 12.1193 | 11.8663 | 24.4654 | 66.5447 | 146.1829 | 119.0915 | 87.1372 | 99.52% | 99.54% | 99.47% | 99.49% | 99.5% | 99.25% | 122.9048 | 129.3312 | 151.4071 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 124.595 | 10 | 20 | 41 | 17 | 98.84% | 0.093143 | 0.094531 | 41.7014 | 39.8851 | 133.7584 | 20.233 | 98.84% | 3694.2541 | 99.48% | 99.46% | 85% |  |  | 99.47% | 1.0156
2021-01-16 | 181.0523 | 163.9663 | 163.9663 | 152.5525 | 139.7521 | 14.0232 | 14.0232 | 3452.7681 | 1012.1091 | 316.2841 | 608.2376 | 20.4447 | 12.0263 | 24.0525 | 49.3077 | 9698.4425 | 374.1342 |  |  | 24.5361 | 1.0159 | 18.9666 | 4061.0057 | 2124.3749 | 1936.6308 | 924.5217 | 17.086 | 11.4139 | 12.8079 | 14.0069 | 10.844 | 6.7775 | 3654.5245 | 7628.9404 | 11570.3564 | 2471.9422 | 5162.8506 | 9327.6225 | 0.097341 | 0.092935 | 0.080308 | 16.968 | 10.7259 | 12.0662 | 11.9078 | 24.5402 | 66.7049 | 146.1866 | 118.5422 | 85.7375 | 99.51% | 99.53% | 99.47% | 99.52% | 99.52% | 99.28% | 123.2781 | 129.1226 | 149.4239 |  |  |  | 31 | 24 | 15 | 2418 | 1152 | 360 | 3930 | 125.7178 | 10 | 20 | 41 | 17 | 98.83% | 0.093206 | 0.094489 | 41.3077 | 39.7601 | 133.2672 | 20.2954 | 98.83% | 3888.7288 | 99.47% | 99.48% | 85.02% |  |  | 99.47% | 1.0159
2021-01-15 | 179.4876 | 162.548 | 162.548 | 151.2626 | 138.4623 | 14.0426 | 14.0426 | 3431.2678 | 1002.7449 | 369.0658 | 604.0642 | 19.6305 | 9.9711 | 20.5653 | 43.3118 | 9625.3558 | 368.2843 |  |  | 24.5826 | 1.0143 | 16.6532 | 4035.3319 | 2059.457 | 1975.8749 | 973.13 | 16.9397 | 11.2853 | 12.7315 | 13.5788 | 10.7437 | 7.9086 | 3527.3945 | 7140.9458 | 11477.3963 | 2420.5833 | 4916.3257 | 8968.7591 | 0.095039 | 0.092052 | 0.093068 | 16.7658 | 10.1348 | 11.4909 | 9.7588 | 21.796 | 70.9948 | 144.9222 | 118.3839 | 86.1927 | 99.59% | 99.58% | 99.52% | 99.6% | 99.56% | 99.21% | 126.264 | 130.3606 | 128.9379 |  |  |  | 30.3333 | 24 | 17.6667 | 2366 | 1152 | 424 | 3942 | 124.46 | 10.6667 | 22 | 46.3333 | 21 | 98.87% | 0.093768 | 0.093954 | 40.9565 | 38.3915 | 131.9919 | 19.5082 | 98.87% | 3854.252 | 99.49% | 99.52% | 85.03% |  |  | 99.49% | 1.0143
2021-01-14 | 180.4247 | 163.3536 | 163.3536 | 151.9157 | 138.7822 | 14.0364 | 14.0364 | 3451.4741 | 1007.1171 | 398.6505 | 609.4086 | 18.5151 | 8.855 | 18.5151 | 39.4452 | 9714.016 | 372.6648 |  |  | 24.2441 | 1.0261 | 15.207 | 4060.8827 | 2045.7065 | 2015.1762 | 1008.0591 | 17.0711 | 11.4379 | 12.8343 | 13.4882 | 10.7905 | 8.5425 | 3490.5893 | 6959.4187 | 11486.1858 | 2412.7913 | 4832.2994 | 8847.9154 | 0.094905 | 0.092632 | 0.10044 | 16.626 | 9.8958 | 11.1538 | 8.7368 | 20.2844 | 71.6164 | 145.8331 | 119.5294 | 87.2703 | 99.63% | 99.62% | 99.55% | 99.64% | 99.58% | 99.19% | 126.4423 | 129.5451 | 119.4731 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 124.8261 | 11 | 23 | 49 | 23 | 98.93% | 0.095063 | 0.094881 | 41.3432 | 37.6757 | 132.8002 | 18.6854 | 98.93% | 3862.0542 | 99.52% | 99.55% | 84.99% |  |  | 99.51% | 1.0261
2021-01-13 | 179.2825 | 162.1153 | 162.1153 | 150.7177 | 137.4716 | 13.9471 | 13.9471 | 3456.8573 | 1008.6878 | 399.2723 | 610.7843 | 19.0121 | 9.0928 | 19.0121 | 40.5041 | 9610.5138 | 370.2971 |  |  | 24.1144 | 1.0307 | 15.6152 | 4067.6416 | 2048.8972 | 2018.7444 | 1010.0566 | 17.1671 | 11.3976 | 12.7148 | 13.5092 | 10.8074 | 8.5558 | 3448.4113 | 6873.1633 | 11339.7015 | 2383.9115 | 4773.244 | 8736.7974 | 0.096105 | 0.093841 | 0.10175 | 16.6771 | 9.8338 | 11.0155 | 9.1347 | 21.2134 | 74.922 | 144.8777 | 118.6982 | 86.666 | 99.62% | 99.6% | 99.54% | 99.62% | 99.56% | 99.14% | 124.8632 | 127.8754 | 117.9368 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 123.6281 | 11 | 23 | 49 | 23 | 98.89% | 0.096284 | 0.096097 | 41.2796 | 37.5264 | 132.0441 | 19.5411 | 98.89% | 3814.8707 | 99.5% | 99.52% | 84.98% |  |  | 99.49% | 1.0307
2021-01-12 | 182.2405 | 164.9711 | 164.9711 | 153.4712 | 140.1878 | 13.6677 | 13.6677 | 3449.6463 | 1006.5837 | 398.4394 | 609.7742 | 19.1206 | 9.1446 | 19.1206 | 40.7352 | 9423.885 | 373.6849 |  |  | 23.9 | 1.0383 | 15.7043 | 4059.4205 | 2044.6232 | 2014.7973 | 1008.2136 | 17.2694 | 11.4998 | 12.9121 | 13.481 | 10.7848 | 8.538 | 3420.6932 | 6816.767 | 11244.37 | 2364.8852 | 4734.5231 | 8664.302 | 0.094471 | 0.0918 | 0.098448 | 16.8269 | 9.9505 | 11.216 | 9.3095 | 21.6222 | 76.3801 | 148.1594 | 121.9764 | 90.044 | 99.61% | 99.6% | 99.53% | 99.61% | 99.54% | 99.12% | 127.0225 | 130.7186 | 121.8916 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 126.7005 | 11 | 23 | 49 | 23 | 98.88% | 0.094253 | 0.094151 | 41.6814 | 37.9934 | 135.3663 | 19.9177 | 98.88% | 3783.9219 | 99.49% | 99.51% | 84.98% |  |  | 99.48% | 1.0383
2021-01-11 | 179.9186 | 163.0528 | 163.0528 | 151.5537 | 138.4834 | 14.1491 | 14.1491 | 3413.5254 | 996.0439 | 394.2674 | 603.1085 | 16.5207 | 7.9012 | 16.5207 | 35.1964 | 8764.1994 | 366.2047 |  |  | 23.876 | 1.0391 | 13.569 | 4016.6339 | 2023.2141 | 1993.4197 | 997.3758 | 16.8658 | 11.4991 | 12.8438 | 13.3399 | 10.6719 | 8.4486 | 3200.18 | 6379.5875 | 10527.0776 | 2212.0918 | 4430.0097 | 8109.9918 | 0.094738 | 0.091582 | 0.097011 | 16.6975 | 10.1111 | 11.3402 | 8.5162 | 19.7735 | 69.8242 | 146.3157 | 121.0867 | 90.4955 | 99.64% | 99.63% | 99.57% | 99.62% | 99.55% | 99.14% | 126.6652 | 131.0306 | 123.6975 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 124.346 | 11 | 23 | 49 | 23 | 98.96% | 0.094092 | 0.094079 | 41.2087 | 38.1487 | 134.1531 | 18.2151 | 98.96% | 3540.4818 | 99.53% | 99.52% | 84.98% |  |  | 99.52% | 1.0391
2021-01-10 | 181.4216 | 164.2866 | 164.2866 | 152.6903 | 139.6434 | 14.0059 | 14.0059 | 3442.2064 | 1004.4128 | 397.5801 | 608.4692 | 16.6527 | 7.9643 | 16.6527 | 35.4774 | 9000.5049 | 372.764 |  |  | 23.9508 | 1.0365 | 13.6773 | 4050.6756 | 2040.2135 | 2010.462 | 1006.0492 | 17.135 | 11.5963 | 13.0112 | 13.452 | 10.7616 | 8.5196 | 3270.865 | 6519.7841 | 10756.6975 | 2261.0008 | 4527.6391 | 8287.6075 | 0.094471 | 0.09148 | 0.097141 | 16.75 | 10.0664 | 11.3385 | 8.4474 | 19.6152 | 69.2745 | 147.5831 | 121.9276 | 90.9003 | 99.65% | 99.63% | 99.57% | 99.63% | 99.57% | 99.16% | 127.0227 | 131.1768 | 123.5316 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 125.5445 | 11 | 23 | 49 | 23 | 98.98% | 0.093941 | 0.093907 | 41.7425 | 38.155 | 135.1974 | 18.0694 | 98.98% | 3618.4729 | 99.54% | 99.53% | 84.98% |  |  | 99.53% | 1.0365
2021-01-09 | 183.2466 | 165.9418 | 165.9418 | 154.2796 | 141.1948 | 14.1409 | 14.1409 | 3463.664 | 1010.674 | 400.0585 | 611.1856 | 17.1293 | 8.1923 | 17.1293 | 36.4928 | 9442.5922 | 378.8753 |  |  | 23.9416 | 1.0368 | 14.0688 | 4074.8497 | 2052.9316 | 2021.9181 | 1011.2441 | 17.3048 | 11.6622 | 13.0388 | 13.5358 | 10.8287 | 8.5727 | 3401.8255 | 6784.6136 | 11201.6722 | 2351.1424 | 4710.0837 | 8627.0856 | 0.094351 | 0.091645 | 0.098055 | 16.7679 | 10.0403 | 11.2796 | 8.4107 | 19.5221 | 68.9014 | 148.7386 | 122.5051 | 90.6434 | 99.65% | 99.64% | 99.58% | 99.64% | 99.59% | 99.2% | 127.1843 | 130.9405 | 122.3809 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 127.0603 | 11 | 23 | 49 | 23 | 98.99% | 0.094078 | 0.093989 | 42.0058 | 38.0879 | 135.9442 | 17.9833 | 98.99% | 3764.3467 | 99.54% | 99.55% | 85% |  |  | 99.53% | 1.0368
2021-01-08 | 182.8696 | 165.5929 | 165.5929 | 153.9709 | 140.8521 | 14.1142 | 14.1142 | 3468.005 | 1011.9407 | 400.5598 | 612.9173 | 17.3679 | 8.3064 | 17.3679 | 37.0013 | 9525.6973 | 378.5427 |  |  | 24.1069 | 1.0309 | 14.2648 | 4080.9223 | 2055.5045 | 2025.4178 | 1013.4771 | 17.2767 | 11.6221 | 13.055 | 13.5528 | 10.8422 | 8.5834 | 3435.5855 | 6848.6208 | 11300.2184 | 2374.8048 | 4755.8047 | 8705.9565 | 0.094224 | 0.091638 | 0.098373 | 16.7013 | 9.9775 | 11.2523 | 8.4059 | 19.5177 | 68.9244 | 148.2846 | 121.9756 | 89.9526 | 99.65% | 99.63% | 99.57% | 99.65% | 99.59% | 99.21% | 127.3557 | 130.9499 | 121.9842 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 126.703 | 11 | 23 | 49 | 23 | 98.98% | 0.094061 | 0.093949 | 41.9538 | 37.9312 | 135.3871 | 17.9795 | 98.98% | 3800.8223 | 99.54% | 99.56% | 84.98% |  |  | 99.53% | 1.0309
2021-01-07 | 181.8171 | 164.6657 | 164.6657 | 153.1497 | 140.1041 | 14.0084 | 14.0084 | 3458.9511 | 1009.2988 | 399.5141 | 611.426 | 17.2912 | 8.2697 | 17.2912 | 36.8379 | 9568.253 | 375.4828 |  |  | 24.0837 | 1.0318 | 14.2018 | 4070.3771 | 2050.1382 | 2020.2389 | 1010.9401 | 17.1514 | 11.516 | 12.9841 | 13.5174 | 10.8139 | 8.561 | 3468.4118 | 6913.9292 | 11407.5147 | 2397.4864 | 4801.2059 | 8788.8131 | 0.09469 | 0.092224 | 0.099403 | 16.6444 | 9.9242 | 11.2329 | 8.2745 | 19.2127 | 67.8494 | 147.2869 | 120.9797 | 88.8586 | 99.66% | 99.64% | 99.58% | 99.65% | 99.6% | 99.23% | 126.7294 | 130.1175 | 120.7203 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 126.0486 | 11 | 23 | 49 | 23 | 99% | 0.094655 | 0.094515 | 41.6514 | 37.8016 | 134.2986 | 17.6987 | 99% | 3837.0836 | 99.55% | 99.57% | 84.98% |  |  | 99.54% | 1.0318
2021-01-06 | 181.5713 | 164.5303 | 164.5303 | 153.0748 | 140.0624 | 14.0484 | 14.0484 | 3450.3941 | 1006.8019 | 398.5258 | 607.4769 | 17.8807 | 8.5516 | 17.8807 | 38.0936 | 9635.3543 | 373.8505 |  |  | 24.1412 | 1.0297 | 14.6859 | 4057.871 | 2045.0664 | 2012.8046 | 1006.0027 | 17.041 | 11.4555 | 12.9099 | 13.484 | 10.7872 | 8.5398 | 3485.9571 | 6956.7888 | 11495.691 | 2408.893 | 4827.9177 | 8849.459 | 0.094453 | 0.092025 | 0.099405 | 16.6189 | 9.9329 | 11.2611 | 8.4783 | 19.6701 | 69.3724 | 147.0006 | 120.7039 | 88.4633 | 99.64% | 99.63% | 99.57% | 99.65% | 99.59% | 99.22% | 127.0467 | 130.3993 | 120.7188 |  |  |  | 30 | 24 | 19 | 2340 | 1152 | 456 | 3948 | 126.0734 | 11 | 23 | 49 | 23 | 98.97% | 0.094469 | 0.094317 | 41.4065 | 37.8129 | 133.942 | 18.119 | 98.97% | 3858.6434 | 99.54% | 99.56% | 85.03% |  |  | 99.53% | 1.0297
2021-01-05 | 180.8948 | 163.7007 | 163.7007 | 152.1054 | 139.0631 | 14.2273 | 14.2273 | 3453.8112 | 1008.1903 | 360.3822 | 609.8145 | 17.3778 | 8.3111 | 17.3778 | 37.0223 | 9303.147 | 374.1422 |  |  | 24.1166 | 1.0306 | 13.9536 | 4063.6257 | 2085.2387 | 1978.387 | 970.1967 | 17.194 | 11.5954 | 13.0115 | 13.7488 | 10.802 | 7.7225 | 3449.0069 | 7015.0209 | 11138.8107 | 2358.7061 | 4817.0191 | 8761.3692 | 0.09684 | 0.093021 | 0.090713 | 16.8876 | 10.4154 | 11.7123 | 8.5877 | 19.2028 | 61.6334 | 146.3185 | 119.6776 | 87.7352 | 99.65% | 99.64% | 99.58% | 99.64% | 99.6% | 99.3% | 123.9163 | 129.0036 | 132.2855 |  |  |  | 30 | 23.5701 | 16.8505 | 2340 | 1131.3646 | 404.4115 | 3875.776 | 124.8585 | 11 | 23 | 49 | 23 | 98.97% | 0.094637 | 0.095086 | 41.8009 | 39.0153 | 133.6773 | 18.1802 | 98.97% | 3744.3792 | 99.54% | 99.57% | 84.99% |  |  | 99.52% | 1.0306
2021-01-04 | 180.4197 | 163.1656 | 163.1656 | 151.4111 | 138.1091 | 14.1839 | 14.1839 | 3469.5026 | 1013.3151 | 308.4002 | 611.434 | 17.9195 | 8.5702 | 17.9195 | 38.1764 | 8865.522 | 374.925 |  |  | 23.9266 | 1.0373 | 13.9325 | 4080.9367 | 2147.7873 | 1933.1493 | 919.8343 | 17.254 | 11.7546 | 13.1097 | 14.1612 | 10.8569 | 6.6086 | 3385.4715 | 7095.2605 | 10654.7719 | 2280.3486 | 4791.0553 | 8635.1326 | 0.10044 | 0.09445 | 0.078263 | 17.0647 | 11.0936 | 12.3686 | 9.496 | 20.1405 | 55.5426 | 146.2499 | 119.2388 | 87.5914 | 99.62% | 99.63% | 99.56% | 99.58% | 99.58% | 99.36% | 119.4715 | 127.0515 | 153.3287 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 123.9175 | 11 | 23 | 49 | 23 | 98.89% | 0.094976 | 0.096721 | 42.1184 | 40.5269 | 134.1612 | 19.8336 | 98.89% | 3578.504 | 99.5% | 99.55% | 85.02% |  |  | 99.48% | 1.0373
2021-01-03 | 178.1361 | 160.9753 | 160.9753 | 149.2834 | 135.9772 | 14.0602 | 14.0602 | 3446.2813 | 1006.5329 | 306.3361 | 608.404 | 17.0467 | 8.1528 | 17.0467 | 36.3169 | 8557.4432 | 366.3364 |  |  | 23.9478 | 1.0366 | 13.2538 | 4054.6853 | 2133.4122 | 1921.2731 | 914.7401 | 17.1608 | 11.6919 | 13.0925 | 14.0665 | 10.7843 | 6.5643 | 3276.4001 | 6862.8246 | 10300.0238 | 2207.181 | 4635.56 | 8350.0956 | 0.1009 | 0.094752 | 0.07821 | 17.1352 | 11.1336 | 12.4513 | 9.2637 | 19.6553 | 54.2357 | 144.5003 | 117.9766 | 87.0012 | 99.63% | 99.63% | 99.57% | 99.58% | 99.58% | 99.35% | 118.9243 | 126.6458 | 153.4335 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 121.924 | 11 | 23 | 49 | 23 | 98.91% | 0.095305 | 0.09709 | 41.9452 | 40.7201 | 132.7445 | 19.3552 | 98.91% | 3462.4587 | 99.51% | 99.54% | 85% |  |  | 99.49% | 1.0366
2021-01-02 | 177.2745 | 160.1929 | 160.1929 | 148.5495 | 135.4257 | 13.79 | 13.79 | 3435.6664 | 1003.4327 | 305.3926 | 606.144 | 18.511 | 8.8531 | 18.511 | 39.4364 | 8512.3775 | 362.7833 |  |  | 23.8857 | 1.0388 | 14.3923 | 4041.8105 | 2126.8411 | 1914.9694 | 911.5366 | 17.0816 | 11.6433 | 12.9669 | 14.0231 | 10.7511 | 6.5441 | 3272.1267 | 6853.7541 | 10287.0008 | 2204.4694 | 4629.4784 | 8339.2825 | 0.10118 | 0.095024 | 0.078408 | 17.1385 | 11.1433 | 12.3985 | 10.0622 | 21.3512 | 58.9143 | 143.9656 | 117.5264 | 86.6984 | 99.6% | 99.6% | 99.53% | 99.54% | 99.54% | 99.29% | 118.5978 | 126.2835 | 153.046 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 121.5787 | 11 | 23 | 49 | 23 | 98.81% | 0.095568 | 0.097359 | 41.6918 | 40.6804 | 132.2369 | 21.0245 | 98.81% | 3458.0427 | 99.46% | 99.5% | 85% |  |  | 99.45% | 1.0388
2021-01-01 | 178.6655 | 161.6179 | 161.6179 | 150.0297 | 136.8921 | 13.8554 | 13.8554 | 3437.4727 | 1003.9603 | 305.5531 | 606.5016 | 18.4872 | 8.8417 | 18.4872 | 39.3859 | 8858.6509 | 364.8063 |  |  | 23.9027 | 1.0382 | 14.3739 | 4043.9743 | 2127.9593 | 1916.015 | 912.0547 | 17.0476 | 11.5882 | 12.9698 | 14.0305 | 10.7567 | 6.5476 | 3393.4954 | 7108.5949 | 10670.0347 | 2286.1082 | 4801.3784 | 8649.5618 | 0.10052 | 0.094594 | 0.078534 | 17.0906 | 11.0814 | 12.3906 | 9.6899 | 20.5592 | 56.7249 | 144.9 | 118.054 | 86.5546 | 99.61% | 99.61% | 99.54% | 99.58% | 99.57% | 99.34% | 119.3743 | 126.8576 | 152.8009 |  |  |  | 30 | 23 | 14 | 2340 | 1104 | 336 | 3780 | 122.995 | 11 | 23 | 49 | 23 | 98.85% | 0.095108 | 0.096838 | 41.6056 | 40.5625 | 132.8142 | 20.2451 | 98.85% | 3586.3671 | 99.48% | 99.54% | 85% |  |  | 99.47% | 1.0382
2020-12-31 | 179.4895 | 162.5591 | 162.5591 | 151.1821 | 138.2654 | 13.9886 | 13.9886 | 3423.6731 | 1029.3835 | 300.6283 | 603.9146 | 19.3761 | 8.8923 | 18.5929 | 39.611 | 9376.4899 | 365.9787 |  |  | 24.035 | 1.0335 | 14.5063 | 4027.5877 | 2093.6613 | 1933.9264 | 904.5429 | 16.9303 | 11.3771 | 12.8067 | 13.8044 | 11.0291 | 6.442 | 3519.62 | 7503.8417 | 11219.5308 | 2388.705 | 5018.425 | 9113.9216 | 0.098296 | 0.096691 | 0.077992 | 16.9665 | 10.8198 | 12.3578 | 9.1349 | 20.1917 | 53.029 | 145.1367 | 117.8829 | 85.3636 | 99.63% | 99.63% | 99.57% | 99.62% | 99.6% | 99.42% | 122.0799 | 124.1062 | 153.8626 |  |  |  | 30 | 23.9688 | 14 | 2340 | 1150.5 | 336 | 3826.5 | 124.309 | 11 | 23 | 49 | 23.9688 | 98.86% | 0.094534 | 0.096031 | 41.1141 | 40.144 | 132.5258 | 20.0135 | 98.86% | 3769.906 | 99.49% | 99.58% | 85.01% |  |  | 99.48% | 1.0335
2020-12-30 | 182.4485 | 165.1117 | 165.1117 | 153.3565 | 140.1487 | 13.9762 | 13.9762 | 3471.997 | 1044.8643 | 304.7521 | 611.7901 | 18.93 | 8.6762 | 18.1412 | 38.6487 | 9344.885 | 378.0892 |  |  | 23.7445 | 1.0438 | 14.1554 | 4083.7871 | 2122.3806 | 1961.4065 | 916.5422 | 17.3367 | 11.7553 | 13.0757 | 13.9937 | 11.195 | 6.5304 | 3497.7729 | 7464.5763 | 11163.6666 | 2374.1457 | 4989.4134 | 9067.3091 | 0.09871 | 0.097054 | 0.077785 | 17.0143 | 10.9502 | 12.3721 | 9.1816 | 20.315 | 53.2475 | 147.9766 | 120.4015 | 87.6331 | 99.63% | 99.64% | 99.57% | 99.61% | 99.59% | 99.41% | 121.5681 | 123.6428 | 154.2724 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 126.1751 | 11 | 23 | 49 | 24 | 98.88% | 0.094832 | 0.096375 | 42.1677 | 40.3366 | 135.363 | 20.1405 | 98.88% | 3748.6732 | 99.5% | 99.57% | 85.02% |  |  | 99.47% | 1.0438
2020-12-29 | 182.3181 | 164.8735 | 164.8735 | 152.9333 | 139.7018 | 13.994 | 13.994 | 3468.5947 | 1043.8404 | 304.4535 | 613.1237 | 17.7109 | 8.1175 | 16.973 | 36.1598 | 8897.8295 | 378.0876 |  |  | 23.3651 | 1.0575 | 13.2439 | 4081.7184 | 2120.3008 | 1961.4176 | 917.5772 | 17.4446 | 11.9402 | 13.2782 | 13.98 | 11.184 | 6.524 | 3345.5381 | 7132.1304 | 10655.7141 | 2271.3892 | 4770.0454 | 8659.4034 | 0.099698 | 0.097628 | 0.077338 | 17.1289 | 11.1164 | 12.5345 | 9.0877 | 20.1218 | 52.7975 | 148.2854 | 121.144 | 89.2073 | 99.64% | 99.64% | 99.58% | 99.6% | 99.58% | 99.39% | 120.363 | 122.9154 | 155.163 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 125.6296 | 11 | 23 | 49 | 24 | 98.9% | 0.095458 | 0.097113 | 42.663 | 40.7798 | 136.0837 | 19.948 | 98.9% | 3584.0393 | 99.51% | 99.56% | 84.98% |  |  | 99.48% | 1.0575
2020-12-28 | 179.3657 | 162.015 | 162.015 | 150.2393 | 137.1479 | 14.08 | 14.08 | 3472.4942 | 1045.0139 | 304.7957 | 612.3587 | 18.7431 | 8.5906 | 17.9621 | 38.2672 | 9034.7714 | 370.8288 |  |  | 23.9 | 1.0383 | 14.0157 | 4084.8529 | 2122.6845 | 1962.1683 | 917.1544 | 17.3508 | 11.7757 | 13.1635 | 13.9957 | 11.1966 | 6.5313 | 3391.1984 | 7234.694 | 10816.6473 | 2302.0441 | 4836.6755 | 8786.8486 | 0.10012 | 0.098556 | 0.07897 | 17.0203 | 10.9614 | 12.4407 | 9.3272 | 20.6423 | 54.1232 | 145.143 | 117.9535 | 85.8706 | 99.63% | 99.63% | 99.56% | 99.59% | 99.57% | 99.38% | 119.8603 | 121.7587 | 151.9557 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 123.0431 | 11 | 23 | 49 | 24 | 98.85% | 0.096234 | 0.097791 | 42.2899 | 40.4224 | 132.8346 | 20.4645 | 98.85% | 3634.0163 | 99.48% | 99.55% | 85.01% |  |  | 99.46% | 1.0383
2020-12-27 | 176.489 | 159.1944 | 159.1944 | 147.5224 | 134.3287 | 14.0884 | 14.0884 | 3469.4964 | 1044.1118 | 304.5326 | 612.9518 | 19.1353 | 8.7704 | 18.338 | 39.068 | 8721.3869 | 365.3186 |  |  | 24.3201 | 1.0234 | 14.309 | 4082.4482 | 2120.852 | 1961.5961 | 917.4844 | 17.2945 | 11.672 | 13.1124 | 13.9836 | 11.1869 | 6.5257 | 3287.4891 | 7007.8349 | 10470.1248 | 2232.1944 | 4687.1202 | 8508.5344 | 0.10034 | 0.098763 | 0.079047 | 16.9777 | 10.8662 | 12.3812 | 9.6718 | 21.4179 | 56.2005 | 142.6362 | 115.9262 | 84.4899 | 99.61% | 99.61% | 99.54% | 99.57% | 99.54% | 99.34% | 119.5985 | 121.5031 | 151.8076 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 120.1725 | 11 | 23 | 49 | 24 | 98.79% | 0.096426 | 0.097994 | 42.0789 | 40.2251 | 130.6735 | 21.232 | 98.79% | 3521.8822 | 99.46% | 99.52% | 84.99% |  |  | 99.44% | 1.0234
2020-12-26 | 174.3309 | 157.3107 | 157.3107 | 145.7606 | 132.6579 | 13.7908 | 13.7908 | 3436.1152 | 1034.066 | 301.6026 | 606.9539 | 19.7651 | 9.059 | 18.9415 | 40.3537 | 8648.3129 | 354.4516 |  |  | 24.3053 | 1.024 | 14.7799 | 4043.069 | 2100.4466 | 1942.6225 | 908.5564 | 17.0202 | 11.5501 | 12.9235 | 13.8491 | 11.0793 | 6.4629 | 3264.0789 | 6957.5052 | 10394.72 | 2216.4098 | 4653.6182 | 8447.3474 | 0.10058 | 0.099019 | 0.079366 | 16.9533 | 10.911 | 12.3836 | 9.9695 | 22.0788 | 57.9372 | 140.9932 | 114.5714 | 83.3834 | 99.59% | 99.59% | 99.52% | 99.55% | 99.53% | 99.31% | 119.3091 | 121.1886 | 151.1988 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 118.8834 | 11 | 23 | 49 | 24 | 98.74% | 0.096686 | 0.098248 | 41.4939 | 40.2479 | 129.1074 | 21.8867 | 98.74% | 3496.7805 | 99.43% | 99.5% | 84.99% |  |  | 99.43% | 1.024
2020-12-25 | 175.1 | 158.2108 | 158.2108 | 146.7892 | 133.7796 | 13.8237 | 13.8237 | 3430.8763 | 1032.4894 | 301.1427 | 605.963 | 19.7514 | 9.0527 | 18.9285 | 40.3259 | 9099.4928 | 355.8176 |  |  | 24.458 | 1.0186 | 14.7697 | 4036.8393 | 2097.2441 | 1939.5951 | 907.1057 | 16.8892 | 11.4216 | 12.8214 | 13.828 | 11.0624 | 6.4531 | 3418.0396 | 7286.9892 | 10888.3315 | 2320.7533 | 4873.5046 | 8847.8982 | 0.099705 | 0.098498 | 0.079751 | 16.8619 | 10.815 | 12.3155 | 9.4508 | 20.9265 | 54.9048 | 141.2732 | 114.4034 | 82.4228 | 99.61% | 99.61% | 99.54% | 99.59% | 99.57% | 99.38% | 120.3545 | 121.8293 | 150.4677 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 120.0107 | 11 | 23 | 49 | 24 | 98.8% | 0.096127 | 0.097591 | 41.1321 | 39.9924 | 128.9433 | 20.7451 | 98.8% | 3661.8949 | 99.46% | 99.55% | 84.99% |  |  | 99.46% | 1.0186
2020-12-24 | 179.8839 | 162.7303 | 162.7303 | 151.2808 | 138.1738 | 14.0557 | 14.0557 | 3470.791 | 1044.5014 | 304.6462 | 614.4354 | 20.7705 | 9.5198 | 19.905 | 42.4064 | 9812.6885 | 372.7421 |  |  | 24.3872 | 1.0211 | 15.5317 | 4085.2264 | 2121.6434 | 1963.583 | 919.0816 | 17.1536 | 11.4495 | 12.7858 | 13.9889 | 11.1911 | 6.5281 | 3667.4796 | 7812.8097 | 11665.4917 | 2490.5592 | 5227.4148 | 9483.1173 | 0.098615 | 0.097742 | 0.079861 | 16.8194 | 10.6392 | 12.0365 | 9.3912 | 20.8052 | 54.6285 | 144.8462 | 116.9123 | 83.4681 | 99.62% | 99.62% | 99.55% | 99.62% | 99.6% | 99.42% | 121.6851 | 122.7724 | 150.2601 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 124.1042 | 11 | 23 | 49 | 24 | 98.83% | 0.095335 | 0.096706 | 41.3889 | 39.4951 | 131.8308 | 20.6241 | 98.83% | 3927.9565 | 99.47% | 99.58% | 84.96% |  |  | 99.46% | 1.0211
2020-12-23 | 178.1644 | 161.2549 | 161.2549 | 150.0159 | 137.2572 | 14.0241 | 14.0241 | 3442.2103 | 1035.9003 | 302.1376 | 608.5955 | 21.8404 | 10.0102 | 20.9304 | 44.5908 | 10052.7732 | 364.0589 |  |  | 24.6108 | 1.0133 | 16.3318 | 4050.8058 | 2104.1724 | 1946.6333 | 910.7331 | 16.9095 | 11.239 | 12.6893 | 13.8737 | 11.0989 | 6.4744 | 3732.1055 | 7953.3284 | 11879.6258 | 2534.2845 | 5320.362 | 9655.3172 | 0.098269 | 0.097703 | 0.080442 | 16.7936 | 10.5826 | 12.1134 | 9.5515 | 21.1557 | 55.5283 | 143.0642 | 115.1141 | 81.5588 | 99.61% | 99.61% | 99.54% | 99.62% | 99.6% | 99.42% | 122.1139 | 122.8211 | 149.1757 |  |  |  | 30 | 24 | 14 | 2340 | 1152 | 336 | 3828 | 123.273 | 11 | 23 | 49 | 24 | 98.79% | 0.095236 | 0.096534 | 40.8378 | 39.4896 | 129.8574 | 20.9717 | 98.79% | 3997.7715 | 99.45% | 99.58% | 84.98% |  |  | 99.45% | 1.0133
2020-12-22 | 177.4939 | 160.3289 | 160.3289 | 148.8773 | 135.9005 | 14.0824 | 14.0824 | 3469.469 | 1039.4703 | 303.1788 | 612.8677 | 20.7185 | 9.496 | 20.2329 | 44.9441 | 9602.9477 | 367.3694 |  |  | 24.6694 | 1.0113 | 15.8104 | 4082.3367 | 2126.8199 | 1955.5168 | 916.0465 | 17.165 | 11.4515 | 12.9307 | 14.023 | 11.1372 | 6.4967 | 3577.5671 | 7614.1998 | 11358.6267 | 2424.9749 | 5097.1881 | 9238.1315 | 0.099345 | 0.097826 | 0.079793 | 16.8765 | 10.7029 | 12.2279 | 9.5521 | 21.377 | 58.5801 | 142.7516 | 115.136 | 82.3406 | 99.61% | 99.6% | 99.51% | 99.61% | 99.58% | 99.37% | 120.7907 | 122.6673 | 150.3886 |  |  |  | 30.2188 | 24 | 14 | 2357.0625 | 1152 | 336 | 3845.0625 | 121.7742 | 11 | 23.4375 | 52.0625 | 24 | 98.79% | 0.095731 | 0.097181 | 41.5473 | 39.8073 | 130.0161 | 20.938 | 98.79% | 3820.9496 | 99.46% | 99.56% | 84.99% |  |  | 99.45% | 1.0113
2020-12-21 | 174.4951 | 157.4449 | 157.4449 | 145.918 | 133.1927 | 14.0279 | 14.0279 | 3446.3114 | 1016.4236 | 296.4569 | 608.9597 | 20.135 | 9.2285 | 20.974 | 52.8544 | 9111.2785 | 358.4233 |  |  | 24.6962 | 1.0104 | 16.4454 | 4055.271 | 2133.4308 | 1921.8402 | 905.4166 | 17.0502 | 11.5269 | 12.933 | 14.0666 | 10.8903 | 6.3526 | 3455.0117 | 7310.0738 | 10843.0708 | 2327.9648 | 4909.8649 | 8845.6078 | 0.10127 | 0.097196 | 0.078695 | 17.0198 | 11.0275 | 12.4066 | 9.6911 | 22.4748 | 70.288 | 140.3484 | 113.2091 | 81.5637 | 99.6% | 99.57% | 99.4% | 99.58% | 99.54% | 99.21% | 118.4974 | 123.462 | 152.4867 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 119.0792 | 11 | 25 | 63 | 24 | 98.77% | 0.096353 | 0.098125 | 41.51 | 40.4538 | 128.1064 | 21.1393 | 98.77% | 3650.1043 | 99.45% | 99.51% | 84.98% |  |  | 99.45% | 1.0104
2020-12-20 | 175.1151 | 157.8512 | 157.8512 | 146.3195 | 133.3177 | 13.9857 | 13.9857 | 3468.5738 | 1022.9895 | 298.3719 | 612.2446 | 19.9384 | 9.1384 | 20.7691 | 52.3382 | 9057.4618 | 361.829 |  |  | 24.6155 | 1.0132 | 16.2848 | 4080.8184 | 2147.2123 | 1933.606 | 910.6165 | 17.2639 | 11.5317 | 12.9633 | 14.1574 | 10.9606 | 6.3937 | 3463.8156 | 7331.745 | 10879.2991 | 2333.6192 | 4923.2717 | 8873.3874 | 0.10182 | 0.097767 | 0.079263 | 17.073 | 10.9335 | 12.3318 | 9.6616 | 22.3996 | 70.0242 | 140.8751 | 113.5872 | 81.7277 | 99.61% | 99.58% | 99.41% | 99.59% | 99.55% | 99.21% | 117.8539 | 122.741 | 151.3954 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 119.3512 | 11 | 25 | 63 | 24 | 98.79% | 0.096914 | 0.098685 | 41.7588 | 40.3383 | 128.6482 | 21.0693 | 98.79% | 3659.9484 | 99.46% | 99.51% | 85% |  |  | 99.45% | 1.0132
2020-12-19 | 174.4729 | 157.4849 | 157.4849 | 146.147 | 133.4072 | 13.8308 | 13.8308 | 3438.9499 | 1014.2525 | 295.8236 | 607.8525 | 20.5636 | 9.425 | 21.4204 | 53.9794 | 9509.7418 | 357.1787 |  |  | 24.6262 | 1.0128 | 16.7954 | 4046.8024 | 2128.8738 | 1917.9287 | 903.6762 | 16.9879 | 11.3379 | 12.7462 | 14.0365 | 10.867 | 6.3391 | 3586.1954 | 7587.1663 | 11253.3432 | 2416.3627 | 5096.1515 | 9180.6234 | 0.10146 | 0.097736 | 0.079941 | 17.0105 | 10.8794 | 12.262 | 9.5377 | 22.1196 | 69.1817 | 140.1134 | 112.6115 | 80.3131 | 99.61% | 99.58% | 99.41% | 99.61% | 99.57% | 99.25% | 118.2699 | 122.78 | 150.1116 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 119.5756 | 11 | 25 | 63 | 24 | 98.79% | 0.096827 | 0.098512 | 41.0721 | 40.1518 | 127.5582 | 20.8052 | 98.79% | 3788.5871 | 99.46% | 99.54% | 84.98% |  |  | 99.46% | 1.0128
2020-12-18 | 173.0839 | 156.0045 | 156.0045 | 144.5924 | 131.8467 | 13.9386 | 13.9386 | 3453.9289 | 1018.6703 | 297.1122 | 609.919 | 20.7329 | 9.5026 | 21.5968 | 54.4238 | 9368.1618 | 356.9213 |  |  | 24.7134 | 1.0098 | 16.9337 | 4063.8479 | 2138.1465 | 1925.7015 | 907.0312 | 17.0794 | 11.4121 | 12.8468 | 14.0977 | 10.9143 | 6.3667 | 3521.436 | 7452.042 | 11055.6718 | 2372.6216 | 5004.6798 | 9018.1669 | 0.10257 | 0.098895 | 0.080908 | 16.9958 | 10.8861 | 12.2926 | 9.807 | 22.7405 | 71.1054 | 138.79 | 111.4445 | 79.4623 | 99.6% | 99.57% | 99.4% | 99.59% | 99.55% | 99.21% | 116.9919 | 121.3407 | 148.3174 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 117.8695 | 11 | 25 | 63 | 24 | 98.76% | 0.097929 | 0.099623 | 41.3383 | 40.1745 | 126.4023 | 21.3894 | 98.76% | 3720.5567 | 99.44% | 99.51% | 84.99% |  |  | 99.44% | 1.0098
2020-12-17 | 172.9677 | 156.0428 | 156.0428 | 144.8231 | 131.1955 | 13.8884 | 13.8884 | 3435.0963 | 1013.116 | 295.4922 | 608.2712 | 21.41 | 9.8129 | 22.302 | 56.2011 | 9324.2873 | 351.8462 |  |  | 24.6225 | 1.0129 | 17.4867 | 4043.3675 | 2126.4882 | 1916.8793 | 903.7633 | 16.925 | 11.2197 | 12.7127 | 14.0208 | 10.8548 | 6.332 | 3500.78 | 7400.1433 | 10967.7583 | 2359.464 | 4972.9137 | 8951.1988 | 0.10227 | 0.098355 | 0.08053 | 16.9665 | 10.7714 | 12.2236 | 10.1596 | 23.5773 | 73.8019 | 138.8686 | 111.7915 | 79.6459 | 99.58% | 99.55% | 99.37% | 99.57% | 99.53% | 99.18% | 117.3355 | 122.007 | 149.0125 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 117.8758 | 11 | 25 | 63 | 24 | 98.71% | 0.097539 | 0.099246 | 40.8573 | 39.9615 | 126.5936 | 22.1744 | 98.71% | 3697.282 | 99.42% | 99.49% | 84.96% |  |  | 99.42% | 1.0129
2020-12-16 | 174.4731 | 157.2914 | 157.2914 | 145.9075 | 132.7569 | 13.6572 | 13.6572 | 3468.5872 | 1022.9935 | 298.3731 | 611.7987 | 19.0264 | 8.7204 | 19.8191 | 49.9442 | 9210.3493 | 358.1091 |  |  | 24.7092 | 1.0099 | 15.5399 | 4080.3859 | 2147.2206 | 1933.1653 | 910.1718 | 17.1817 | 11.3839 | 12.8618 | 14.1575 | 10.9606 | 6.3937 | 3442.9958 | 7290.4974 | 10821.7018 | 2319.2826 | 4894.5093 | 8824.8415 | 0.10164 | 0.097471 | 0.07894 | 16.9953 | 10.7985 | 12.2461 | 9.2471 | 21.4321 | 66.9747 | 140.6722 | 113.5688 | 81.8005 | 99.62% | 99.6% | 99.43% | 99.6% | 99.56% | 99.24% | 118.0605 | 123.1135 | 152.0147 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 119.1063 | 11 | 25 | 63 | 24 | 98.84% | 0.096675 | 0.098459 | 41.4274 | 40.0399 | 128.5503 | 20.1601 | 98.84% | 3638.4144 | 99.48% | 99.53% | 85.01% |  |  | 99.47% | 1.0099
2020-12-15 | 173.3968 | 156.2304 | 156.2304 | 144.7246 | 131.6158 | 13.6925 | 13.6925 | 3466.5116 | 1022.3813 | 298.1945 | 612.0478 | 19.0451 | 8.729 | 19.8386 | 49.9934 | 8980.6953 | 355.6832 |  |  | 24.7106 | 1.0099 | 15.5552 | 4078.5594 | 2145.9358 | 1932.6236 | 910.2423 | 17.1664 | 11.5058 | 12.8943 | 14.149 | 10.9541 | 6.3899 | 3372.5821 | 7138.373 | 10591.8879 | 2272.1411 | 4793.5207 | 8639.1746 | 0.10221 | 0.097971 | 0.079149 | 16.9903 | 10.9168 | 12.2732 | 9.4422 | 21.8911 | 68.4374 | 139.8041 | 112.9166 | 81.5318 | 99.62% | 99.59% | 99.42% | 99.58% | 99.54% | 99.21% | 117.4074 | 122.4853 | 151.6129 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 117.9464 | 11 | 25 | 63 | 24 | 98.81% | 0.097163 | 0.098975 | 41.5666 | 40.1803 | 127.8536 | 20.591 | 98.81% | 3563.4756 | 99.47% | 99.51% | 84.99% |  |  | 99.46% | 1.0099
2020-12-14 | 170.5818 | 153.5033 | 153.5033 | 142.0807 | 128.998 | 13.8179 | 13.8179 | 3455.502 | 1019.1342 | 297.2475 | 608.9895 | 18.8167 | 8.6243 | 19.6007 | 49.3939 | 8472.4105 | 348.7071 |  |  | 24.9095 | 1.0031 | 15.3687 | 4064.4915 | 2139.1203 | 1925.3712 | 906.2369 | 17.0785 | 11.4226 | 12.879 | 14.1041 | 10.9193 | 6.3696 | 3196.4265 | 6769.0153 | 10048.8596 | 2153.2444 | 4544.1741 | 8194.0754 | 0.10289 | 0.098364 | 0.078881 | 16.9936 | 10.9025 | 12.3444 | 9.7466 | 22.5894 | 70.5834 | 137.5015 | 111.3512 | 80.998 | 99.6% | 99.57% | 99.4% | 99.55% | 99.5% | 99.14% | 116.6291 | 121.9958 | 152.1274 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 115.1565 | 11 | 25 | 63 | 24 | 98.76% | 0.0976 | 0.09949 | 41.3801 | 40.2406 | 126.0732 | 21.2483 | 98.76% | 3378.0448 | 99.44% | 99.47% | 85.02% |  |  | 99.44% | 1.0031
2020-12-13 | 168.4898 | 151.8335 | 151.8335 | 140.6168 | 127.9922 | 14.0419 | 14.0419 | 3396.7644 | 1001.8107 | 292.1948 | 600.1302 | 16.1682 | 7.4104 | 16.8418 | 42.4414 | 8597.5334 | 338.3602 |  |  | 24.9109 | 1.003 | 13.2055 | 3996.8946 | 2102.7589 | 1894.1357 | 892.325 | 16.6563 | 11.2167 | 12.5855 | 13.8643 | 10.7337 | 6.2613 | 3246.6684 | 6872.7855 | 10198.3821 | 2187.0308 | 4614.8277 | 8317.9668 | 0.10284 | 0.098598 | 0.079614 | 16.9924 | 10.9673 | 12.3402 | 8.1048 | 18.7869 | 58.7269 | 135.2217 | 109.1933 | 78.885 | 99.66% | 99.64% | 99.49% | 99.63% | 99.59% | 99.29% | 116.684 | 121.7059 | 150.7278 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 113.9612 | 11 | 25 | 63 | 24 | 98.95% | 0.097767 | 0.099592 | 40.4586 | 40.2999 | 123.6842 | 17.6721 | 98.95% | 3430.4554 | 99.53% | 99.56% | 84.99% |  |  | 99.54% | 1.003
2020-12-12 | 170.073 | 153.4407 | 153.4407 | 142.4067 | 129.6291 | 14.0495 | 14.0495 | 3410.7994 | 1005.95 | 293.4021 | 602.6339 | 18.149 | 8.3183 | 18.9052 | 47.6412 | 9072.5923 | 343.3314 |  |  | 25.0256 | 0.99913 | 14.8233 | 4013.4332 | 2111.4472 | 1901.986 | 896.0359 | 16.6323 | 11.0341 | 12.5943 | 13.9216 | 10.778 | 6.2872 | 3406.2942 | 7209.2043 | 10695.9278 | 2294.7946 | 4841.2825 | 8724.4941 | 0.10207 | 0.098109 | 0.079936 | 16.863 | 10.7219 | 12.2721 | 8.6724 | 20.1066 | 62.8641 | 136.275 | 109.7623 | 78.5841 | 99.64% | 99.61% | 99.45% | 99.62% | 99.58% | 99.28% | 117.5668 | 122.3129 | 150.1194 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 115.5799 | 11 | 25 | 63 | 24 | 98.88% | 0.097261 | 0.098998 | 40.2606 | 39.857 | 124.2903 | 18.9128 | 98.88% | 3598.9249 | 99.5% | 99.56% | 84.98% |  |  | 99.51% | 0.99913
2020-12-11 | 170.4183 | 153.6688 | 153.6688 | 142.4962 | 129.8002 | 13.9582 | 13.9582 | 3424.606 | 1010.022 | 294.5898 | 604.1183 | 19.9635 | 9.1499 | 20.7953 | 52.4041 | 9191.3291 | 344.5056 |  |  | 24.9569 | 1.0015 | 16.3053 | 4028.7243 | 2119.9942 | 1908.7301 | 898.708 | 16.7495 | 11.1726 | 12.5727 | 13.978 | 10.8217 | 6.3126 | 3452.3093 | 7308.8508 | 10847.3546 | 2325.754 | 4907.3469 | 8846.4517 | 0.10255 | 0.0988 | 0.080822 | 16.8874 | 10.802 | 12.2003 | 9.4727 | 21.9586 | 68.6318 | 136.5024 | 109.6916 | 78.2198 | 99.61% | 99.58% | 99.41% | 99.59% | 99.55% | 99.22% | 117.0147 | 121.4574 | 148.4741 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 115.8823 | 11 | 25 | 63 | 24 | 98.78% | 0.097874 | 0.099576 | 40.4948 | 39.8897 | 124.366 | 20.6547 | 98.78% | 3648.0657 | 99.45% | 99.52% | 85% |  |  | 99.46% | 1.0015
2020-12-10 | 170.2801 | 153.3992 | 153.3992 | 142.2568 | 129.3628 | 14.1221 | 14.1221 | 3443.4828 | 1015.5894 | 296.2136 | 608.9835 | 20.8954 | 9.577 | 21.766 | 54.8504 | 9269.9957 | 348.8334 |  |  | 25.1305 | 0.99557 | 17.0664 | 4052.4662 | 2131.6798 | 1920.7864 | 905.197 | 16.8808 | 11.1425 | 12.6106 | 14.055 | 10.8813 | 6.3474 | 3487.563 | 7376.0276 | 10937.0964 | 2350.1953 | 4955.2644 | 8923.9656 | 0.10288 | 0.099352 | 0.081706 | 16.867 | 10.6669 | 12.0997 | 9.8078 | 22.7521 | 71.1828 | 136.0144 | 109.0384 | 77.3421 | 99.59% | 99.56% | 99.39% | 99.58% | 99.54% | 99.2% | 116.6436 | 120.783 | 146.8674 |  |  |  | 31 | 24 | 14 | 2418 | 1152 | 336 | 3906 | 115.2391 | 11 | 25 | 63 | 24 | 98.74% | 0.098362 | 0.10002 | 40.6339 | 39.6337 | 123.8098 | 21.3993 | 98.74% | 3683.9962 | 99.43% | 99.51% | 84.97% |  |  | 99.44% | 0.99557
2020-12-09 | 168.5974 | 151.7544 | 151.7544 | 140.6565 | 128.0037 | 14.0586 | 14.0586 | 3429.1673 | 1002.6066 | 303.7428 | 606.1594 | 21.1627 | 9.7388 | 20.1805 | 48.4871 | 9224.7882 | 343.3104 |  |  | 25.4096 | 0.98619 | 16.2239 | 4035.3267 | 2122.8179 | 1912.5088 | 909.9022 | 16.8429 | 11.0979 | 12.5996 | 13.9966 | 10.7422 | 6.5088 | 3512.2604 | 7360.1272 | 11023.9465 | 2366.7714 | 4970.2306 | 8946.6785 | 0.10275 | 0.098642 | 0.084703 | 16.9372 | 10.6444 | 12.0666 | 9.7694 | 20.5667 | 63.7535 | 134.3321 | 107.3966 | 75.7806 | 99.59% | 99.59% | 99.46% | 99.59% | 99.59% | 99.29% | 116.783 | 121.652 | 141.671 |  |  |  | 30.1059 | 23.1059 | 14 | 2348.2588 | 1109.0824 | 336 | 3793.3412 | 114.0327 | 11.0824 | 22.9647 | 55.1765 | 24.0824 | 98.73% | 0.09855 | 0.099953 | 40.5404 | 39.6483 | 122.0547 | 21.2251 | 98.73% | 3710.7843 | 99.43% | 99.54% | 84.98% |  |  | 99.44% | 0.98619
2020-12-08 | 170.4481 | 153.4766 | 153.4766 | 142.301 | 129.5772 | 14.12 | 14.12 | 3452.9441 | 1020.8315 | 304.2624 | 610.2895 | 21.6997 | 10.4159 | 19.0958 | 38.1916 | 9309.2496 | 349.7544 |  |  | 25.4709 | 0.98414 | 15.4295 | 4063.2336 | 2127.8501 | 1935.3835 | 914.552 | 16.9715 | 11.1756 | 12.6674 | 14.0298 | 10.9375 | 6.5199 | 3469.02 | 7319.858 | 10950.1638 | 2344.4921 | 4923.9235 | 8892.6286 | 0.1014 | 0.098531 | 0.082743 | 16.8502 | 10.5641 | 12.0269 | 10.551 | 19.9597 | 50.5029 | 136.172 | 109.2446 | 77.5469 | 99.56% | 99.61% | 99.57% | 99.55% | 99.59% | 99.43% | 118.3483 | 121.789 | 145.0268 |  |  |  | 31.759 | 24.759 | 14.759 | 2477.2048 | 1188.4337 | 354.2169 | 4019.8554 | 115.412 | 12 | 22 | 44 | 25 | 98.69% | 0.097495 | 0.098905 | 40.8146 | 39.4413 | 123.9344 | 22.0277 | 98.69% | 3684.0785 | 99.41% | 99.55% | 84.98% |  |  | 99.42% | 0.98414
2020-12-07 | 171.1468 | 153.9707 | 153.9707 | 142.5671 | 129.3198 | 14.0828 | 14.0828 | 3462.7008 | 1024.4677 | 307.3403 | 611.9456 | 20.1405 | 9.6674 | 17.7236 | 35.4472 | 8604.4709 | 351.9981 |  |  | 25.0663 | 0.99775 | 14.3391 | 4074.6464 | 2130.8928 | 1943.7536 | 919.2859 | 17.1761 | 11.4036 | 12.9151 | 14.0498 | 10.9764 | 6.5859 | 3241.0608 | 6833.202 | 10247.2705 | 2192.2473 | 4598.6927 | 8310.9173 | 0.1019 | 0.098415 | 0.081645 | 16.9693 | 10.7057 | 12.1854 | 10.6329 | 20.1816 | 51.3628 | 137.5631 | 111.2813 | 80.4833 | 99.56% | 99.61% | 99.57% | 99.51% | 99.56% | 99.38% | 117.7581 | 121.9329 | 146.9784 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 115.3192 | 12 | 22 | 44 | 25 | 98.7% | 0.097546 | 0.099073 | 41.4948 | 39.8604 | 125.927 | 22.2139 | 98.7% | 3447.2906 | 99.42% | 99.51% | 84.98% |  |  | 99.42% | 0.99775
2020-12-06 | 169.5002 | 152.6313 | 152.6313 | 141.4524 | 128.8942 | 14.0194 | 14.0194 | 3431.918 | 1015.3604 | 304.6081 | 605.6603 | 20.2787 | 9.7338 | 17.8453 | 35.6906 | 8806.1511 | 344.1227 |  |  | 25.0721 | 0.99755 | 14.4375 | 4037.5783 | 2111.9495 | 1925.6288 | 910.2684 | 16.8689 | 11.179 | 12.6912 | 13.9249 | 10.8789 | 6.5273 | 3306.0542 | 6973.892 | 10463.3603 | 2235.8698 | 4691.9914 | 8483.9633 | 0.1022 | 0.09897 | 0.082514 | 16.8977 | 10.6458 | 12.156 | 10.4017 | 19.7352 | 50.2004 | 135.9157 | 109.6517 | 78.9125 | 99.56% | 99.62% | 99.58% | 99.53% | 99.58% | 99.41% | 117.4144 | 121.2487 | 145.4307 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 114.693 | 12 | 22 | 44 | 25 | 98.72% | 0.098018 | 0.099498 | 40.7391 | 39.6995 | 124.1132 | 21.7234 | 98.72% | 3517.0975 | 99.42% | 99.53% | 85% |  |  | 99.43% | 0.99755
2020-12-05 | 172.9021 | 155.8352 | 155.8352 | 144.6171 | 131.6508 | 14.1634 | 14.1634 | 3468.9469 | 1026.3156 | 307.8947 | 613.2415 | 21.2494 | 10.1997 | 18.6995 | 37.399 | 9407.2896 | 355.915 |  |  | 25.1938 | 0.99343 | 15.1286 | 4082.1883 | 2134.7365 | 1947.4518 | 921.1362 | 17.0669 | 11.2181 | 12.8605 | 14.0752 | 10.9962 | 6.5977 | 3515.2845 | 7411.1254 | 11113.307 | 2377.6817 | 4987.7172 | 9013.5796 | 0.10106 | 0.098222 | 0.082873 | 16.8143 | 10.501 | 12.0966 | 10.3173 | 19.5824 | 49.8401 | 138.3678 | 111.2177 | 79.0896 | 99.57% | 99.63% | 99.59% | 99.57% | 99.61% | 99.45% | 118.7471 | 122.1719 | 144.7992 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 117.4725 | 12 | 22 | 44 | 25 | 98.74% | 0.09724 | 0.098603 | 41.1455 | 39.4119 | 125.9352 | 21.5547 | 98.74% | 3738.8666 | 99.43% | 99.56% | 84.98% |  |  | 99.44% | 0.99343
2020-12-04 | 173.1589 | 156.1353 | 156.1353 | 145.0101 | 132.1286 | 14.1905 | 14.1905 | 3470.8647 | 1026.883 | 308.0649 | 611.2049 | 21.9215 | 10.5223 | 19.2909 | 38.5818 | 9624.2797 | 357.5518 |  |  | 25.2931 | 0.99009 | 15.6071 | 4082.0696 | 2135.9167 | 1946.1529 | 919.2698 | 17.0237 | 11.1252 | 12.6801 | 14.083 | 11.0023 | 6.6014 | 3607.8279 | 7616.4527 | 11435.9183 | 2439.431 | 5122.0384 | 9268.866 | 0.10081 | 0.098255 | 0.083551 | 16.7776 | 10.4313 | 11.9726 | 10.345 | 19.6167 | 49.8597 | 138.312 | 110.8684 | 78.2274 | 99.57% | 99.62% | 99.58% | 99.58% | 99.62% | 99.46% | 119.034 | 122.1318 | 143.6245 |  |  |  | 32 | 25 | 15 | 2496 | 1200 | 360 | 4056 | 117.9503 | 12 | 22 | 44 | 25 | 98.73% | 0.097232 | 0.098523 | 40.829 | 39.1815 | 125.6388 | 21.594 | 98.73% | 3839.2647 | 99.43% | 99.57% | 85.03% |  |  | 99.43% | 0.99009
2020-12-03 | 172.784 | 155.7094 | 155.7094 | 144.5278 | 131.7913 | 13.9042 | 13.9042 | 3469.8584 | 1000.7129 | 311.2368 | 613.149 | 22.2221 | 10.6666 | 19.5555 | 39.1109 | 9616.9076 | 355.9918 |  |  | 25.2801 | 0.99053 | 15.7815 | 4083.0074 | 2157.9087 | 1925.0987 | 924.3858 | 17.0745 | 11.1816 | 12.6126 | 14.228 | 10.7219 | 6.6694 | 3675.7319 | 7633.8007 | 11488.895 | 2469.968 | 5181.074 | 9300.145 | 0.10209 | 0.096193 | 0.084749 | 16.9124 | 10.5723 | 11.8269 | 10.4685 | 19.1665 | 50.9144 | 138.046 | 110.4069 | 77.9502 | 99.57% | 99.62% | 99.58% | 99.58% | 99.63% | 99.45% | 117.5426 | 124.7492 | 141.5948 |  |  |  | 32 | 24.1146 | 15 | 2496 | 1157.5 | 360 | 4013.5 | 117.8523 | 12 | 22 | 44 | 25 | 98.72% | 0.097429 | 0.098834 | 40.8687 | 39.3115 | 125.3881 | 21.7504 | 98.72% | 3864.5037 | 99.42% | 99.57% | 84.98% |  |  | 99.43% | 0.99053
2020-12-02 | 170.8955 | 153.7771 | 153.7771 | 142.5835 | 130.0361 | 13.9454 | 13.9454 | 3473.9471 | 998.4998 | 312.0312 | 612.9783 | 22.5842 | 10.8404 | 19.8741 | 39.7482 | 9526.4375 | 351.6397 |  |  | 25.6561 | 0.97798 | 16.0334 | 4086.9254 | 2163.4162 | 1923.5093 | 925.0095 | 17.1185 | 11.1936 | 12.6754 | 14.2643 | 10.6982 | 6.6864 | 3644.3636 | 7556.8121 | 11383.3068 | 2446.5616 | 5133.3237 | 9210.2277 | 0.10242 | 0.096281 | 0.085466 | 16.946 | 10.589 | 11.8806 | 10.6318 | 19.368 | 51.7191 | 136.2123 | 108.6676 | 76.512 | 99.56% | 99.61% | 99.57% | 99.57% | 99.62% | 99.44% | 117.17 | 124.6347 | 140.4069 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 116.0415 | 12 | 22 | 44 | 25 | 98.69% | 0.097741 | 0.09913 | 40.9875 | 39.4156 | 123.6564 | 22.0686 | 98.69% | 3826.3195 | 99.41% | 99.56% | 85% |  |  | 99.42% | 0.97798
2020-12-01 | 170.1042 | 153.1166 | 153.1166 | 142.0562 | 129.1479 | 14.0681 | 14.0681 | 3468.6456 | 996.976 | 311.555 | 612.7245 | 22.4869 | 10.7937 | 19.7885 | 39.577 | 9338.5707 | 349.6259 |  |  | 25.6048 | 0.97968 | 15.9644 | 4081.3701 | 2160.1146 | 1921.2555 | 924.2795 | 16.9876 | 11.0604 | 12.672 | 14.2425 | 10.6819 | 6.6762 | 3581.9859 | 7424.3576 | 11179.3328 | 2404.9967 | 5044.5313 | 9047.1148 | 0.10292 | 0.096544 | 0.085501 | 16.8493 | 10.4795 | 11.8888 | 10.7713 | 19.6282 | 52.4358 | 135.5713 | 108.3946 | 76.4963 | 99.55% | 99.61% | 99.56% | 99.55% | 99.61% | 99.42% | 116.5942 | 124.2955 | 140.3486 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 115.0678 | 12 | 22 | 44 | 25 | 98.67% | 0.098093 | 0.099524 | 40.72 | 39.2175 | 123.2061 | 22.3643 | 98.67% | 3760.2627 | 99.4% | 99.55% | 84.99% |  |  | 99.41% | 0.97968
2020-11-30 | 167.997 | 150.8899 | 150.8899 | 139.5259 | 126.6867 | 14.151 | 14.151 | 3472.46 | 998.0723 | 311.8976 | 613.2556 | 21.7072 | 10.4194 | 19.1023 | 38.2046 | 8720.3079 | 344.9245 |  |  | 25.58 | 0.98051 | 15.4108 | 4085.7156 | 2162.4901 | 1923.2256 | 925.1532 | 17.107 | 11.364 | 12.8217 | 14.2582 | 10.6936 | 6.6835 | 3378.3633 | 7002.3959 | 10544.3359 | 2268.3329 | 4757.7939 | 8533.0666 | 0.10433 | 0.097661 | 0.085684 | 16.941 | 10.751 | 12.0127 | 11.0456 | 20.1285 | 53.771 | 134.0028 | 107.3634 | 76.4809 | 99.54% | 99.6% | 99.55% | 99.51% | 99.58% | 99.37% | 115.0221 | 122.8746 | 140.0487 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 112.5074 | 12 | 22 | 44 | 25 | 98.64% | 0.099211 | 0.10074 | 41.2928 | 39.7048 | 122.1579 | 22.934 | 98.64% | 3546.5673 | 99.39% | 99.51% | 84.99% |  |  | 99.4% | 0.98051
2020-11-29 | 167.6783 | 150.4605 | 150.4605 | 138.9937 | 126.0682 | 13.9789 | 13.9789 | 3473.8035 | 998.4585 | 312.0183 | 614.1453 | 21.428 | 10.2854 | 18.8567 | 37.7133 | 8553.1524 | 343.43 |  |  | 25.4534 | 0.98472 | 15.2126 | 4087.9488 | 2163.3267 | 1924.6221 | 926.1636 | 17.2179 | 11.4667 | 12.9053 | 14.2637 | 10.6978 | 6.6861 | 3326.5107 | 6892.3551 | 10374.8756 | 2233.7523 | 4684.0027 | 8397.5541 | 0.10484 | 0.098065 | 0.085781 | 17.0353 | 10.8344 | 12.0687 | 11.1243 | 20.2773 | 54.189 | 133.9731 | 107.4224 | 76.7528 | 99.54% | 99.6% | 99.55% | 99.5% | 99.57% | 99.35% | 114.4598 | 122.3683 | 139.8905 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 112.157 | 12 | 22 | 44 | 25 | 98.64% | 0.099623 | 0.10118 | 41.5899 | 39.9384 | 122.2677 | 23.103 | 98.64% | 3491.6507 | 99.39% | 99.5% | 84.98% |  |  | 99.4% | 0.98472
2020-11-28 | 167.3916 | 150.335 | 150.335 | 139.1015 | 126.1715 | 13.8636 | 13.8636 | 3459.7434 | 994.4173 | 310.7554 | 610.0547 | 22.6686 | 10.8809 | 19.9483 | 39.8967 | 8681.2854 | 340.4187 |  |  | 25.4523 | 0.98476 | 16.0933 | 4069.7981 | 2154.5707 | 1915.2274 | 920.8101 | 17.0566 | 11.2335 | 12.7223 | 14.206 | 10.6545 | 6.659 | 3368.037 | 6983.7631 | 10520.8949 | 2261.275 | 4744.0791 | 8512.1015 | 0.1046 | 0.097843 | 0.085819 | 16.9924 | 10.697 | 12.0078 | 11.5785 | 21.0946 | 56.3279 | 133.7478 | 107.2341 | 76.412 | 99.52% | 99.58% | 99.53% | 99.49% | 99.56% | 99.34% | 114.7273 | 122.6455 | 139.83 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 112.3205 | 12 | 22 | 44 | 25 | 98.57% | 0.099431 | 0.10097 | 41.0123 | 39.6971 | 121.9676 | 24.0348 | 98.57% | 3536.3468 | 99.36% | 99.49% | 85.01% |  |  | 99.37% | 0.98476
2020-11-27 | 167.4075 | 150.4325 | 150.4325 | 139.2728 | 126.3552 | 13.8862 | 13.8862 | 3449.8265 | 991.5669 | 309.8647 | 610.2605 | 21.3545 | 10.2502 | 18.792 | 37.5839 | 8796.0691 | 340.4235 |  |  | 25.3622 | 0.98777 | 15.1604 | 4060.0871 | 2148.395 | 1911.6921 | 920.1252 | 16.975 | 11.1597 | 12.7151 | 14.1652 | 10.6239 | 6.64 | 3408.711 | 7061.8351 | 10628.4546 | 2288.9528 | 4799.498 | 8603.4674 | 0.1047 | 0.098017 | 0.086188 | 16.9674 | 10.6504 | 12.0066 | 10.7774 | 19.646 | 52.5089 | 133.6403 | 107.063 | 76.0984 | 99.55% | 99.61% | 99.56% | 99.53% | 99.59% | 99.39% | 114.6139 | 122.4271 | 139.2304 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 112.4839 | 12 | 22 | 44 | 25 | 98.67% | 0.099599 | 0.10112 | 40.8497 | 39.6245 | 121.7586 | 22.3839 | 98.67% | 3577.7186 | 99.4% | 99.53% | 84.97% |  |  | 99.41% | 0.98777
2020-11-26 | 168.1579 | 151.2173 | 151.2173 | 140.1272 | 127.2421 | 14.115 | 14.115 | 3469.6326 | 997.2597 | 311.6437 | 613.5018 | 22.604 | 10.8499 | 19.8916 | 39.7831 | 9249.5273 | 345.3449 |  |  | 25.813 | 0.97281 | 16.0475 | 4083.1345 | 2160.7293 | 1922.4052 | 925.1455 | 16.9406 | 11.0901 | 12.5592 | 14.2466 | 10.6849 | 6.6781 | 3559.71 | 7375.454 | 11101.7921 | 2390.314 | 5012.3434 | 8986.05 | 0.10368 | 0.097513 | 0.086807 | 16.7904 | 10.4965 | 11.7641 | 10.8205 | 19.7233 | 52.7095 | 133.6753 | 106.595 | 74.8383 | 99.55% | 99.6% | 99.56% | 99.55% | 99.61% | 99.41% | 115.7434 | 123.0611 | 138.2381 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 113.1803 | 12 | 22 | 44 | 25 | 98.66% | 0.099005 | 0.10039 | 40.5899 | 39.051 | 121.3882 | 22.472 | 98.66% | 3736.3826 | 99.4% | 99.54% | 84.97% |  |  | 99.41% | 0.97281
2020-11-25 | 167.9842 | 151.0765 | 151.0765 | 140.1312 | 127.5357 | 14.2558 | 14.2558 | 3469.8418 | 997.3198 | 311.6624 | 613.0729 | 24.2265 | 11.6287 | 21.3193 | 42.6386 | 9569.5594 | 343.6757 |  |  | 25.993 | 0.9669 | 17.1994 | 4082.9147 | 2160.8596 | 1922.0551 | 924.7353 | 16.9077 | 10.9453 | 12.5549 | 14.2474 | 10.6856 | 6.6785 | 3659.7172 | 7583.7007 | 11417.2836 | 2457.4923 | 5153.4717 | 9240.5382 | 0.10354 | 0.097759 | 0.087751 | 16.7603 | 10.3636 | 11.7696 | 11.2123 | 20.4366 | 54.6069 | 133.0453 | 105.6873 | 73.5882 | 99.53% | 99.59% | 99.54% | 99.54% | 99.6% | 99.41% | 115.8943 | 122.7507 | 136.7506 |  |  |  | 32 | 24 | 15 | 2496 | 1152 | 360 | 4008 | 113.265 | 12 | 22 | 44 | 25 | 98.6% | 0.099165 | 0.10046 | 40.4079 | 38.8935 | 120.4813 | 23.2843 | 98.6% | 3841.6402 | 99.37% | 99.54% | 84.98% |  |  | 99.39% | 0.9669
2020-11-24 | 166.37 | 149.3708 | 149.3708 | 138.245 | 125.6473 | 14.3188 | 14.3188 | 3469.4039 | 997.4477 | 305.0817 | 613.806 | 23.5992 | 11.5686 | 21.2092 | 42.4183 | 9160.7861 | 341.4645 |  |  | 26.0474 | 0.96513 | 17.053 | 4083.2098 | 2166.8745 | 1916.3353 | 918.8877 | 16.9993 | 11.1257 | 12.6609 | 14.2871 | 10.6869 | 6.5375 | 3540.7778 | 7361.2508 | 10998.9505 | 2373.7114 | 4993.1553 | 8937.9367 | 0.10467 | 0.098579 | 0.086254 | 16.8739 | 10.5989 | 11.9285 | 11.559 | 20.9479 | 54.8772 | 131.7408 | 104.6293 | 73.1497 | 99.51% | 99.58% | 99.53% | 99.51% | 99.58% | 99.39% | 114.6499 | 121.7298 | 139.1234 |  |  |  | 32.7812 | 24.5208 | 15 | 2556.9375 | 1177 | 360 | 4093.9375 | 111.2406 | 12 | 22 | 44 | 24.4792 | 98.59% | 0.099773 | 0.1013 | 40.7858 | 39.4012 | 119.5361 | 23.478 | 98.59% | 3704.0215 | 99.36% | 99.51% | 84.97% |  |  | 99.39% | 0.96513
2020-11-23 | 164.3723 | 147.361 | 147.361 | 136.2482 | 123.3771 | 14.2948 | 14.2948 | 3470.3774 | 998.3935 | 287.9981 | 613.0496 | 22.8626 | 11.9283 | 21.8685 | 43.7371 | 8700.8939 | 336.6601 |  |  | 26.041 | 0.96534 | 17.4277 | 4083.427 | 2183.9858 | 1899.4412 | 901.0477 | 17.0113 | 11.1129 | 12.7271 | 14.3999 | 10.6971 | 6.1714 | 3410.5803 | 7165.3956 | 10511.0047 | 2275.4167 | 4831.774 | 8625.5899 | 0.10672 | 0.099809 | 0.082049 | 16.9564 | 10.7842 | 12.2125 | 12.5341 | 22.3466 | 55.361 | 130.2544 | 103.4602 | 72.6085 | 99.48% | 99.55% | 99.49% | 99.45% | 99.54% | 99.36% | 112.4437 | 120.2295 | 146.2539 |  |  |  | 35 | 26 | 15 | 2730 | 1248 | 360 | 4338 | 109.0974 | 12 | 22 | 44 | 23 | 98.56% | 0.10056 | 0.10268 | 40.8513 | 39.9531 | 118.5408 | 23.8253 | 98.56% | 3537.8409 | 99.35% | 99.46% | 84.99% |  |  | 99.38% | 0.96534
2020-11-22 | 163.1426 | 146.3678 | 146.3678 | 135.4678 | 122.8749 | 14.131 | 14.131 | 3451.7237 | 993.027 | 286.4501 | 608.0158 | 23.0285 | 12.0149 | 22.0273 | 44.0546 | 8949.2419 | 330.8123 |  |  | 26.224 | 0.95939 | 17.5542 | 4059.7395 | 2172.2466 | 1887.4929 | 894.4659 | 16.7748 | 10.9 | 12.4789 | 14.3225 | 10.6396 | 6.1382 | 3489.5698 | 7339.2006 | 10776.1103 | 2327.3936 | 4946.0009 | 8838.7113 | 0.10648 | 0.09991 | 0.082865 | 16.8712 | 10.6835 | 12.1134 | 12.2012 | 21.7362 | 53.7926 | 129.0474 | 102.167 | 71.0671 | 99.48% | 99.55% | 99.5% | 99.48% | 99.56% | 99.39% | 112.6976 | 120.1076 | 144.8141 |  |  |  | 35 | 26 | 15 | 2730 | 1248 | 360 | 4338 | 108.7173 | 12 | 22 | 44 | 23 | 98.59% | 0.1006 | 0.10263 | 40.1538 | 39.6682 | 117.1489 | 23.1769 | 98.59% | 3621.0995 | 99.36% | 99.49% | 85.02% |  |  | 99.39% | 0.95939
2020-11-21 | 165.1434 | 148.2029 | 148.2029 | 137.3423 | 124.7481 | 14.2215 | 14.2215 | 3465.1069 | 996.8772 | 287.5607 | 612.6166 | 24.1071 | 12.5776 | 23.059 | 46.1179 | 9487.4692 | 337.4087 |  |  | 26.3609 | 0.95497 | 18.3764 | 4077.7235 | 2180.6689 | 1897.0546 | 900.1774 | 16.9405 | 10.8605 | 12.5563 | 14.378 | 10.6808 | 6.162 | 3674.4451 | 7718.0745 | 11319.272 | 2451.5325 | 5205.0938 | 9289.9494 | 0.10541 | 0.099375 | 0.083345 | 16.9202 | 10.5578 | 12.0642 | 12.1169 | 21.6054 | 53.5368 | 130.2568 | 102.6409 | 70.6045 | 99.49% | 99.56% | 99.5% | 99.51% | 99.58% | 99.42% | 113.8389 | 120.7551 | 143.9791 |  |  |  | 35 | 26 | 15 | 2730 | 1248 | 360 | 4338 | 110.5465 | 12 | 22 | 44 | 23 | 98.6% | 0.099949 | 0.10184 | 40.3574 | 39.5421 | 117.8632 | 23.035 | 98.6% | 3811.2085 | 99.37% | 99.52% | 84.98% |  |  | 99.4% | 0.95497
2020-11-20 | 165.0207 | 148.159 | 148.159 | 137.3532 | 124.8224 | 14.0965 | 14.0965 | 3471.5421 | 998.7286 | 288.0948 | 612.4757 | 24.1318 | 12.5905 | 23.0825 | 46.1651 | 9622.6733 | 338.0929 |  |  | 26.4794 | 0.95117 | 18.3952 | 4084.0178 | 2184.7187 | 1899.299 | 900.5705 | 16.8617 | 10.8058 | 12.4514 | 14.4047 | 10.7007 | 6.1735 | 3712.1467 | 7803.3022 | 11452.0849 | 2476.1384 | 5260.2861 | 9395.5381 | 0.10525 | 0.099324 | 0.083594 | 16.8055 | 10.4897 | 11.9603 | 11.9831 | 21.3549 | 52.8761 | 130.1757 | 102.4736 | 70.2445 | 99.49% | 99.56% | 99.51% | 99.52% | 99.59% | 99.44% | 114.0114 | 120.8162 | 143.5514 |  |  |  | 35 | 26 | 15 | 2730 | 1248 | 360 | 4338 | 110.6644 | 12 | 22 | 44 | 23 | 98.61% | 0.09989 | 0.10175 | 40.1189 | 39.2555 | 117.6843 | 22.7696 | 98.61% | 3851.3344 | 99.37% | 99.53% | 85% |  |  | 99.4% | 0.95117
2020-11-19 | 164.0149 | 147.2157 | 147.2157 | 136.3819 | 123.8004 | 14.1716 | 14.1716 | 3469.3289 | 994.9195 | 293.3628 | 612.5382 | 24.7728 | 12.5278 | 22.9676 | 48.2188 | 9567.2183 | 334.9714 |  |  | 26.5663 | 0.94839 | 18.5396 | 4081.867 | 2181.0466 | 1900.8204 | 905.9009 | 16.7993 | 10.8338 | 12.3566 | 14.3805 | 10.6599 | 6.2863 | 3690.316 | 7718.0373 | 11391.3417 | 2463.4078 | 5217.6858 | 9317.5547 | 0.10557 | 0.099453 | 0.085693 | 16.7458 | 10.4784 | 11.8061 | 11.9299 | 21.278 | 56.5435 | 129.1893 | 101.6536 | 69.5729 | 99.49% | 99.56% | 99.48% | 99.52% | 99.59% | 99.39% | 113.6696 | 120.6603 | 140.0343 |  |  |  | 32.8125 | 24.3229 | 14.3438 | 2559.375 | 1167.5 | 344.25 | 4071.125 | 109.6316 | 12 | 22 | 46.1875 | 23.7292 | 98.56% | 0.10043 | 0.10213 | 39.9897 | 39.0304 | 116.7467 | 23.4037 | 98.56% | 3832.8474 | 99.35% | 99.52% | 84.99% |  |  | 99.39% | 0.94839
2020-11-18 | 163.9133 | 147.0936 | 147.0936 | 136.1968 | 123.6479 | 14.3214 | 14.3214 | 3473.2854 | 994.7657 | 295.9113 | 612.6711 | 24.6614 | 12.3307 | 22.6063 | 48.2953 | 9504.8804 | 335.8855 |  |  | 26.4064 | 0.95351 | 18.3377 | 4085.9565 | 2182.6083 | 1903.3482 | 908.5825 | 16.8197 | 10.8968 | 12.555 | 14.3908 | 10.6582 | 6.341 | 3663.5326 | 7649.8177 | 11321.2435 | 2445.9311 | 5176.1926 | 9246.8866 | 0.10636 | 0.10007 | 0.086861 | 16.7384 | 10.5101 | 11.9624 | 11.8986 | 21.2219 | 57.8725 | 129.0141 | 101.5559 | 69.608 | 99.5% | 99.56% | 99.48% | 99.51% | 99.59% | 99.37% | 112.8251 | 119.9156 | 138.1525 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 109.3156 | 12 | 22 | 47 | 24 | 98.56% | 0.10123 | 0.1029 | 40.2715 | 39.2109 | 116.5795 | 23.6083 | 98.56% | 3807.3079 | 99.35% | 99.52% | 85.01% |  |  | 99.38% | 0.95351
2020-11-17 | 163.1244 | 146.1794 | 146.1794 | 135.1425 | 122.7257 | 14.3471 | 14.3471 | 3472.8462 | 994.64 | 295.8739 | 613.921 | 24.8657 | 12.4328 | 22.7936 | 48.6953 | 9335.4125 | 334.3927 |  |  | 26.569 | 0.94831 | 18.4896 | 4086.7672 | 2182.3323 | 1904.4349 | 909.7949 | 16.945 | 11.037 | 12.6403 | 14.389 | 10.6569 | 6.3402 | 3609.3215 | 7530.3194 | 11136.0234 | 2410.3608 | 5097.725 | 9099.244 | 0.10634 | 0.10012 | 0.086716 | 16.8551 | 10.6322 | 12.0145 | 12.1062 | 21.6057 | 58.9675 | 128.3152 | 100.9392 | 69.3342 | 99.48% | 99.55% | 99.46% | 99.5% | 99.58% | 99.35% | 112.8443 | 119.8569 | 138.3821 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 108.3725 | 12 | 22 | 47 | 24 | 98.53% | 0.10121 | 0.10289 | 40.6223 | 39.5018 | 116.0209 | 24.0332 | 98.53% | 3749.9036 | 99.34% | 99.5% | 84.98% |  |  | 99.37% | 0.94831
2020-11-16 | 160.4255 | 143.4712 | 143.4712 | 132.4335 | 119.6793 | 14.1392 | 14.1392 | 3471.2955 | 994.1958 | 295.7418 | 611.8141 | 24.8725 | 12.4363 | 22.7998 | 48.7087 | 8585.925 | 327.2701 |  |  | 26.5621 | 0.94853 | 18.4947 | 4083.1096 | 2181.3579 | 1901.7517 | 907.5559 | 16.9543 | 11.0377 | 12.7257 | 14.3826 | 10.6521 | 6.3373 | 3352.1611 | 6999.3602 | 10359.2014 | 2238.3635 | 4736.1727 | 8460.8583 | 0.10769 | 0.10079 | 0.08605 | 16.8912 | 10.6609 | 12.1476 | 13.0372 | 23.2565 | 63.4204 | 126.6795 | 100.2463 | 69.8564 | 99.44% | 99.52% | 99.42% | 99.42% | 99.51% | 99.25% | 111.4297 | 119.0596 | 139.4543 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 105.5377 | 12 | 22 | 47 | 24 | 98.41% | 0.10202 | 0.10387 | 40.7177 | 39.6997 | 115.1019 | 25.8699 | 98.41% | 3483.8822 | 99.29% | 99.42% | 85.02% |  |  | 99.32% | 0.94853
2020-11-15 | 159.9581 | 143.2248 | 143.2248 | 132.3222 | 119.7325 | 13.93 | 13.93 | 3447.7862 | 987.4626 | 293.7389 | 607.9188 | 24.9255 | 12.4627 | 22.8484 | 48.8124 | 8840.1504 | 322.7646 |  |  | 26.4571 | 0.95188 | 18.5341 | 4055.7049 | 2166.5846 | 1889.1203 | 901.6577 | 16.7334 | 10.9026 | 12.4445 | 14.2852 | 10.58 | 6.2944 | 3433.8994 | 7169.5583 | 10610.2152 | 2292.9144 | 4851.518 | 8666.2574 | 0.1077 | 0.10101 | 0.086821 | 16.8398 | 10.6355 | 11.995 | 12.7126 | 22.6778 | 61.8471 | 126.2592 | 99.7001 | 69.0101 | 99.46% | 99.53% | 99.44% | 99.45% | 99.53% | 99.29% | 111.4229 | 118.7979 | 138.215 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 105.8259 | 12 | 22 | 47 | 24 | 98.45% | 0.10222 | 0.104 | 40.0805 | 39.4702 | 114.494 | 25.2264 | 98.45% | 3568.6966 | 99.3% | 99.45% | 85.01% |  |  | 99.34% | 0.95188
2020-11-14 | 162.4242 | 145.5303 | 145.5303 | 134.808 | 122.3702 | 14.2287 | 14.2287 | 3459.5384 | 990.8285 | 294.7401 | 611.1127 | 26.6746 | 13.3373 | 24.4517 | 52.2377 | 9405.2759 | 330.8298 |  |  | 26.3058 | 0.95675 | 19.8347 | 4070.651 | 2173.9697 | 1896.6813 | 905.8528 | 16.8939 | 10.7223 | 12.4805 | 14.3339 | 10.616 | 6.3159 | 3631.015 | 7575.9007 | 11204.5694 | 2425.0302 | 5128.4599 | 9154.7572 | 0.1074 | 0.10114 | 0.087769 | 16.9052 | 10.3938 | 11.9419 | 12.9733 | 23.1545 | 63.1901 | 127.69 | 100.4204 | 68.8478 | 99.45% | 99.52% | 99.43% | 99.47% | 99.55% | 99.31% | 111.7319 | 118.6434 | 136.7228 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 108.0912 | 12 | 22 | 47 | 24 | 98.43% | 0.10226 | 0.10394 | 40.0967 | 39.2409 | 115.4265 | 25.7551 | 98.43% | 3772.6539 | 99.29% | 99.47% | 84.99% |  |  | 99.33% | 0.95675
2020-11-13 | 162.9353 | 146.0728 | 146.0728 | 135.2963 | 122.7222 | 14.0988 | 14.0988 | 3470.6064 | 993.9985 | 295.6831 | 613.2777 | 27.2702 | 13.6351 | 24.9977 | 53.4041 | 9538.7733 | 332.2622 |  |  | 26.4696 | 0.95148 | 20.2776 | 4083.8841 | 2180.9249 | 1902.9592 | 908.9607 | 16.8625 | 10.7765 | 12.4321 | 14.3797 | 10.65 | 6.3361 | 3678.6645 | 7674.1498 | 11348.3838 | 2456.9872 | 5195.4127 | 9272.9114 | 0.10673 | 0.10059 | 0.08761 | 16.7914 | 10.3941 | 11.8338 | 13.0601 | 23.3123 | 63.63 | 128.1885 | 100.7337 | 68.8129 | 99.45% | 99.52% | 99.42% | 99.47% | 99.55% | 99.31% | 112.4289 | 119.2904 | 136.9714 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 108.61 | 12 | 22 | 47 | 24 | 98.42% | 0.10171 | 0.10335 | 40.0711 | 39.0193 | 115.7756 | 25.9301 | 98.42% | 3821.9775 | 99.29% | 99.47% | 84.98% |  |  | 99.32% | 0.95148
2020-11-12 | 162.6568 | 145.8073 | 145.8073 | 135.0588 | 122.6459 | 14.1997 | 14.1997 | 3469.8172 | 993.7724 | 295.6159 | 612.3033 | 27.7365 | 13.8683 | 25.4251 | 54.3173 | 9644.1516 | 332.4335 |  |  | 26.4843 | 0.95101 | 20.6243 | 4082.1205 | 2180.4289 | 1901.6915 | 907.9191 | 16.8495 | 10.7484 | 12.3768 | 14.3765 | 10.6476 | 6.3346 | 3716.5845 | 7756.782 | 11475.4796 | 2482.0289 | 5250.016 | 9374.6302 | 0.10707 | 0.10115 | 0.088526 | 16.7912 | 10.3798 | 11.8047 | 13.1399 | 23.4474 | 63.9696 | 127.6915 | 100.1104 | 68.0511 | 99.44% | 99.52% | 99.42% | 99.47% | 99.55% | 99.32% | 112.074 | 118.6379 | 135.553 |  |  |  | 32 | 23.7 | 14.1 | 2496 | 1137.6 | 338.4 | 3972 | 108.416 | 12 | 22 | 47 | 24 | 98.4% | 0.10221 | 0.1038 | 39.9748 | 38.9757 | 115.178 | 26.0812 | 98.4% | 3862.0184 | 99.28% | 99.47% | 85% |  |  | 99.32% | 0.95101
2020-11-11 | 159.9167 | 143.441 | 143.441 | 132.8741 | 120.8965 | 14.2465 | 14.2465 | 3416.2975 | 979.285 | 294.8669 | 602.2216 | 26.375 | 13.1354 | 24.1988 | 52.9654 | 9543.444 | 320.1814 |  |  | 26.5422 | 0.94916 | 19.7445 | 4018.5191 | 2142.1456 | 1876.3735 | 897.0885 | 16.4757 | 10.5669 | 12.1669 | 14.124 | 10.4923 | 6.3186 | 3673.5139 | 7657.2006 | 11380.4761 | 2456.1722 | 5186.2928 | 9274.2251 | 0.10706 | 0.10152 | 0.090142 | 16.7916 | 10.4047 | 11.8481 | 12.3316 | 22.218 | 62.7705 | 125.2172 | 98.1007 | 66.5326 | 99.47% | 99.53% | 99.43% | 99.5% | 99.57% | 99.32% | 112.0846 | 118.2062 | 133.1238 |  |  |  | 32 | 23.7719 | 14.3156 | 2496 | 1141.05 | 343.575 | 3980.625 | 106.6008 | 12.0719 | 22.2396 | 48.6771 | 24.2396 | 98.47% | 0.10258 | 0.10401 | 39.2095 | 39.0443 | 112.7966 | 24.5924 | 98.47% | 3827.2425 | 99.31% | 99.49% | 85.01% |  |  | 99.36% | 0.94916
2020-11-10 | 161.0904 | 144.1323 | 144.1323 | 133.1246 | 120.694 | 14.3317 | 14.3317 | 3471.4021 | 995.7391 | 313.6186 | 613.4794 | 23.4838 | 11.2998 | 22.0599 | 51.3314 | 9342.838 | 329.7279 |  |  | 26.4429 | 0.95234 | 18.0028 | 4084.8816 | 2162.0444 | 1922.8372 | 927.0981 | 16.9582 | 11.0077 | 12.5617 | 14.2552 | 10.6686 | 6.7204 | 3543.9617 | 7326.6201 | 11045.8417 | 2379.6798 | 4985.3209 | 8933.1707 | 0.10737 | 0.10213 | 0.093887 | 16.7987 | 10.4053 | 11.7443 | 11.0881 | 21.4964 | 67.3979 | 126.4378 | 99.4804 | 68.1684 | 99.53% | 99.56% | 99.43% | 99.53% | 99.57% | 99.25% | 111.7614 | 117.4947 | 127.8137 |  |  |  | 31.8178 | 23.8125 | 15 | 2481.7914 | 1143 | 360 | 3984.7914 | 106.37 | 12.3 | 24.0125 | 55.875 | 25.5625 | 98.6% | 0.10354 | 0.10465 | 40.5275 | 38.9484 | 114.2166 | 22.9731 | 98.6% | 3719.1488 | 99.37% | 99.5% | 84.98% |  |  | 99.4% | 0.95234
2020-11-09 | 158.244 | 141.275 | 141.275 | 130.304 | 117.4977 | 14.2231 | 14.2231 | 3467.8915 | 986.2319 | 321.5974 | 611.6185 | 24.2962 | 10.673 | 24.6433 | 55.5342 | 8812.7784 | 322.6224 |  |  | 26.2248 | 0.95937 | 18.8062 | 4079.51 | 2160.0622 | 1919.4478 | 933.2159 | 16.9689 | 10.971 | 12.7054 | 14.2422 | 10.5668 | 6.8914 | 3313.9953 | 6790.2155 | 10331.4028 | 2224.7514 | 4643.5065 | 8314.5453 | 0.10978 | 0.10295 | 0.096682 | 16.8462 | 10.3558 | 11.8296 | 11.2746 | 25.7238 | 80.9271 | 124.466 | 98.4721 | 68.3827 | 99.52% | 99.47% | 99.33% | 99.49% | 99.45% | 99.03% | 109.3129 | 116.5649 | 124.1188 |  |  |  | 31 | 23 | 15 | 2418 | 1104 | 360 | 3882 | 103.3267 | 12.3 | 28.4 | 64 | 28 | 98.45% | 0.1055 | 0.10662 | 40.6453 | 39.0316 | 112.8994 | 25.5821 | 98.45% | 3477.3613 | 99.3% | 99.4% | 85.01% |  |  | 99.33% | 0.95937
2020-11-08 | 156.9804 | 140.2278 | 140.2278 | 129.3677 | 116.5785 | 13.9821 | 13.9821 | 3455.2417 | 982.6344 | 320.4243 | 611.3599 | 24.5707 | 10.7936 | 24.9217 | 56.1616 | 8928.5773 | 317.4661 |  |  | 26.3484 | 0.95538 | 19.0187 | 4066.6016 | 2152.183 | 1914.4186 | 931.7842 | 16.7526 | 10.8601 | 12.5424 | 14.1902 | 10.5282 | 6.8662 | 3358.575 | 6874.1557 | 10447.5839 | 2255.3557 | 4703.7391 | 8413.0096 | 0.10986 | 0.10325 | 0.097607 | 16.7064 | 10.286 | 11.697 | 11.1597 | 25.4812 | 80.2533 | 123.3992 | 97.4216 | 67.2068 | 99.52% | 99.47% | 99.33% | 99.51% | 99.46% | 99.05% | 109.227 | 116.2269 | 122.9422 |  |  |  | 31 | 23 | 15 | 2418 | 1104 | 360 | 3882 | 102.6402 | 12.3 | 28.4 | 64 | 28 | 98.45% | 0.10578 | 0.10684 | 40.1552 | 38.6894 | 111.7265 | 25.3393 | 98.45% | 3522.6846 | 99.3% | 99.42% | 84.97% |  |  | 99.34% | 0.95538
2020-11-07 | 157.6446 | 140.876 | 140.876 | 130.2677 | 117.6931 | 14.1505 | 14.1505 | 3472.039 | 987.4114 | 321.982 | 611.9503 | 26.5053 | 11.6434 | 26.884 | 60.5836 | 9540.123 | 321.1995 |  |  | 26.8298 | 0.94003 | 20.5162 | 4083.9893 | 2162.6456 | 1921.3437 | 933.9323 | 16.7687 | 10.6083 | 12.2764 | 14.2592 | 10.5794 | 6.8996 | 3559.0854 | 7293.5489 | 11099.2248 | 2389.215 | 4987.2704 | 8931.6178 | 0.10878 | 0.10293 | 0.099059 | 16.6209 | 9.9997 | 11.4185 | 11.2357 | 25.6323 | 80.6253 | 123.2219 | 96.6194 | 65.4747 | 99.51% | 99.46% | 99.32% | 99.53% | 99.49% | 99.1% | 110.3147 | 116.5852 | 121.1405 |  |  |  | 31 | 23 | 15 | 2418 | 1104 | 360 | 3882 | 103.5381 | 12.3 | 28.4 | 64 | 28 | 98.42% | 0.10535 | 0.10621 | 39.6533 | 38.0391 | 111.0672 | 25.4911 | 98.42% | 3734.789 | 99.29% | 99.45% | 85.02% |  |  | 99.33% | 0.94003
2020-11-06 | 154.1482 | 137.5029 | 137.5029 | 126.9736 | 114.608 | 14.0298 | 14.0298 | 3463.0697 | 985.6223 | 318.7203 | 612.8848 | 26.8909 | 11.8128 | 27.2751 | 61.465 | 9461.5121 | 312.1157 |  |  | 27.5501 | 0.91761 | 20.7832 | 4075.9545 | 2158.7271 | 1917.2274 | 931.605 | 16.6453 | 10.5293 | 12.1515 | 14.2334 | 10.5602 | 6.8297 | 3528.0857 | 7231.8839 | 10960.7377 | 2368.2877 | 4944.3922 | 8839.3691 | 0.10883 | 0.1035 | 0.099679 | 16.5488 | 9.9589 | 11.3177 | 11.2052 | 25.5587 | 79.8633 | 120.0134 | 93.6229 | 62.8715 | 99.5% | 99.45% | 99.3% | 99.53% | 99.48% | 99.1% | 110.2674 | 115.94 | 120.3859 |  |  |  | 31 | 23 | 14.875 | 2418 | 1104 | 357 | 3879 | 100.6051 | 12.3 | 28.4 | 64 | 28 | 98.39% | 0.10566 | 0.10647 | 39.3261 | 37.8254 | 107.9988 | 25.4371 | 98.39% | 3697.031 | 99.27% | 99.44% | 84.96% |  |  | 99.33% | 0.91761
2020-11-05 | 153.9362 | 137.3994 | 137.3994 | 127.1287 | 114.6735 | 14.2258 | 14.2258 | 3452.7553 | 994.2206 | 280.9754 | 611.4811 | 28.3113 | 12.4367 | 28.7157 | 64.7115 | 9653.7599 | 312.1268 |  |  | 27.8368 | 0.90886 | 21.3783 | 4064.2363 | 2177.5593 | 1886.6771 | 892.4564 | 16.5368 | 10.2707 | 12.1374 | 14.3575 | 10.6524 | 6.0209 | 3639.0708 | 7661.104 | 11151.6444 | 2424.9774 | 5160.1075 | 9188.9858 | 0.10931 | 0.1048 | 0.089629 | 16.6164 | 10.0821 | 11.7648 | 11.5111 | 25.7609 | 70.6245 | 119.3793 | 92.3813 | 61.0539 | 99.49% | 99.44% | 99.3% | 99.53% | 99.5% | 99.23% | 109.7823 | 114.5041 | 133.886 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 100.5043 | 12.3 | 28.4 | 64 | 28 | 98.33% | 0.10472 | 0.10641 | 38.9449 | 38.4633 | 107.2867 | 25.9829 | 98.33% | 3762.9936 | 99.25% | 99.47% | 84.95% |  |  | 99.32% | 0.90886
2020-11-04 | 154.5404 | 137.7989 | 137.7989 | 127.3251 | 115.1806 | 14.3034 | 14.3034 | 3473.5843 | 1000.2183 | 282.6704 | 613.4178 | 27.8235 | 12.2225 | 28.221 | 63.5966 | 9751.1408 | 315.1708 |  |  | 27.8137 | 0.90956 | 21.0099 | 4087.0021 | 2190.6956 | 1896.3065 | 896.0882 | 16.7414 | 10.4739 | 12.2188 | 14.4441 | 10.7166 | 6.0572 | 3668.3094 | 7731.3951 | 11264.8101 | 2443.6494 | 5204.1466 | 9277.4845 | 0.10975 | 0.10552 | 0.090496 | 16.6856 | 10.2084 | 11.7782 | 11.3027 | 25.2737 | 69.2136 | 119.7091 | 92.379 | 60.88 | 99.5% | 99.46% | 99.31% | 99.54% | 99.51% | 99.25% | 109.3412 | 113.727 | 132.6019 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 100.869 | 12.3 | 28.4 | 64 | 28 | 98.37% | 0.10531 | 0.10696 | 39.4341 | 38.6722 | 107.5028 | 25.4946 | 98.37% | 3794.6524 | 99.27% | 99.48% | 84.99% |  |  | 99.33% | 0.90956
2020-11-03 | 153.1789 | 136.5298 | 136.5298 | 125.9759 | 113.6923 | 14.2954 | 14.2954 | 3473.3215 | 1000.1427 | 282.649 | 613.9436 | 24.1873 | 10.6252 | 24.5329 | 55.2853 | 9504.8255 | 312.2819 |  |  | 27.8029 | 0.90989 | 18.2642 | 4087.2651 | 2190.5299 | 1896.7353 | 896.5926 | 16.6491 | 10.5539 | 12.3131 | 14.4431 | 10.7158 | 6.0568 | 3585.8075 | 7558.3839 | 11012.6806 | 2388.3359 | 5087.3602 | 9069.8566 | 0.11074 | 0.10639 | 0.091142 | 16.5907 | 10.2812 | 11.857 | 10.056 | 22.4815 | 61.5632 | 118.6704 | 91.6433 | 60.4658 | 99.56% | 99.52% | 99.39% | 99.58% | 99.56% | 99.32% | 108.3616 | 112.7892 | 131.6622 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 99.3746 | 12.3 | 28.4 | 64 | 28 | 98.55% | 0.10621 | 0.10789 | 39.5162 | 38.729 | 106.6554 | 22.6795 | 98.55% | 3709.2429 | 99.35% | 99.53% | 84.98% |  |  | 99.41% | 0.90989
2020-11-02 | 148.9671 | 132.43 | 132.43 | 121.862 | 109.6894 | 13.9973 | 13.9973 | 3440.7752 | 990.7709 | 280.0005 | 609.1252 | 24.4038 | 10.7202 | 24.7524 | 55.7801 | 8751.7776 | 298.3433 |  |  | 27.7923 | 0.91021 | 18.4276 | 4049.9004 | 2170.0038 | 1879.8966 | 889.1257 | 16.537 | 10.568 | 12.2044 | 14.3077 | 10.6154 | 6 | 3333.7609 | 7021.0568 | 10222.8304 | 2221.1539 | 4727.9841 | 8422.3927 | 0.11261 | 0.1078 | 0.091104 | 16.7055 | 10.4308 | 11.8971 | 10.8113 | 24.1866 | 66.2857 | 115.6491 | 89.6326 | 59.9454 | 99.52% | 99.48% | 99.34% | 99.51% | 99.49% | 99.21% | 106.564 | 111.3187 | 131.7172 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 95.6826 | 12.3 | 28.4 | 64 | 28 | 98.43% | 0.10763 | 0.10947 | 39.3094 | 39.0334 | 104.3622 | 24.3968 | 98.43% | 3447.6346 | 99.29% | 99.46% | 84.96% |  |  | 99.36% | 0.91021
2020-11-01 | 150.2356 | 133.654 | 133.654 | 123.2207 | 110.9824 | 13.8136 | 13.8136 | 3449.9282 | 993.4065 | 280.7453 | 609.2526 | 24.6505 | 10.8286 | 25.0026 | 56.3439 | 8990.6652 | 301.0115 |  |  | 27.88 | 0.90755 | 18.6139 | 4059.1807 | 2175.7763 | 1883.4044 | 889.9979 | 16.5817 | 10.4332 | 12.1708 | 14.3458 | 10.6436 | 6.016 | 3405.3969 | 7178.5585 | 10460.4955 | 2268.2909 | 4831.5372 | 8614.5498 | 0.11143 | 0.10663 | 0.090249 | 16.6966 | 10.2734 | 11.8526 | 10.6907 | 23.901 | 65.4445 | 116.8439 | 90.591 | 60.4969 | 99.52% | 99.48% | 99.35% | 99.53% | 99.51% | 99.24% | 107.6941 | 112.5396 | 132.965 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 97.1409 | 12.3 | 28.4 | 64 | 28 | 98.45% | 0.1065 | 0.10832 | 39.1858 | 38.8225 | 105.3932 | 24.1109 | 98.45% | 3522.8179 | 99.3% | 99.48% | 84.99% |  |  | 99.37% | 0.90755
2020-10-31 | 153.2685 | 136.6254 | 136.6254 | 126.2406 | 114.063 | 14.0057 | 14.0057 | 3465.8849 | 998.0013 | 282.0438 | 612.6632 | 26.7919 | 11.7693 | 27.1747 | 61.2387 | 9681.6601 | 310.3778 |  |  | 27.7759 | 0.91071 | 20.231 | 4078.548 | 2185.8397 | 1892.7083 | 894.707 | 16.6431 | 10.3848 | 12.0483 | 14.4121 | 10.6929 | 6.0438 | 3649.3801 | 7689.7705 | 11201.6193 | 2431.1042 | 5176.7818 | 9226.5543 | 0.11044 | 0.10622 | 0.09125 | 16.6378 | 10.1487 | 11.6386 | 10.9293 | 24.4418 | 66.9512 | 118.8445 | 91.6792 | 60.3195 | 99.52% | 99.48% | 99.34% | 99.55% | 99.53% | 99.27% | 108.6556 | 112.9737 | 131.5069 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 100.0397 | 12.3 | 28.4 | 64 | 28 | 98.42% | 0.10602 | 0.10766 | 39.0762 | 38.4251 | 106.7417 | 24.6554 | 98.42% | 3774.7162 | 99.29% | 99.5% | 84.98% |  |  | 99.35% | 0.91071
2020-10-30 | 153.1987 | 136.5598 | 136.5598 | 126.22 | 113.9333 | 14.0771 | 14.0771 | 3471.0025 | 999.4749 | 282.4603 | 613.6883 | 27.3526 | 12.0156 | 27.7434 | 62.5202 | 9685.4103 | 311.3255 |  |  | 27.8734 | 0.90775 | 20.6543 | 4084.6908 | 2189.0673 | 1895.6235 | 896.1486 | 16.6389 | 10.3398 | 12.0467 | 14.4334 | 10.7087 | 6.0527 | 3659.242 | 7709.4537 | 11229.0824 | 2437.813 | 5190.4474 | 9249.7043 | 0.1104 | 0.10624 | 0.091476 | 16.5959 | 10.081 | 11.6085 | 11.1076 | 24.8434 | 68.06 | 118.6732 | 91.4993 | 60.0636 | 99.51% | 99.47% | 99.32% | 99.54% | 99.52% | 99.26% | 108.6921 | 112.9528 | 131.1823 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 99.8524 | 12.3 | 28.4 | 64 | 28 | 98.4% | 0.10604 | 0.10766 | 39.0254 | 38.2854 | 106.5508 | 25.0599 | 98.4% | 3784.7661 | 99.28% | 99.49% | 84.98% |  |  | 99.34% | 0.90775
2020-10-29 | 152.2206 | 135.8821 | 135.8821 | 125.7111 | 113.3405 | 13.985 | 13.985 | 3438.8892 | 990.2279 | 279.847 | 607.2615 | 27.8389 | 12.2292 | 28.2366 | 63.6317 | 9726.6087 | 301.9364 |  |  | 27.8239 | 0.90925 | 21.0215 | 4046.1507 | 2168.8143 | 1877.3364 | 887.1085 | 16.3385 | 10.1711 | 11.9667 | 14.2999 | 10.6096 | 5.9967 | 3675.8361 | 7747.4403 | 11288.4037 | 2448.6441 | 5214.8783 | 9296.8215 | 0.1103 | 0.10615 | 0.091832 | 16.5313 | 10.0639 | 11.7109 | 11.1693 | 24.975 | 68.3941 | 117.8843 | 90.8784 | 59.3749 | 99.5% | 99.46% | 99.32% | 99.54% | 99.52% | 99.26% | 108.798 | 113.0471 | 130.6731 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 99.4982 | 12.3 | 28.4 | 64 | 28 | 98.37% | 0.10602 | 0.1076 | 38.4762 | 38.3062 | 105.6939 | 25.1934 | 98.37% | 3802.4661 | 99.27% | 99.49% | 84.99% |  |  | 99.34% | 0.90925
2020-10-28 | 151.747 | 135.3096 | 135.3096 | 125.1275 | 113.0344 | 14.0001 | 14.0001 | 3437.5875 | 989.8531 | 279.7411 | 606.7993 | 27.269 | 11.9789 | 27.6585 | 62.3291 | 9736.3221 | 303.5516 |  |  | 27.6085 | 0.91582 | 20.5912 | 4044.3868 | 2167.9934 | 1876.3934 | 886.5404 | 16.4374 | 10.1822 | 12.0195 | 14.2945 | 10.6056 | 5.9945 | 3671.7846 | 7740.5776 | 11280.3338 | 2445.7521 | 5209.6251 | 9289.3311 | 0.11155 | 0.10755 | 0.093133 | 16.6428 | 10.0832 | 11.7748 | 11.0285 | 24.6559 | 67.5066 | 117.3593 | 90.3086 | 58.9458 | 99.51% | 99.47% | 99.33% | 99.55% | 99.53% | 99.27% | 107.5777 | 111.5751 | 128.8475 |  |  |  | 31 | 23 | 13 | 2418 | 1104 | 312 | 3834 | 99.0745 | 12.3 | 28.4 | 64 | 28 | 98.41% | 0.10732 | 0.1089 | 38.6391 | 38.5008 | 105.1903 | 24.8722 | 98.41% | 3798.5201 | 99.28% | 99.5% | 85% |  |  | 99.35% | 0.91582
2020-10-27 | 151.7085 | 134.936 | 134.936 | 124.4642 | 112.0512 | 13.9729 | 13.9729 | 3472.9031 | 952.2511 | 269.8766 | 613.5886 | 25.8447 | 12.9223 | 25.8447 | 55.6654 | 9274.6057 | 308.2144 |  |  | 27.34 | 0.92408 | 19.7871 | 4086.4917 | 2250.7754 | 1835.7163 | 883.4652 | 16.7725 | 10.4718 | 12.2963 | 14.8403 | 10.2027 | 5.7831 | 3634.0763 | 7523.2419 | 10807.7299 | 2377.734 | 5115.175 | 8968.0405 | 0.11669 | 0.10443 | 0.08948 | 16.976 | 10.6213 | 12.0011 | 12.8194 | 22.7766 | 60.7908 | 117.5253 | 90.2805 | 59.7229 | 99.46% | 99.49% | 99.38% | 99.46% | 99.55% | 99.32% | 102.8397 | 114.9082 | 134.1078 |  |  |  | 32 | 22 | 12.47 | 2496 | 1056 | 299.28 | 3851.28 | 98.0227 | 13 | 26 | 56 | 26 | 98.42% | 0.10841 | 0.11121 | 39.5406 | 39.5984 | 105.9015 | 25.0735 | 98.42% | 3640.4531 | 99.29% | 99.47% | 84.98% |  |  | 99.34% | 0.92408
2020-10-26 | 149.7071 | 132.9776 | 132.9776 | 122.3953 | 109.836 | 13.6862 | 13.6862 | 3471.7434 | 951.9331 | 269.7865 | 613.7987 | 25.3951 | 12.6976 | 25.3951 | 54.6972 | 8962.6177 | 301.9722 |  |  | 27.3239 | 0.92458 | 19.4429 | 4085.5421 | 2250.0238 | 1835.5184 | 883.5852 | 16.7295 | 10.5824 | 12.3781 | 14.8353 | 10.1993 | 5.7811 | 3524.7808 | 7294.8543 | 10477.1625 | 2306.4585 | 4960.6997 | 8694.8289 | 0.11805 | 0.10557 | 0.090245 | 16.9374 | 10.7339 | 12.077 | 12.9883 | 23.0821 | 61.6229 | 116.1874 | 89.3238 | 59.2288 | 99.45% | 99.49% | 99.37% | 99.44% | 99.53% | 99.29% | 101.6484 | 113.6673 | 132.9713 |  |  |  | 32 | 22 | 12.47 | 2496 | 1056 | 299.28 | 3851.28 | 96.1666 | 13 | 26 | 56 | 26 | 98.4% | 0.10961 | 0.11247 | 39.69 | 39.7483 | 104.8102 | 25.4086 | 98.4% | 3530.6723 | 99.28% | 99.44% | 84.98% |  |  | 99.34% | 0.92458
2020-10-25 | 147.5891 | 130.8742 | 130.8742 | 120.5694 | 108.216 | 13.7328 | 13.7328 | 3474.062 | 952.5689 | 269.9667 | 613.1193 | 26.3875 | 13.1938 | 26.3875 | 56.8347 | 9109.9361 | 296.3887 |  |  | 27.9753 | 0.90467 | 20.2027 | 4087.1813 | 2251.5265 | 1835.6549 | 883.086 | 16.7149 | 10.3048 | 12.149 | 14.8452 | 10.2061 | 5.785 | 3568.1873 | 7388.6626 | 10616.989 | 2334.5872 | 5022.9778 | 8808.6268 | 0.11792 | 0.10612 | 0.091976 | 16.9149 | 10.4544 | 11.8675 | 13.0549 | 23.1922 | 61.8844 | 113.8919 | 87.0061 | 56.901 | 99.43% | 99.47% | 99.35% | 99.44% | 99.54% | 99.3% | 101.7645 | 113.0785 | 130.4688 |  |  |  | 32 | 22 | 12.47 | 2496 | 1056 | 299.28 | 3851.28 | 94.4982 | 13 | 26 | 56 | 26 | 98.36% | 0.10999 | 0.11267 | 39.1686 | 39.2368 | 102.5067 | 25.5311 | 98.36% | 3574.8219 | 99.26% | 99.45% | 85% |  |  | 99.33% | 0.90467
2020-10-24 | 147.1693 | 130.8115 | 130.8115 | 120.7781 | 108.7579 | 13.9325 | 13.9325 | 3442.9036 | 944.0254 | 267.5454 | 608.1549 | 28.4268 | 14.2134 | 28.4268 | 61.2269 | 9536.1603 | 292.8892 |  |  | 28.2501 | 0.89643 | 21.764 | 4051.0585 | 2231.3328 | 1819.7257 | 875.7003 | 16.3579 | 10.0333 | 11.9352 | 14.7121 | 10.1146 | 5.7331 | 3721.8004 | 7703.3436 | 11065.3375 | 2435.518 | 5238.2019 | 9182.292 | 0.11676 | 0.10566 | 0.093053 | 16.7743 | 10.3114 | 11.8045 | 13.2384 | 23.5268 | 62.8028 | 112.9513 | 85.8134 | 55.2302 | 99.42% | 99.46% | 99.33% | 99.46% | 99.55% | 99.32% | 102.7739 | 113.5726 | 128.9589 |  |  |  | 32 | 22 | 12.47 | 2496 | 1056 | 299.28 | 3851.28 | 94.7848 | 13 | 26 | 56 | 26 | 98.31% | 0.10942 | 0.11187 | 38.3265 | 38.8902 | 101.1687 | 25.8974 | 98.31% | 3728.2853 | 99.24% | 99.46% | 84.99% |  |  | 99.32% | 0.89643
2020-10-23 | 148.0284 | 131.4174 | 131.4174 | 121.2722 | 109.2068 | 14.1102 | 14.1102 | 3470.3199 | 951.5428 | 269.6759 | 612.5032 | 29.3664 | 14.6832 | 29.3664 | 63.2507 | 9657.1911 | 298.2541 |  |  | 28.3981 | 0.89203 | 22.4834 | 4082.8231 | 2249.1012 | 1833.7219 | 882.1791 | 16.611 | 10.1452 | 12.0979 | 14.8292 | 10.1951 | 5.7788 | 3762.9988 | 7790.1981 | 11192.2561 | 2462.414 | 5296.6594 | 9286.6629 | 0.11668 | 0.10587 | 0.093703 | 16.8367 | 10.3087 | 11.8356 | 13.5674 | 24.1087 | 64.343 | 113.374 | 85.8981 | 55.0122 | 99.4% | 99.45% | 99.32% | 99.45% | 99.54% | 99.31% | 102.8484 | 113.343 | 128.0639 |  |  |  | 32 | 22 | 12.47 | 2496 | 1056 | 299.28 | 3851.28 | 95.1127 | 13 | 26 | 56 | 26 | 98.27% | 0.10954 | 0.11193 | 38.8541 | 38.9809 | 101.4648 | 26.5382 | 98.27% | 3769.8558 | 99.22% | 99.46% | 85% |  |  | 99.31% | 0.89203
2020-10-22 | 146.7757 | 130.196 | 130.196 | 120.0359 | 108.1296 | 13.826 | 13.826 | 3471.6054 | 954.9702 | 263.9607 | 612.4559 | 29.4568 | 13.6604 | 30.118 | 70.2448 | 9652.8408 | 295.0333 |  |  | 28.5488 | 0.88757 | 22.4899 | 4084.0613 | 2252.6745 | 1831.3868 | 876.4166 | 16.5798 | 10.16 | 12.0543 | 14.8528 | 10.2318 | 5.6563 | 3768.698 | 7842.3682 | 11192.0547 | 2463.4896 | 5316.7329 | 9319.4849 | 0.11727 | 0.10702 | 0.092952 | 16.8096 | 10.3701 | 11.8621 | 12.5737 | 24.5976 | 69.3489 | 112.4107 | 84.8568 | 54.0105 | 99.45% | 99.43% | 99.25% | 99.49% | 99.54% | 99.26% | 102.324 | 112.1275 | 129.0993 |  |  |  | 32.7448 | 22.5573 | 12.47 | 2554.0938 | 1082.75 | 299.28 | 3936.1238 | 94.2911 | 13.9896 | 30.8437 | 71.9375 | 30.1667 | 98.26% | 0.1101 | 0.1126 | 38.7941 | 39.0418 | 100.5171 | 26.4982 | 98.26% | 3769.6506 | 99.22% | 99.47% | 85% |  |  | 99.31% | 0.88757
2020-10-21 | 146.1753 | 129.679 | 129.679 | 119.678 | 107.5543 | 13.9565 | 13.9565 | 3471.584 | 957.6783 | 258.8264 | 613.3837 | 30.7854 | 13.4913 | 31.9625 | 78.4123 | 9708.1713 | 293.3935 |  |  | 28.7479 | 0.88173 | 23.427 | 4084.9678 | 2255.0793 | 1829.8885 | 872.2101 | 16.4963 | 10.001 | 11.8981 | 14.8687 | 10.2608 | 5.5463 | 3798.4261 | 7933.967 | 11248.735 | 2481.347 | 5367.5196 | 9399.2654 | 0.11744 | 0.10765 | 0.092174 | 16.7275 | 10.2401 | 11.7471 | 12.2605 | 25.7596 | 74.7666 | 111.6313 | 84.0442 | 53.0554 | 99.46% | 99.4% | 99.17% | 99.51% | 99.52% | 99.2% | 102.179 | 111.4736 | 130.1892 |  |  |  | 33.43 | 23.07 | 12.47 | 2607.54 | 1107.36 | 299.28 | 4014.18 | 93.644 | 14.9 | 35.3 | 86.6 | 34 | 98.2% | 0.11026 | 0.11286 | 38.3954 | 38.7147 | 99.7426 | 27.3393 | 98.2% | 3793.3028 | 99.19% | 99.46% | 84.98% |  |  | 99.28% | 0.88173
2020-10-20 | 144.1285 | 127.5863 | 127.5863 | 117.4247 | 105.3992 | 14.0311 | 14.0311 | 3470.8003 | 957.4621 | 258.768 | 612.7535 | 27.9697 | 12.2573 | 29.0391 | 71.2405 | 9368.4821 | 288.3864 |  |  | 28.7639 | 0.88126 | 21.2843 | 4083.5538 | 2254.5702 | 1828.9836 | 871.5214 | 16.5422 | 10.1616 | 11.9958 | 14.8653 | 10.2585 | 5.545 | 3678.1433 | 7687.0857 | 10903.284 | 2402.2053 | 5198.8441 | 9108.589 | 0.11923 | 0.10941 | 0.093624 | 16.7839 | 10.4138 | 11.8594 | 11.4974 | 24.1446 | 70.0429 | 109.8766 | 82.6254 | 52.1942 | 99.49% | 99.44% | 99.22% | 99.52% | 99.54% | 99.23% | 100.649 | 109.6748 | 128.1729 |  |  |  | 33.43 | 23.07 | 12.47 | 2607.54 | 1107.36 | 299.28 | 4014.18 | 91.3816 | 14.9 | 35.3 | 86.6 | 34 | 98.31% | 0.11199 | 0.11461 | 38.6996 | 39.0571 | 98.2736 | 25.628 | 98.31% | 3673.691 | 99.24% | 99.48% | 84.99% |  |  | 99.33% | 0.88126
2020-10-19 | 141.2631 | 124.5938 | 124.5938 | 114.2874 | 102.152 | 13.8581 | 13.8581 | 3469.5102 | 957.1062 | 258.6718 | 612.9505 | 27.5338 | 12.0663 | 28.5865 | 70.1301 | 8724.5354 | 282.4008 |  |  | 28.7197 | 0.88255 | 20.9526 | 4082.4606 | 2253.7322 | 1828.7285 | 871.6222 | 16.6693 | 10.3064 | 12.2007 | 14.8598 | 10.2547 | 5.543 | 3449.8084 | 7206.5652 | 10218.2185 | 2253.4999 | 4875.1211 | 8537.833 | 0.12158 | 0.11125 | 0.094035 | 16.9187 | 10.563 | 12.0583 | 12.0783 | 25.3743 | 73.6413 | 107.8631 | 81.3498 | 52.023 | 99.46% | 99.41% | 99.18% | 99.46% | 99.48% | 99.14% | 98.6964 | 107.8633 | 127.6127 |  |  |  | 33.43 | 23.07 | 12.47 | 2607.54 | 1107.36 | 299.28 | 4014.18 | 88.3263 | 14.9 | 35.3 | 86.6 | 34 | 98.23% | 0.11387 | 0.11668 | 39.1764 | 39.5401 | 96.8343 | 26.931 | 98.23% | 3445.2386 | 99.2% | 99.42% | 84.99% |  |  | 99.3% | 0.88255
2020-10-18 | 140.5165 | 123.7853 | 123.7853 | 113.5496 | 101.7098 | 13.8823 | 13.8823 | 3471.1294 | 952.104 | 263.7639 | 612.1878 | 29.659 | 13.3756 | 31.9852 | 94.211 | 8846.1212 | 279.8553 |  |  | 28.8326 | 0.87925 | 24.6226 | 4083.3171 | 2255.2614 | 1828.0558 | 875.9517 | 16.7312 | 10.2357 | 12.1781 | 14.8699 | 10.2011 | 5.6521 | 3485.7151 | 7239.7008 | 10318.3682 | 2276.7539 | 4913.3965 | 8597.9733 | 0.12225 | 0.11159 | 0.097009 | 16.9807 | 10.4693 | 11.9928 | 13.2116 | 27.9179 | 99.7951 | 106.9517 | 80.3781 | 51.2286 | 99.41% | 99.35% | 98.9% | 99.42% | 99.43% | 98.84% | 98.1632 | 107.537 | 123.7004 |  |  |  | 34.78 | 23.86 | 13.22 | 2712.8399 | 1145.28 | 317.28 | 4175.3999 | 87.8011 | 23 | 55 | 162 | 51 | 98.11% | 0.1148 | 0.1174 | 39.145 | 39.4428 | 95.8478 | 28.6234 | 98.11% | 3480.301 | 99.15% | 99.33% | 85.01% |  |  | 99.25% | 0.87925
2020-10-17 | 141.8128 | 125.4451 | 125.4451 | 115.5841 | 103.5704 | 14.0792 | 14.0792 | 3463.5707 | 950.0307 | 263.1896 | 610.2917 | 30.5619 | 13.7828 | 32.959 | 97.0791 | 9435.8937 | 281.9378 |  |  | 28.8876 | 0.87765 | 25.3722 | 4073.8624 | 2250.3504 | 1823.512 | 873.4813 | 16.3677 | 9.861 | 11.8307 | 14.8375 | 10.1789 | 5.6398 | 3693.6897 | 7675.2367 | 10943.333 | 2412.1878 | 5207.6216 | 9116.8757 | 0.12107 | 0.11089 | 0.098211 | 16.671 | 10.1254 | 11.702 | 12.7982 | 27.0341 | 96.5929 | 107.5577 | 80.5621 | 50.3991 | 99.43% | 99.37% | 98.94% | 99.47% | 99.48% | 98.94% | 99.1153 | 108.2153 | 122.1855 |  |  |  | 34.78 | 23.86 | 13.22 | 2712.8399 | 1145.28 | 317.28 | 4175.3999 | 89.5197 | 23 | 55 | 162 | 51 | 98.16% | 0.11416 | 0.11654 | 38.0593 | 38.4985 | 95.9661 | 27.7193 | 98.16% | 3688.4291 | 99.17% | 99.39% | 85.02% |  |  | 99.27% | 0.87765
2020-10-16 | 142.132 | 125.6583 | 125.6583 | 115.862 | 103.9567 | 14.2951 | 14.2951 | 3473.4778 | 952.7482 | 263.9424 | 612.1668 | 31.5542 | 14.2303 | 34.0291 | 100.2311 | 9591.9705 | 284.3898 |  |  | 28.9947 | 0.87454 | 26.196 | 4085.6446 | 2256.7872 | 1828.8574 | 876.1092 | 16.4737 | 9.7963 | 11.842 | 14.8799 | 10.208 | 5.6559 | 3736.2876 | 7762.4066 | 11066.0368 | 2440.1912 | 5267.2776 | 9219.7982 | 0.12109 | 0.11118 | 0.098894 | 16.7061 | 10.0146 | 11.6601 | 13.053 | 27.5766 | 98.5476 | 107.4702 | 80.2988 | 50.0164 | 99.42% | 99.35% | 98.91% | 99.47% | 99.48% | 98.93% | 99.1032 | 107.9364 | 121.3417 |  |  |  | 34.78 | 23.86 | 13.22 | 2712.8399 | 1145.28 | 317.28 | 4175.3999 | 89.6348 | 23 | 55 | 162 | 51 | 98.12% | 0.11436 | 0.11668 | 38.112 | 38.3808 | 95.798 | 28.2747 | 98.12% | 3730.8075 | 99.15% | 99.38% | 85.02% |  |  | 99.26% | 0.87454
2020-10-15 | 141.1763 | 124.7726 | 124.7726 | 114.965 | 103.1569 | 14.1632 | 14.1632 | 3465.3395 | 950.5159 | 263.324 | 611.8742 | 31.9889 | 14.4263 | 34.4978 | 101.6116 | 9567.0344 | 281.2272 |  |  | 28.964 | 0.87543 | 26.5568 | 4077.2137 | 2251.4996 | 1825.7141 | 875.1982 | 16.4037 | 9.8076 | 11.8384 | 14.8451 | 10.1841 | 5.6427 | 3703.778 | 7688.8288 | 10954.0362 | 2419.573 | 5219.6456 | 9129.6189 | 0.1217 | 0.11175 | 0.099276 | 16.6841 | 10.0487 | 11.6708 | 13.3278 | 28.1741 | 100.7578 | 106.7855 | 79.7799 | 49.7578 | 99.4% | 99.34% | 98.89% | 99.45% | 99.46% | 98.9% | 98.6028 | 107.3815 | 120.8747 |  |  |  | 34.78 | 23.86 | 13.22 | 2712.8399 | 1145.28 | 317.28 | 4175.3999 | 89.0094 | 23 | 55 | 162 | 51 | 98.08% | 0.11493 | 0.11727 | 38.0497 | 38.4035 | 95.1881 | 28.884 | 98.08% | 3697.4939 | 99.13% | 99.36% | 84.99% |  |  | 99.24% | 0.87543
2020-10-14 | 141.1977 | 124.8357 | 124.8357 | 115.1087 | 103.1813 | 14.1251 | 14.1251 | 3471.7733 | 952.2807 | 263.8129 | 613.0575 | 31.928 | 14.3989 | 34.4321 | 101.4183 | 9722.1445 | 281.6748 |  |  | 28.9162 | 0.87682 | 26.5063 | 4084.8307 | 2255.6797 | 1829.151 | 876.8703 | 16.362 | 9.727 | 11.7723 | 14.8726 | 10.203 | 5.6531 | 3757.076 | 7799.865 | 11112.6855 | 2454.3041 | 5294.8743 | 9261.6421 | 0.12223 | 0.11247 | 0.10071 | 16.595 | 9.9379 | 11.5723 | 13.1594 | 27.8165 | 99.4741 | 106.692 | 79.5449 | 49.2188 | 99.41% | 99.35% | 98.9% | 99.46% | 99.47% | 98.93% | 98.1782 | 106.6976 | 119.1549 |  |  |  | 34.78 | 23.86 | 13.22 | 2712.8399 | 1145.28 | 317.28 | 4175.3999 | 89.0621 | 23 | 55 | 162 | 51 | 98.11% | 0.11566 | 0.11791 | 37.8613 | 38.1052 | 94.9755 | 28.5178 | 98.11% | 3750.7261 | 99.15% | 99.38% | 84.99% |  |  | 99.25% | 0.87682
2020-10-13 | 139.0792 | 122.6431 | 122.6431 | 112.7587 | 100.8816 | 14.265 | 14.265 | 3472.244 | 964.3418 | 245.7651 | 612.2877 | 33.8924 | 15.2848 | 36.5506 | 107.6582 | 9309.8866 | 283.6219 |  |  | 28.8979 | 0.87735 | 27.7291 | 4084.5317 | 2262.1371 | 1822.3946 | 858.0528 | 16.4361 | 9.8844 | 11.891 | 14.9152 | 10.3322 | 5.2664 | 3626.3572 | 7660.8414 | 10692.6002 | 2364.7273 | 5149.8979 | 9008.8627 | 0.12481 | 0.11641 | 0.096162 | 16.7001 | 10.2436 | 11.9233 | 14.5486 | 30.7624 | 101.1921 | 104.8489 | 77.8691 | 48.0491 | 99.35% | 99.29% | 98.8% | 99.38% | 99.4% | 98.88% | 96.1483 | 103.0808 | 124.7897 |  |  |  | 33.745 | 23.3763 | 11.915 | 2632.1099 | 1122.06 | 285.96 | 4040.1299 | 86.5873 | 23 | 55 | 162 | 51 | 97.92% | 0.11754 | 0.12045 | 38.2115 | 38.8669 | 93.4761 | 31.4887 | 97.92% | 3608.5203 | 99.06% | 99.31% | 85.01% |  |  | 99.18% | 0.87735
2020-10-12 | 136.4977 | 119.9703 | 119.9703 | 109.9971 | 98.0147 | 13.8912 | 13.8912 | 3470.1428 | 973.5999 | 230.7008 | 611.6274 | 33.1336 | 14.9426 | 35.7323 | 105.2479 | 8821.8987 | 279.2964 |  |  | 28.7437 | 0.88185 | 26.7791 | 4081.7702 | 2265.8421 | 1815.9281 | 842.3282 | 16.5274 | 9.9732 | 11.9976 | 14.9396 | 10.4314 | 4.9436 | 3469.4152 | 7438.2167 | 10204.1526 | 2258.8828 | 4958.9325 | 8675.9205 | 0.12776 | 0.12028 | 0.092243 | 16.8322 | 10.4653 | 12.2341 | 14.9901 | 31.6932 | 96.9207 | 103.1231 | 76.4765 | 47.2613 | 99.34% | 99.28% | 98.79% | 99.34% | 99.36% | 98.88% | 93.9297 | 99.7633 | 130.0918 |  |  |  | 32.94 | 23 | 10.9 | 2569.3199 | 1104 | 261.6 | 3934.9199 | 84.0907 | 23 | 55 | 162 | 51 | 97.86% | 0.11968 | 0.1233 | 38.4982 | 39.5317 | 92.1935 | 32.409 | 97.86% | 3443.037 | 99.04% | 99.27% | 85.02% |  |  | 99.15% | 0.88185
2020-10-11 | 136.8171 | 120.2848 | 120.2848 | 110.3573 | 98.4859 | 13.9393 | 13.9393 | 3471.5444 | 973.9932 | 230.794 | 612.2651 | 34.6108 | 15.6088 | 37.3254 | 109.9402 | 9091.1877 | 280.3527 |  |  | 28.5843 | 0.88653 | 27.973 | 4083.8095 | 2266.7572 | 1817.0523 | 843.0592 | 16.5323 | 9.9276 | 11.948 | 14.9457 | 10.4356 | 4.9456 | 3561.5942 | 7633.2108 | 10469.1159 | 2319.1776 | 5089.9195 | 8902.338 | 0.12852 | 0.12154 | 0.094247 | 16.8237 | 10.4065 | 12.1663 | 15.3384 | 32.4384 | 99.2302 | 103.0939 | 76.1188 | 46.5204 | 99.33% | 99.27% | 98.77% | 99.34% | 99.36% | 98.89% | 93.37 | 98.733 | 127.3252 |  |  |  | 32.94 | 23 | 10.9 | 2569.3199 | 1104 | 261.6 | 3934.9199 | 84.553 | 23 | 55 | 162 | 51 | 97.83% | 0.1208 | 0.12428 | 38.4079 | 39.3966 | 91.9348 | 33.1689 | 97.83% | 3534.2096 | 99.02% | 99.27% | 85.01% |  |  | 99.13% | 0.88653
2020-10-10 | 136.3957 | 120.0038 | 120.0038 | 110.365 | 98.5959 | 13.944 | 13.944 | 3462.223 | 971.3779 | 230.1743 | 611.3552 | 38.0117 | 17.1425 | 40.993 | 120.743 | 9480.297 | 277.3174 |  |  | 28.5475 | 0.88761 | 30.7217 | 4073.5782 | 2260.6708 | 1812.9074 | 841.5295 | 16.3919 | 9.6389 | 11.7673 | 14.9055 | 10.4076 | 4.9323 | 3702.4755 | 7928.9262 | 10868.6954 | 2411.6372 | 5289.441 | 9244.8025 | 0.12935 | 0.12318 | 0.09747 | 16.742 | 10.1363 | 12.0125 | 16.176 | 34.2317 | 104.7897 | 102.2833 | 74.9982 | 44.9161 | 99.29% | 99.23% | 98.69% | 99.33% | 99.35% | 98.87% | 92.7719 | 97.4222 | 123.1149 |  |  |  | 32.94 | 23 | 10.9 | 2569.3199 | 1104 | 261.6 | 3934.9199 | 84.6255 | 23 | 55 | 162 | 51 | 97.71% | 0.12227 | 0.1255 | 37.798 | 38.8908 | 90.8131 | 34.9971 | 97.71% | 3673.3278 | 98.97% | 99.26% | 84.99% |  |  | 99.08% | 0.88761
2020-10-09 | 134.8833 | 118.5484 | 118.5484 | 108.9815 | 97.0477 | 13.864 | 13.864 | 3471.2536 | 973.9116 | 230.7747 | 612.7688 | 40.0914 | 18.0804 | 43.2358 | 127.3492 | 9449.5344 | 274.2742 |  |  | 28.8546 | 0.87861 | 32.4025 | 4084.0224 | 2266.5674 | 1817.455 | 843.5435 | 16.3349 | 9.5669 | 11.6688 | 14.9444 | 10.4348 | 4.9452 | 3695.5289 | 7912.2772 | 10844.1568 | 2407.4816 | 5278.9999 | 9224.6986 | 0.13013 | 0.12436 | 0.099508 | 16.6202 | 10.0235 | 11.87 | 16.9613 | 35.9027 | 109.9271 | 100.9049 | 73.7221 | 43.6639 | 99.25% | 99.18% | 98.62% | 99.3% | 99.32% | 98.81% | 92.2183 | 96.4937 | 120.5936 |  |  |  | 32.94 | 23 | 10.9 | 2569.3199 | 1104 | 261.6 | 3934.9199 | 83.1356 | 23 | 55 | 162 | 51 | 97.58% | 0.12338 | 0.12647 | 37.5707 | 38.5137 | 89.4713 | 36.7028 | 97.58% | 3666.3484 | 98.91% | 99.23% | 85% |  |  | 99.04% | 0.87861
2020-10-08 | 133.1617 | 116.7877 | 116.7877 | 107.3985 | 95.5691 | 14.0069 | 14.0069 | 3471.3727 | 946.3975 | 233.3282 | 613.3365 | 44.0811 | 19.8797 | 47.5384 | 140.0222 | 9564.7198 | 269.3222 |  |  | 28.7904 | 0.88049 | 35.4956 | 4084.7091 | 2291.647 | 1793.0622 | 846.6647 | 16.3739 | 9.3892 | 11.703 | 15.1098 | 10.14 | 4.9999 | 3797.2796 | 7988.7213 | 10974.5587 | 2455.4758 | 5382.8334 | 9324.1443 | 0.13467 | 0.12503 | 0.10594 | 16.7608 | 9.9565 | 11.8596 | 18.5264 | 37.7005 | 121.158 | 98.7898 | 71.4097 | 41.5563 | 99.19% | 99.12% | 98.5% | 99.25% | 99.3% | 98.7% | 89.1074 | 95.9798 | 113.2754 |  |  |  | 32.94 | 22.1056 | 10.9 | 2569.3199 | 1061.07 | 261.6 | 3891.9899 | 81.5078 | 23 | 55 | 162 | 51 | 97.37% | 0.12699 | 0.13011 | 37.4662 | 38.5769 | 87.3249 | 39.9104 | 97.37% | 3715.2363 | 98.81% | 99.18% | 84.98% |  |  | 98.96% | 0.88049
2020-10-07 | 130.3703 | 114.101 | 114.101 | 104.7691 | 92.9316 | 13.8982 | 13.8982 | 3471.718 | 941.3229 | 233.8291 | 613.1298 | 44.4614 | 20.0512 | 47.9486 | 141.2304 | 9619.3222 | 262.4359 |  |  | 28.9112 | 0.87697 | 35.7771 | 4084.8478 | 2296.566 | 1788.2818 | 846.9589 | 16.2693 | 9.332 | 11.5936 | 15.1422 | 10.0856 | 5.0106 | 3827.0794 | 8027.2626 | 11034.7554 | 2471.0044 | 5417.9309 | 9372.0449 | 0.13821 | 0.12877 | 0.11326 | 16.6735 | 9.921 | 11.7477 | 18.5343 | 37.4267 | 121.3529 | 96.0828 | 68.687 | 38.7981 | 99.19% | 99.12% | 98.49% | 99.25% | 99.31% | 98.71% | 86.8271 | 93.1904 | 105.9539 |  |  |  | 32.94 | 21.94 | 10.9 | 2569.3199 | 1053.12 | 261.6 | 3884.0399 | 79.0632 | 23 | 55 | 162 | 51 | 97.36% | 0.13119 | 0.13397 | 37.1949 | 38.3423 | 84.5912 | 39.8875 | 97.36% | 3734.8378 | 98.81% | 99.18% | 84.99% |  |  | 98.96% | 0.87697
2020-10-06 | 124.2005 | 107.9198 | 107.9198 | 98.7257 | 86.8535 | 13.7642 | 13.7642 | 3472.6139 | 1081.8054 | 131.272 | 613.3746 | 58.2189 | 22.3173 | 72.6524 | 252.7066 | 9362.9077 | 245.879 |  |  | 29.027 | 0.87361 | 46.7071 | 4085.9885 | 2259.5365 | 1826.4521 | 744.6466 | 16.2807 | 9.1942 | 11.7606 | 14.898 | 11.5908 | 2.813 | 3670.322 | 8896.9334 | 10746.9372 | 2399.0151 | 5531.9365 | 9763.7559 | 0.14395 | 0.16263 | 0.078088 | 16.519 | 10.1426 | 13.2854 | 20.8254 | 63.5855 | 116.564 | 90.4124 | 62.2621 | 31.4701 | 99.07% | 98.69% | 97.41% | 99.13% | 98.85% | 98.81% | 83.3609 | 73.7861 | 153.6724 |  |  |  | 34.6294 | 26.9419 | 6.5385 | 2701.0912 | 1293.21 | 156.925 | 4151.2262 | 73.0853 | 23 | 74.875 | 260.4375 | 60 | 96.48% | 0.13939 | 0.14728 | 37.2355 | 39.947 | 78.9975 | 53.2033 | 96.48% | 3653.4004 | 98.41% | 98.99% | 84.99% |  |  | 98.61% | 0.87361
2020-10-05 | 115.7335 | 99.5455 | 99.5455 | 90.5186 | 78.5664 | 13.6812 | 13.6812 | 3473.6934 | 1183.3461 | 57.2587 | 614.5694 | 95.5253 | 32.7923 | 129.7433 | 480.4779 | 9233.8486 | 227.9612 |  |  | 29.0596 | 0.87267 | 73.199 | 4088.2628 | 2233.0886 | 1855.1742 | 671.8281 | 16.188 | 9.0269 | 11.652 | 14.7237 | 12.6787 | 1.227 | 3418.158 | 9210.3133 | 10023.6614 | 2258.3519 | 5387.6242 | 9605.5186 | 0.15512 | 0.20094 | 0.042429 | 16.2967 | 10.2198 | 14.2771 | 32.091 | 127.3992 | 98.1562 | 82.8305 | 55.0615 | 25.2361 | 98.55% | 97.59% | 95% | 98.58% | 97.64% | 98.98% | 77.3583 | 59.718 | 282.8265 |  |  |  | 36 | 31 | 3 | 2808 | 1488 | 72 | 4368 | 65.0401 | 23 | 91 | 337 | 67 | 93.91% | 0.15175 | 0.16887 | 36.8669 | 40.7936 | 71.8403 | 92.4926 | 93.91% | 3445.4749 | 97.23% | 98.34% | 84.97% |  |  | 97.58% | 0.87267
2020-10-04
2020-10-03
2020-10-02
2020-10-01
2020-09-30
2020-09-29
2020-09-28
2020-09-27
2020-09-26 | 182.1295 | 157.6587 | 157.6587 | 146.154 | 133.6807 | 13.7211 | 13.7211 | 3472.2218 | 1182.8448 | 57.2344 | 613.0135 | 60.3252 | 20.7087 | 81.9343 | 303.427 | 9397.0113 | 372.6285 |  |  | 28.8299 | 0.89139 | 46.2259 | 4085.2353 | 2232.1426 | 1853.0927 | 670.2479 | 24.4708 | 11.5047 | 12.3329 | 14.7174 | 12.6733 | 1.2265 | 3660.5145 | 9975.9461 | 10879.0275 | 2411.5611 | 5797.0792 | 10414.4466 | 0.090966 | 0.10307 | 0.014453 | 24.6668 | 13.0534 | 15.1669 | 19.3773 | 76.3436 | 58.3741 | 144.2188 | 109.6096 | 75.6412 | 99.14% | 98.59% | 97.09% | 99.2% | 98.68% | 99.44% | 131.9171 | 116.431 | 830.2693 |  |  |  | 36 | 31 | 3 | 2808 | 1488 | 72 | 4368 | 119.9594 | 23 | 91 | 337 | 67 | 96.39% | 0.082596 | 0.093827 | 48.3084 | 52.8872 | 133.9471 | 55.584 | 96.39% | 3696.7852 | 98.37% | 99.07% | 84.99% |  |  | 98.55% | 0.89139
2020-09-25 | 180.7761 | 156.6258 | 156.6258 | 145.3404 | 133.242 | 13.9301 | 13.9301 | 3436.718 | 1170.7501 | 56.6492 | 606.5591 | 63.308 | 21.7326 | 85.9855 | 318.4297 | 9577.1662 | 365.5265 |  |  | 28.8134 | 0.89183 | 48.5115 | 4043.2771 | 2209.3187 | 1833.9583 | 663.2083 | 24.1502 | 11.2854 | 12.1971 | 14.5669 | 12.5438 | 1.2139 | 3739.3561 | 10188.5883 | 11110.4056 | 2463.6832 | 5921.3991 | 10636.1933 | 0.091128 | 0.1037 | 0.014675 | 24.7243 | 13.0064 | 15.2397 | 19.7113 | 77.6722 | 59.3989 | 142.5611 | 107.876 | 73.7723 | 99.12% | 98.55% | 97.01% | 99.2% | 98.69% | 99.44% | 131.6835 | 115.7167 | 817.7205 |  |  |  | 36 | 31 | 3 | 2808 | 1488 | 72 | 4368 | 119.2974 | 23 | 91 | 337 | 67 | 96.29% | 0.082919 | 0.094151 | 47.6328 | 52.9704 | 132.0664 | 56.5479 | 96.29% | 3776.2981 | 98.32% | 99.07% | 85% |  |  | 98.52% | 0.89183
2020-09-24 | 181.8401 | 157.3788 | 157.3788 | 145.9129 | 133.5912 | 13.8921 | 13.8921 | 3465.1791 | 1183.6796 | 88.9187 | 612.8548 | 63.1677 | 20.4863 | 73.2093 | 375.2238 | 9532.4599 | 371.1166 |  |  | 28.9183 | 0.88906 | 47.5989 | 4078.0339 | 2192.5808 | 1885.4531 | 701.7735 | 24.4613 | 11.4659 | 12.2566 | 14.4566 | 12.6823 | 1.9054 | 3662.0557 | 9715.3538 | 11070.5076 | 2438.2468 | 5734.561 | 10363.4555 | 0.089487 | 0.10302 | 0.022314 | 24.5014 | 12.5305 | 14.5368 | 18.5747 | 68.8258 | 112.4054 | 143.6285 | 109.447 | 75.9188 | 99.16% | 98.72% | 96.38% | 99.24% | 98.8% | 98.92% | 134.0983 | 116.4808 | 537.7879 |  |  |  | 34.4583 | 30.2292 | 4.5417 | 2687.75 | 1451 | 109 | 4247.75 | 119.667 | 22.2292 | 79.4375 | 407.1458 | 68.5417 | 96.29% | 0.08307 | 0.092386 | 48.1838 | 51.5687 | 133.0962 | 56.8441 | 96.29% | 3767.6093 | 98.32% | 99.05% | 84.97% |  |  | 98.51% | 0.88906
2020-09-23 | 181.9702 | 157.4837 | 157.4837 | 145.8581 | 133.541 | 13.7463 | 13.7463 | 3470.5635 | 1186.5174 | 98.8765 | 612.4453 | 62.3285 | 19.8729 | 68.6517 | 386.6174 | 9444.4978 | 372.0847 |  |  | 28.8158 | 0.89177 | 46.9979 | 4083.0088 | 2185.1696 | 1897.8391 | 711.3217 | 24.4865 | 11.6256 | 12.3252 | 14.4077 | 12.7127 | 2.1188 | 3607.5084 | 9510.4848 | 10983.4909 | 2408.9249 | 5634.1953 | 10211.6605 | 0.089203 | 0.10297 | 0.024593 | 24.4199 | 12.5452 | 14.4671 | 18.2315 | 66.0486 | 131.1007 | 144.0354 | 110.0969 | 76.828 | 99.18% | 98.78% | 96.21% | 99.24% | 98.83% | 98.72% | 134.525 | 116.5377 | 487.9355 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 119.7988 | 22 | 76 | 428 | 69 | 96.31% | 0.083271 | 0.092069 | 48.4374 | 51.4323 | 133.517 | 56.8559 | 96.31% | 3733.8816 | 98.33% | 99.03% | 85% |  |  | 98.51% | 0.89177
2020-09-22 | 181.9215 | 157.3596 | 157.3596 | 145.7134 | 133.4459 | 13.7028 | 13.7028 | 3472.3003 | 1187.1112 | 98.9259 | 613.3829 | 62.5744 | 19.9513 | 68.9225 | 388.1426 | 9422.8792 | 371.4424 |  |  | 28.707 | 0.89465 | 47.1834 | 4085.6833 | 2186.2632 | 1899.4201 | 712.3089 | 24.5619 | 11.6462 | 12.3725 | 14.4149 | 12.719 | 2.1198 | 3601.6686 | 9489.2305 | 10957.0471 | 2405.3108 | 5623.6151 | 10187.9782 | 0.089551 | 0.10339 | 0.024669 | 24.469 | 12.5489 | 14.491 | 18.3994 | 66.682 | 132.4164 | 144.0109 | 110.0602 | 76.8776 | 99.17% | 98.77% | 96.19% | 99.24% | 98.81% | 98.7% | 134.0019 | 116.0656 | 486.4345 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 119.6816 | 22 | 76 | 428 | 69 | 96.29% | 0.083598 | 0.092434 | 48.5806 | 51.5089 | 133.5147 | 57.3943 | 96.29% | 3727.3142 | 98.32% | 99.01% | 84.99% |  |  | 98.5% | 0.89465
2020-09-21 | 179.8664 | 155.2066 | 155.2066 | 143.5674 | 130.9925 | 13.6138 | 13.6138 | 3468.2909 | 1185.7405 | 98.8117 | 612.9555 | 58.8162 | 18.753 | 64.7831 | 364.831 | 8799.812 | 367.6921 |  |  | 28.5966 | 0.89758 | 44.3495 | 4081.2464 | 2183.7387 | 1897.5077 | 711.7672 | 24.6598 | 11.6393 | 12.2946 | 14.3983 | 12.7044 | 2.1174 | 3387.6319 | 8923.2008 | 10302.8559 | 2262.4643 | 5288.8935 | 9579.9931 | 0.090563 | 0.10399 | 0.024495 | 24.6057 | 12.5591 | 14.4155 | 18.4252 | 66.7852 | 132.6433 | 142.7041 | 109.6526 | 77.5903 | 99.17% | 98.78% | 96.19% | 99.19% | 98.74% | 98.62% | 132.5049 | 115.391 | 489.9045 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 117.4518 | 22 | 76 | 428 | 69 | 96.29% | 0.08429 | 0.093272 | 48.5937 | 51.5803 | 132.8873 | 57.4805 | 96.29% | 3505.6176 | 98.32% | 98.95% | 84.98% |  |  | 98.5% | 0.89758
2020-09-20 | 178.2391 | 154.0229 | 154.0229 | 142.5677 | 130.5419 | 13.5901 | 13.5901 | 3437.63 | 1175.2581 | 97.9382 | 606.6105 | 61.3688 | 19.5668 | 67.5946 | 380.6642 | 9097.4596 | 359.6585 |  |  | 28.7655 | 0.8931 | 46.2743 | 4044.2405 | 2164.4337 | 1879.8068 | 704.5487 | 24.2161 | 11.4552 | 12.0844 | 14.271 | 12.5921 | 2.0987 | 3488.3784 | 9194.5901 | 10617.6116 | 2329.5176 | 5447.6821 | 9871.9959 | 0.090399 | 0.10432 | 0.024823 | 24.4985 | 12.5398 | 14.3895 | 18.4139 | 66.7192 | 132.4535 | 140.9911 | 107.8047 | 75.508 | 99.16% | 98.76% | 96.14% | 99.21% | 98.78% | 98.66% | 132.7453 | 115.0332 | 483.4253 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 116.9097 | 22 | 76 | 428 | 69 | 96.24% | 0.084361 | 0.093289 | 47.7558 | 51.4277 | 130.8561 | 57.4305 | 96.24% | 3610.4421 | 98.3% | 98.98% | 85% |  |  | 98.5% | 0.8931
2020-09-19 | 181.0193 | 156.4778 | 156.4778 | 144.9637 | 132.5737 | 13.6537 | 13.6537 | 3471.6677 | 1186.8949 | 98.9079 | 612.1293 | 61.0583 | 19.4679 | 67.2526 | 378.7382 | 9475.7592 | 370.258 |  |  | 28.8681 | 0.89039 | 46.0401 | 4083.797 | 2185.8648 | 1897.9321 | 711.0372 | 24.5414 | 11.5141 | 12.1959 | 14.4123 | 12.7167 | 2.1195 | 3621.9842 | 9555.7005 | 11038.5149 | 2418.189 | 5658.56 | 10261.4824 | 0.089674 | 0.10377 | 0.024929 | 24.4693 | 12.4263 | 14.3251 | 17.7696 | 64.3447 | 127.648 | 143.1012 | 109.1105 | 75.7013 | 99.19% | 98.81% | 96.31% | 99.27% | 98.86% | 98.76% | 133.8173 | 115.636 | 481.3723 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 118.9922 | 22 | 76 | 428 | 69 | 96.4% | 0.083827 | 0.09265 | 48.2515 | 51.2207 | 132.6155 | 55.3975 | 96.4% | 3749.4638 | 98.37% | 99.05% | 85.01% |  |  | 98.55% | 0.89039
2020-09-18 | 181.7454 | 157.3106 | 157.3106 | 145.7545 | 133.5495 | 13.7386 | 13.7386 | 3472.8488 | 1187.2987 | 98.9416 | 611.7937 | 60.0274 | 19.1392 | 66.1172 | 372.344 | 9752.0795 | 370.7174 |  |  | 28.9922 | 0.88712 | 45.2628 | 4084.6425 | 2186.6085 | 1898.034 | 710.7353 | 24.4349 | 11.5561 | 12.2452 | 14.4172 | 12.7211 | 2.1202 | 3713.196 | 9805.7205 | 11331.3213 | 2478.5221 | 5803.3928 | 10531.7783 | 0.089132 | 0.10343 | 0.025039 | 24.3573 | 12.473 | 14.3933 | 16.9876 | 61.4742 | 121.8649 | 143.4925 | 109.1075 | 75.1162 | 99.23% | 98.86% | 96.46% | 99.31% | 98.94% | 98.84% | 134.6316 | 116.0193 | 479.2482 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 119.7618 | 22 | 76 | 428 | 69 | 96.54% | 0.083453 | 0.092195 | 48.2361 | 51.2236 | 132.6926 | 52.9367 | 96.54% | 3844.6675 | 98.44% | 99.12% | 85.02% |  |  | 98.61% | 0.88712
2020-09-17 | 182.138 | 157.6298 | 157.6298 | 146.0786 | 133.7883 | 13.8898 | 13.8898 | 3471.6931 | 1186.9036 | 98.9086 | 613.7999 | 67.015 | 21.3671 | 73.8137 | 415.6874 | 9818.5706 | 372.0985 |  |  | 29.1312 | 0.88348 | 50.5317 | 4085.4929 | 2185.8808 | 1899.6121 | 712.7085 | 24.5082 | 11.5512 | 12.1964 | 14.4124 | 12.7168 | 2.1195 | 3736.1103 | 9835.0876 | 11352.9439 | 2495.5885 | 5831.4489 | 10557.7334 | 0.088656 | 0.10291 | 0.024856 | 24.4155 | 12.4423 | 14.2716 | 18.7518 | 67.997 | 135.1143 | 143.623 | 109.1762 | 75.3335 | 99.14% | 98.73% | 96.06% | 99.25% | 98.83% | 98.72% | 135.3545 | 116.6096 | 482.7759 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 119.9249 | 22 | 76 | 428 | 69 | 96.17% | 0.083009 | 0.091711 | 48.2558 | 51.1294 | 132.7811 | 58.5159 | 96.17% | 3865.7443 | 98.27% | 99.03% | 84.98% |  |  | 98.47% | 0.88348
2020-09-16 | 181.5794 | 157.1693 | 157.1693 | 145.6245 | 133.3184 | 13.8814 | 13.8814 | 3469.9633 | 1186.3122 | 98.8594 | 612.5038 | 68.1075 | 21.7154 | 75.017 | 422.4641 | 9801.1966 | 370.8043 |  |  | 29.0338 | 0.88603 | 51.3555 | 4082.4671 | 2184.7917 | 1897.6754 | 711.3631 | 24.4101 | 11.5448 | 12.2776 | 14.4052 | 12.7105 | 2.1184 | 3725.3978 | 9812.9941 | 11328.6447 | 2488.223 | 5816.2508 | 10534.5629 | 0.089155 | 0.1035 | 0.025016 | 24.3481 | 12.4589 | 14.4095 | 19.1595 | 69.4515 | 137.9474 | 143.1604 | 108.8093 | 75.0295 | 99.13% | 98.71% | 95.99% | 99.23% | 98.81% | 98.69% | 134.5974 | 115.9411 | 479.6836 |  |  |  | 34 | 30 | 5 | 2652 | 1440 | 120 | 4212 | 119.427 | 22 | 76 | 428 | 69 | 96.09% | 0.083483 | 0.092232 | 48.2325 | 51.2165 | 132.2962 | 59.774 | 96.09% | 3855.2507 | 98.23% | 99.01% | 85% |  |  | 98.44% | 0.88603
2020-09-15 | 179.5257 | 154.9893 | 154.9893 | 143.2543 | 130.8815 | 13.7052 | 13.7052 | 3470.377 | 1203.8463 | 91.9332 | 612.5472 | 63.0008 | 20.0872 | 69.3922 | 390.7879 | 9171.5826 | 369.559 |  |  | 28.9145 | 0.88916 | 47.0109 | 4082.9242 | 2174.5975 | 1908.3267 | 704.4804 | 24.5363 | 11.735 | 12.3103 | 14.338 | 12.8984 | 1.97 | 3492.3827 | 9341.7354 | 10685.1244 | 2339.5932 | 5487.7711 | 9983.3649 | 0.089809 | 0.10587 | 0.023231 | 24.4059 | 12.6368 | 14.5606 | 18.8273 | 69.3404 | 125.6589 | 141.9548 | 108.3248 | 75.3999 | 99.14% | 98.74% | 96.09% | 99.2% | 98.74% | 98.74% | 133.6166 | 113.3425 | 516.5404 |  |  |  | 32.3234 | 29.0779 | 4.4411 | 2521.2255 | 1395.7379 | 106.5872 | 4023.5507 | 117.2429 | 22 | 76 | 428 | 69 | 96.17% | 0.084297 | 0.093618 | 48.5816 | 51.6032 | 131.6742 | 58.8706 | 96.17% | 3634.1611 | 98.27% | 98.98% | 85% |  |  | 98.46% | 0.88916
2020-09-14 | 177.9023 | 153.3087 | 153.3087 | 141.5242 | 129.2247 | 13.5921 | 13.5921 | 3468.5759 | 1218.1372 | 85.9356 | 612.0042 | 60.1801 | 19.1878 | 66.2853 | 373.2908 | 8682.4522 | 366.2507 |  |  | 28.8066 | 0.89201 | 44.5012 | 4080.5801 | 2164.5031 | 1916.077 | 697.9398 | 24.5936 | 11.7845 | 12.2428 | 14.2714 | 13.0515 | 1.8415 | 3300.5508 | 8945.4205 | 10149.0906 | 2216.8567 | 5214.9629 | 9521.9433 | 0.09027 | 0.10772 | 0.021602 | 24.4298 | 12.6813 | 14.5984 | 18.9525 | 70.754 | 118.0159 | 141.025 | 108.0809 | 76.039 | 99.13% | 98.73% | 96.08% | 99.15% | 98.64% | 98.76% | 132.9348 | 111.4038 | 555.4957 |  |  |  | 31 | 28.35 | 4 | 2418 | 1360.8 | 96 | 3874.8 | 115.5995 | 22 | 76 | 428 | 69 | 96.14% | 0.084866 | 0.094696 | 48.6209 | 51.7094 | 131.2635 | 59.3824 | 96.14% | 3450.7556 | 98.26% | 98.92% | 85% |  |  | 98.45% | 0.89201
2020-09-13 | 177.5692 | 153.3616 | 153.3616 | 141.8386 | 129.5142 | 13.6256 | 13.6256 | 3445.9203 | 1210.1808 | 85.3743 | 608.4999 | 63.2432 | 20.1645 | 69.6591 | 392.2909 | 9026.4098 | 363.2465 |  |  | 28.8686 | 0.89037 | 46.7662 | 4054.4203 | 2150.3653 | 1904.055 | 693.8742 | 24.2076 | 11.523 | 12.2054 | 14.1782 | 12.9662 | 1.8294 | 3416.7096 | 9254.275 | 10497.637 | 2295.1789 | 5397.0414 | 9849.8458 | 0.089873 | 0.10756 | 0.021787 | 24.2779 | 12.5152 | 14.6809 | 19.0767 | 71.2464 | 118.8921 | 140.4647 | 107.3375 | 74.763 | 99.12% | 98.71% | 96.02% | 99.17% | 98.68% | 98.79% | 133.5223 | 111.5699 | 550.7761 |  |  |  | 31 | 28.35 | 4 | 2418 | 1360.8 | 96 | 3874.8 | 115.9049 | 22 | 76 | 428 | 69 | 96.08% | 0.084638 | 0.094396 | 47.9361 | 51.474 | 130.333 | 59.7879 | 96.08% | 3571.6997 | 98.23% | 98.95% | 84.99% |  |  | 98.44% | 0.89037
2020-09-12 | 178.6511 | 154.4929 | 154.4929 | 142.9917 | 130.6213 | 13.7294 | 13.7294 | 3449.7469 | 1211.5246 | 85.4691 | 609.1966 | 65.4079 | 20.8547 | 72.0435 | 405.7184 | 9361.4428 | 365.5477 |  |  | 28.85 | 0.89086 | 48.367 | 4058.9434 | 2152.7532 | 1906.1903 | 694.6657 | 24.1581 | 11.5012 | 12.2156 | 14.194 | 12.9806 | 1.8315 | 3539.5957 | 9587.145 | 10875.2816 | 2377.7206 | 5591.1596 | 10204.1619 | 0.089643 | 0.10765 | 0.022023 | 24.1877 | 12.4705 | 14.668 | 19.0764 | 71.2451 | 118.8894 | 141.0583 | 107.4174 | 74.0849 | 99.12% | 98.71% | 96.02% | 99.2% | 98.73% | 98.83% | 133.8641 | 111.4676 | 544.8752 |  |  |  | 31 | 28.35 | 4 | 2418 | 1360.8 | 96 | 3874.8 | 116.9258 | 22 | 76 | 428 | 69 | 96.09% | 0.084588 | 0.094293 | 47.8749 | 51.3262 | 130.549 | 59.7869 | 96.09% | 3700.1595 | 98.23% | 98.99% | 84.99% |  |  | 98.44% | 0.89086
2020-09-11 | 179.8362 | 155.4169 | 155.4169 | 143.8882 | 131.4479 | 13.7664 | 13.7664 | 3472.6328 | 1192.3453 | 101.9338 | 613.3291 | 66.8723 | 21.3216 | 73.6565 | 414.8024 | 9529.2371 | 371.3217 |  |  | 29.0442 | 0.88576 | 50.8411 | 4085.9619 | 2178.3537 | 1907.6082 | 715.2629 | 24.4193 | 11.5287 | 12.2915 | 14.3628 | 12.7751 | 2.1843 | 3616.8366 | 9523.3282 | 11037.1427 | 2421.6807 | 5645.8363 | 10243.0424 | 0.08968 | 0.10475 | 0.025879 | 24.2754 | 12.3432 | 14.349 | 19.2661 | 70.5857 | 143.5883 | 141.8584 | 108.0253 | 74.7605 | 99.12% | 98.7% | 95.95% | 99.2% | 98.75% | 98.6% | 133.8086 | 114.5585 | 463.6901 |  |  |  | 31.8732 | 28.35 | 4.8473 | 2486.1118 | 1360.8 | 116.335 | 3963.2468 | 117.6948 | 22 | 76 | 428 | 69 | 96.07% | 0.084294 | 0.092982 | 48.2394 | 50.9675 | 131.2507 | 60.2318 | 96.07% | 3758.2942 | 98.22% | 98.96% | 84.99% |  |  | 98.42% | 0.88576
2020-09-10 | 177.9863 | 154.127 | 154.127 | 142.8154 | 130.7467 | 13.5811 | 13.5811 | 3429.3995 | 1173.3995 | 103.0605 | 605.5122 | 64.1466 | 20.4525 | 70.6542 | 397.8949 | 9790.5262 | 361.7605 |  |  | 29.174 | 0.88236 | 48.9724 | 4034.9117 | 2152.9396 | 1881.9722 | 708.5727 | 23.8592 | 11.3117 | 12.1051 | 14.1952 | 12.5721 | 2.2084 | 3711.8232 | 9741.6152 | 11331.952 | 2483.3479 | 5786.1664 | 10496.7325 | 0.089364 | 0.10434 | 0.026802 | 24.1812 | 12.3383 | 14.3661 | 17.7434 | 64.7676 | 135.3717 | 140.1611 | 106.3126 | 72.7058 | 99.18% | 98.78% | 96.21% | 99.29% | 98.88% | 98.71% | 134.2828 | 115.0032 | 447.7319 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 117.1847 | 22 | 76 | 428 | 69 | 96.32% | 0.084148 | 0.09261 | 47.2761 | 50.8856 | 129.2595 | 55.4237 | 96.32% | 3854.2551 | 98.34% | 99.06% | 84.99% |  |  | 98.55% | 0.88236
2020-09-09 | 177.7188 | 153.3436 | 153.3436 | 141.7984 | 129.4791 | 13.6948 | 13.6948 | 3465.9526 | 1185.9064 | 104.159 | 611.8778 | 63.5746 | 20.2702 | 70.0242 | 394.347 | 9313.6503 | 365.4937 |  |  | 29.076 | 0.88492 | 48.5357 | 4077.8304 | 2175.8872 | 1901.9432 | 716.0368 | 24.3752 | 11.5452 | 12.2657 | 14.3465 | 12.7061 | 2.232 | 3546.1638 | 9303.3769 | 10819.9468 | 2372.7953 | 5527.0617 | 10023.5203 | 0.090635 | 0.10549 | 0.026764 | 24.3155 | 12.3955 | 14.3299 | 18.6546 | 68.1127 | 142.4083 | 140.0738 | 106.591 | 73.7981 | 99.15% | 98.73% | 96.07% | 99.21% | 98.77% | 98.58% | 132.3995 | 113.7582 | 448.364 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.7932 | 22 | 76 | 428 | 69 | 96.18% | 0.085168 | 0.093797 | 48.1861 | 51.0408 | 129.6862 | 58.2812 | 96.18% | 3681.9755 | 98.27% | 98.97% | 85% |  |  | 98.47% | 0.88492
2020-09-08 | 175.4973 | 150.9951 | 150.9951 | 139.1837 | 126.7752 | 13.8121 | 13.8121 | 3471.1663 | 1187.6903 | 104.3157 | 612.9672 | 61.2835 | 19.5397 | 67.5007 | 380.1355 | 8510.0899 | 361.3587 |  |  | 29.0964 | 0.88439 | 46.7866 | 4084.1335 | 2179.1603 | 1904.9732 | 717.2828 | 24.5021 | 11.8114 | 12.2583 | 14.3681 | 12.7253 | 2.2353 | 3268.8481 | 8569.699 | 9963.411 | 2187.6619 | 5093.3012 | 9231.5791 | 0.091685 | 0.10602 | 0.02639 | 24.385 | 12.6504 | 14.2835 | 19.5217 | 71.3137 | 149.1865 | 138.5934 | 106.1483 | 74.9101 | 99.11% | 98.67% | 95.88% | 99.11% | 98.6% | 98.38% | 130.8827 | 113.184 | 454.7116 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 112.9587 | 22 | 76 | 428 | 69 | 96.01% | 0.085826 | 0.094628 | 48.5719 | 51.3188 | 128.9887 | 61.0108 | 96.01% | 3393.5363 | 98.19% | 98.83% | 84.99% |  |  | 98.4% | 0.88439
2020-09-07 | 174.0947 | 149.6579 | 149.6579 | 137.8908 | 125.543 | 13.6202 | 13.6202 | 3466.5815 | 1186.1216 | 104.1779 | 612.0685 | 64.4005 | 20.5335 | 70.9339 | 399.47 | 8607.5034 | 357.1855 |  |  | 29.2333 | 0.88082 | 49.1663 | 4078.65 | 2176.282 | 1902.368 | 716.2464 | 24.4368 | 11.7671 | 12.328 | 14.3491 | 12.7084 | 2.2324 | 3299.5339 | 8646.175 | 10049.8156 | 2208.5142 | 5140.1204 | 9312.8285 | 0.092042 | 0.1068 | 0.026742 | 24.3693 | 12.6292 | 14.3961 | 20.2121 | 73.8607 | 154.5746 | 137.3163 | 104.8083 | 73.5299 | 99.07% | 98.62% | 95.71% | 99.08% | 98.56% | 98.34% | 130.3746 | 112.3567 | 448.7365 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 111.9514 | 22 | 76 | 428 | 69 | 95.84% | 0.086318 | 0.09513 | 48.5319 | 51.3946 | 127.589 | 63.1832 | 95.84% | 3425.0885 | 98.12% | 98.8% | 84.99% |  |  | 98.35% | 0.88082
2020-09-06 | 173.3128 | 149.2815 | 149.2815 | 137.6759 | 125.4373 | 13.4691 | 13.4691 | 3442.7132 | 1177.9549 | 103.4606 | 608.6196 | 66.5243 | 21.2106 | 73.2731 | 412.6435 | 8887.9952 | 351.0401 |  |  | 29.576 | 0.87195 | 50.7877 | 4051.3328 | 2161.2977 | 1890.0351 | 712.0802 | 24.0313 | 11.6055 | 12.2121 | 14.2503 | 12.6209 | 2.217 | 3429.0457 | 8980.3144 | 10436.7516 | 2295.4219 | 5340.5674 | 9672.0771 | 0.091058 | 0.10615 | 0.026927 | 24.2053 | 12.5745 | 14.3842 | 19.749 | 72.193 | 151.1457 | 136.4571 | 103.6732 | 71.7904 | 99.08% | 98.63% | 95.73% | 99.14% | 98.65% | 98.44% | 131.7838 | 113.0486 | 445.6445 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 112.0222 | 22 | 76 | 428 | 69 | 95.87% | 0.085626 | 0.094294 | 47.849 | 51.164 | 126.3188 | 61.7501 | 95.87% | 3559.029 | 98.13% | 98.87% | 84.98% |  |  | 98.38% | 0.87195
2020-09-05 | 176.9859 | 152.7878 | 152.7878 | 141.2831 | 129.0155 | 13.6576 | 13.6576 | 3463.1499 | 1184.9475 | 104.0748 | 611.4705 | 68.5566 | 21.8586 | 75.5116 | 425.2495 | 9529.2832 | 363.2792 |  |  | 29.4459 | 0.8753 | 52.3392 | 4074.6204 | 2174.1277 | 1900.4927 | 715.5452 | 24.1982 | 11.5047 | 12.2154 | 14.3349 | 12.6959 | 2.2302 | 3629.0955 | 9513.853 | 11060.7701 | 2428.796 | 5654.5447 | 10248.4989 | 0.090143 | 0.10535 | 0.026972 | 24.1671 | 12.3658 | 14.2856 | 19.4233 | 70.9563 | 148.4435 | 139.1946 | 105.4826 | 72.3754 | 99.1% | 98.66% | 95.85% | 99.2% | 98.75% | 98.55% | 133.1224 | 113.9049 | 444.914 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.3757 | 22 | 76 | 428 | 69 | 95.98% | 0.084902 | 0.093448 | 47.9183 | 50.8185 | 128.5286 | 60.7045 | 95.98% | 3767.5126 | 98.18% | 98.95% | 84.99% |  |  | 98.41% | 0.8753
2020-09-04 | 178.3318 | 154.0125 | 154.0125 | 142.4546 | 130.0126 | 13.7825 | 13.7825 | 3468.8112 | 1186.8845 | 104.2449 | 612.7816 | 69.9745 | 22.3107 | 77.0734 | 434.0449 | 9640.6958 | 368.5562 |  |  | 29.2669 | 0.87994 | 53.4217 | 4081.5929 | 2177.6818 | 1903.9111 | 717.0265 | 24.3192 | 11.5579 | 12.2353 | 14.3583 | 12.7166 | 2.2338 | 3656.6363 | 9581.8394 | 11138.0395 | 2447.4688 | 5696.4022 | 10320.9351 | 0.090077 | 0.10521 | 0.02692 | 24.2248 | 12.3882 | 14.2639 | 19.8104 | 72.3909 | 151.4952 | 140.2639 | 106.3544 | 73.0167 | 99.09% | 98.65% | 95.79% | 99.19% | 98.73% | 98.53% | 133.2199 | 114.0543 | 445.7605 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 116.2505 | 22 | 76 | 428 | 69 | 95.93% | 0.084815 | 0.093358 | 48.1125 | 50.8769 | 129.5273 | 61.9264 | 95.93% | 3795.734 | 98.16% | 98.94% | 84.99% |  |  | 98.38% | 0.87994
2020-09-03 | 176.4009 | 152.3971 | 152.3971 | 140.963 | 128.7215 | 13.6275 | 13.6275 | 3444.6557 | 1178.6195 | 103.519 | 607.9722 | 70.9408 | 22.6188 | 78.1377 | 440.0385 | 9604.9318 | 360.3376 |  |  | 29.0269 | 0.88621 | 54.1594 | 4052.6278 | 2162.5172 | 1890.1106 | 711.4911 | 24.0038 | 11.4341 | 12.2166 | 14.2584 | 12.6281 | 2.2183 | 3645.1387 | 9554.0486 | 11105.8843 | 2439.7277 | 5679.0758 | 10291.068 | 0.091111 | 0.10653 | 0.027319 | 24.1691 | 12.3924 | 14.4098 | 20.1498 | 73.6225 | 154.0497 | 138.686 | 105.0479 | 71.9596 | 99.07% | 98.62% | 95.72% | 99.17% | 98.7% | 98.5% | 131.7069 | 112.6408 | 439.2595 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.0437 | 22 | 76 | 428 | 69 | 95.86% | 0.08584 | 0.094471 | 47.6545 | 50.9713 | 127.9329 | 62.9823 | 95.86% | 3784.0483 | 98.13% | 98.92% | 85% |  |  | 98.35% | 0.88621
2020-09-02 | 177.2803 | 153.0502 | 153.0502 | 141.4489 | 129.0614 | 13.772 | 13.772 | 3455.4392 | 1182.3092 | 103.843 | 610.107 | 70.9023 | 22.6065 | 78.0953 | 439.7996 | 9618.497 | 364.5027 |  |  | 28.9476 | 0.88829 | 54.13 | 4065.5462 | 2169.287 | 1896.2592 | 713.9501 | 24.2301 | 11.6014 | 12.3035 | 14.303 | 12.6676 | 2.2252 | 3640.507 | 9539.9001 | 11088.7791 | 2436.7228 | 5671.3572 | 10275.5306 | 0.091193 | 0.10665 | 0.027338 | 24.28 | 12.5115 | 14.4369 | 20.2744 | 74.0871 | 155.0452 | 139.3227 | 105.5112 | 72.3045 | 99.07% | 98.62% | 95.72% | 99.17% | 98.69% | 98.49% | 131.5892 | 112.52 | 438.9551 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.2697 | 22 | 76 | 428 | 69 | 95.85% | 0.085922 | 0.094562 | 48.1349 | 51.2284 | 128.5778 | 63.3772 | 95.85% | 3779.0539 | 98.12% | 98.91% | 84.99% |  |  | 98.34% | 0.88829
2020-09-01 | 175.2781 | 151.1376 | 151.1376 | 139.4927 | 127.1794 | 13.3947 | 13.3947 | 3429.2123 | 1173.3354 | 103.0549 | 606.6863 | 72.0246 | 22.9644 | 79.3315 | 446.7615 | 9384.1368 | 357.5534 |  |  | 28.7735 | 0.89289 | 54.9869 | 4035.8986 | 2152.822 | 1883.0766 | 709.7412 | 24.1406 | 11.6449 | 12.235 | 14.1944 | 12.5715 | 2.2083 | 3575.0733 | 9354.1905 | 10867.2521 | 2393.7076 | 5565.8555 | 10072.9409 | 0.091868 | 0.10743 | 0.027458 | 24.4534 | 12.685 | 14.4814 | 20.914 | 76.4982 | 160.2728 | 137.9595 | 104.4878 | 71.8105 | 99.04% | 98.57% | 95.56% | 99.13% | 98.63% | 98.41% | 130.6224 | 111.7029 | 437.0291 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 113.7199 | 22 | 76 | 428 | 69 | 95.71% | 0.086541 | 0.095256 | 48.0204 | 51.6198 | 127.3935 | 65.4202 | 95.71% | 3709.8629 | 98.06% | 98.85% | 84.97% |  |  | 98.29% | 0.89289
2020-08-31
2020-08-30 | 174.9617 | 151.1659 | 151.1659 | 139.7718 | 127.7715 | 13.7406 | 13.7406 | 3424.4297 | 1171.699 | 102.9111 | 604.7041 | 61.8902 | 19.7331 | 68.1689 | 383.8985 | 9040.1815 | 355.0169 |  |  | 28.9656 | 0.88782 | 47.2498 | 4029.1339 | 2149.8196 | 1879.3143 | 707.6153 | 23.7957 | 11.3941 | 11.9565 | 14.1746 | 12.5539 | 2.2052 | 3407.2286 | 8936.1838 | 10391.6482 | 2279.9978 | 5309.8427 | 9627.3403 | 0.091178 | 0.10563 | 0.026524 | 24.1685 | 12.4542 | 14.2184 | 18.7342 | 68.4169 | 143.0777 | 138.0218 | 105.5199 | 73.8138 | 99.13% | 98.72% | 96.01% | 99.18% | 98.71% | 98.51% | 131.6111 | 113.6087 | 452.4168 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 113.9722 | 22 | 76 | 428 | 69 | 96.13% | 0.085457 | 0.094178 | 47.1464 | 50.8411 | 128.0154 | 58.5379 | 96.13% | 3537.4888 | 98.25% | 98.92% | 84.99% |  |  | 98.47% | 0.88782
2020-08-29 | 177.3313 | 153.3062 | 153.3062 | 141.8562 | 129.5003 | 13.7313 | 13.7313 | 3451.0427 | 1180.8049 | 103.7109 | 609.4607 | 66.3846 | 21.1661 | 73.1193 | 411.777 | 9400.8836 | 362.7831 |  |  | 28.9732 | 0.88762 | 50.681 | 4060.5034 | 2166.5269 | 1893.9765 | 713.1716 | 24.0252 | 11.45 | 12.1188 | 14.2848 | 12.6515 | 2.2224 | 3575.517 | 9374.4696 | 10899.6359 | 2392.828 | 5571.3323 | 10098.7647 | 0.090743 | 0.10558 | 0.026834 | 24.1192 | 12.37 | 14.2431 | 19.2916 | 70.4687 | 147.4076 | 139.7291 | 106.3588 | 73.512 | 99.12% | 98.69% | 95.92% | 99.19% | 98.74% | 98.54% | 132.2413 | 113.6544 | 447.1928 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.7649 | 22 | 76 | 428 | 69 | 96.05% | 0.085267 | 0.0939 | 47.594 | 50.7323 | 129.2216 | 60.2891 | 96.05% | 3711.9606 | 98.21% | 98.94% | 84.99% |  |  | 98.42% | 0.88762
2020-08-28 | 177.2031 | 153.1069 | 153.1069 | 141.666 | 129.4118 | 13.8225 | 13.8225 | 3454.9899 | 1182.1554 | 103.8295 | 609.8545 | 68.273 | 21.7682 | 75.1992 | 423.4904 | 9501.6119 | 363.5635 |  |  | 29.2497 | 0.88039 | 52.1227 | 4064.8443 | 2169.0049 | 1895.8394 | 713.684 | 24.0962 | 11.4409 | 12.1923 | 14.3011 | 12.666 | 2.2249 | 3635.7979 | 9533.62 | 11084.6465 | 2433.159 | 5665.5372 | 10270.1967 | 0.0904 | 0.10558 | 0.027024 | 24.1527 | 12.3433 | 14.3148 | 19.3747 | 70.7684 | 148.0248 | 139.2755 | 105.6122 | 72.4828 | 99.11% | 98.67% | 95.88% | 99.2% | 98.75% | 98.56% | 132.743 | 113.6537 | 444.0463 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.6128 | 22 | 76 | 428 | 69 | 96% | 0.085119 | 0.093691 | 47.7294 | 50.8108 | 128.5861 | 60.5464 | 96% | 3774.6649 | 98.19% | 98.96% | 85% |  |  | 98.42% | 0.88039
2020-08-27 | 175.3927 | 151.5271 | 151.5271 | 140.1302 | 128.0608 | 13.8431 | 13.8431 | 3438.4688 | 1176.5026 | 103.333 | 607.6663 | 69.6688 | 22.2132 | 76.7367 | 432.1486 | 9503.039 | 357.5486 |  |  | 29.3916 | 0.87671 | 53.1883 | 4046.135 | 2158.6331 | 1887.5019 | 710.9993 | 23.8656 | 11.3969 | 12.13 | 14.2327 | 12.6054 | 2.2143 | 3665.0147 | 9602.5993 | 11162.0251 | 2453.1074 | 5709.1553 | 10343.2303 | 0.090773 | 0.10644 | 0.027459 | 24.0853 | 12.3741 | 14.3207 | 19.4346 | 71.0225 | 148.643 | 137.4623 | 103.8234 | 70.697 | 99.09% | 98.66% | 95.82% | 99.21% | 98.76% | 98.56% | 132.1973 | 112.7371 | 437.0149 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 114.2157 | 22 | 76 | 428 | 69 | 95.95% | 0.085657 | 0.094232 | 47.3925 | 50.7801 | 126.6572 | 60.7545 | 95.95% | 3804.3074 | 98.17% | 98.96% | 84.98% |  |  | 98.41% | 0.87671
2020-08-26 | 177.0283 | 152.7837 | 152.7837 | 141.2092 | 128.9727 | 13.738 | 13.738 | 3470.3989 | 1187.4278 | 104.2926 | 612.9963 | 71.5312 | 22.807 | 78.788 | 443.7006 | 9672.2164 | 365.0965 |  |  | 29.4005 | 0.87648 | 54.6101 | 4083.3952 | 2178.6785 | 1904.7167 | 717.2889 | 24.2446 | 11.5745 | 12.282 | 14.3649 | 12.7224 | 2.2348 | 3715.8907 | 9736.8909 | 11317.9948 | 2487.1613 | 5788.6556 | 10487.8208 | 0.09068 | 0.10649 | 0.027537 | 24.1347 | 12.3984 | 14.3106 | 19.8585 | 72.5685 | 151.8705 | 138.8462 | 104.7091 | 71.1323 | 99.08% | 98.64% | 95.77% | 99.2% | 98.75% | 98.55% | 132.3341 | 112.6821 | 435.7737 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 115.2761 | 22 | 76 | 428 | 69 | 95.9% | 0.085638 | 0.094193 | 48.1012 | 50.8437 | 127.8973 | 62.0778 | 95.9% | 3857.2331 | 98.15% | 98.95% | 84.99% |  |  | 98.38% | 0.87648
2020-08-25 | 175.3677 | 151.0666 | 151.0666 | 139.5186 | 127.104 | 13.6281 | 13.6281 | 3472.1535 | 1188.0281 | 104.3453 | 613.6445 | 69.6006 | 22.1915 | 76.6615 | 431.7253 | 9265.0836 | 361.5661 |  |  | 29.4014 | 0.87645 | 53.1362 | 4085.798 | 2179.78 | 1906.0179 | 717.9898 | 24.3011 | 11.548 | 12.2055 | 14.3722 | 12.7289 | 2.236 | 3577.7346 | 9370.8158 | 10890.8364 | 2394.9144 | 5572.4185 | 10092.7728 | 0.091461 | 0.10708 | 0.027456 | 24.1685 | 12.3558 | 14.1998 | 20.0764 | 73.3849 | 153.629 | 137.7255 | 104.1858 | 71.378 | 99.07% | 98.62% | 95.72% | 99.16% | 98.68% | 98.48% | 131.2032 | 112.0653 | 437.0699 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 113.4686 | 22 | 76 | 428 | 69 | 95.86% | 0.086218 | 0.094882 | 48.0545 | 50.7241 | 127.227 | 62.7709 | 95.86% | 3713.462 | 98.13% | 98.9% | 84.98% |  |  | 98.36% | 0.87645
2020-08-24 | 172.4755 | 148.3884 | 148.3884 | 136.7409 | 124.5384 | 13.6881 | 13.6881 | 3452.4831 | 1181.2977 | 103.7542 | 609.3187 | 58.8449 | 18.7622 | 64.8147 | 365.0091 | 8777.9365 | 353.2329 |  |  | 29.3937 | 0.87665 | 44.9249 | 4061.8018 | 2167.4312 | 1894.3706 | 713.0729 | 24.0871 | 11.6476 | 12.1945 | 14.2908 | 12.6568 | 2.2233 | 3405.3769 | 8939.4513 | 10399.4988 | 2278.2271 | 5308.9879 | 9632.6896 | 0.092494 | 0.10809 | 0.027602 | 24.171 | 12.5814 | 14.336 | 17.7462 | 64.7689 | 135.3516 | 135.4465 | 102.6556 | 70.6131 | 99.18% | 98.78% | 96.21% | 99.22% | 98.78% | 98.59% | 129.7379 | 111.0234 | 434.751 |  |  |  | 32.01 | 28.35 | 4.98 | 2496.7799 | 1360.8 | 119.52 | 3977.0999 | 110.8436 | 22 | 76 | 428 | 69 | 96.32% | 0.087101 | 0.095879 | 47.9292 | 51.0884 | 125.403 | 55.4271 | 96.32% | 3536.2454 | 98.34% | 98.98% | 85% |  |  | 98.55% | 0.87665
2020-08-23 | 173.1826 | 149.0835 | 149.0835 | 137.5238 | 125.1978 | 13.7142 | 13.7142 | 3455.3562 | 1134.812 | 97.8662 | 610.4292 | 67.8853 | 21.4851 | 74.76 | 293.2628 | 8988.927 | 354.9187 |  |  | 29.5186 | 0.87343 | 46.6793 | 4065.7854 | 2222.678 | 1843.1074 | 708.2954 | 24.099 | 11.5597 | 12.2369 | 14.655 | 12.1587 | 2.0971 | 3572.8522 | 9177.4028 | 10601.7396 | 2353.5479 | 5519.2585 | 9855.3459 | 0.094286 | 0.10374 | 0.026228 | 24.4738 | 12.9001 | 14.4459 | 20.0986 | 68.7791 | 99.8892 | 135.7586 | 102.367 | 69.8362 | 99.09% | 98.65% | 97.02% | 99.15% | 98.75% | 98.99% | 127.273 | 115.672 | 457.5201 |  |  |  | 34.9377 | 28.9865 | 4.9996 | 2725.1412 | 1391.35 | 119.99 | 4236.4812 | 111.4959 | 24.9483 | 86.8105 | 340.5335 | 78.8277 | 95.84% | 0.086422 | 0.095464 | 47.8956 | 51.8198 | 125.6548 | 62.5319 | 95.84% | 3605.7079 | 98.12% | 98.99% | 84.99% |  |  | 98.36% | 0.87343
2020-08-22 | 173.2778 | 149.4726 | 149.4726 | 138.1571 | 125.9814 | 13.6186 | 13.6186 | 3432.1945 | 1126.2647 | 97.0918 | 606.4116 | 72.4596 | 22.9302 | 79.7973 | 310.9342 | 9390.5717 | 351.4791 |  |  | 29.5411 | 0.87285 | 49.7382 | 4038.6061 | 2208.838 | 1829.7681 | 703.5034 | 23.8052 | 11.3155 | 12.0555 | 14.5638 | 12.0671 | 2.0805 | 3722.3245 | 9553.7816 | 11033.642 | 2451.4933 | 5748.2374 | 10258.2168 | 0.093736 | 0.10341 | 0.026428 | 24.4263 | 12.7634 | 14.3755 | 20.4516 | 69.9116 | 100.8768 | 135.6138 | 101.854 | 68.7142 | 99.06% | 98.61% | 96.97% | 99.17% | 98.78% | 99.02% | 128.0188 | 116.0428 | 454.0615 |  |  |  | 35 | 29 | 5 | 2730 | 1392 | 120 | 4242 | 112.4332 | 25 | 87 | 339 | 79 | 95.74% | 0.086063 | 0.095007 | 47.1762 | 51.5651 | 125.1211 | 63.6342 | 95.74% | 3754.1511 | 98.07% | 99.02% | 84.98% |  |  | 98.33% | 0.87285
2020-08-21 | 173.6377 | 149.8304 | 149.8304 | 138.4141 | 126.4033 | 13.8638 | 13.8638 | 3435.4511 | 1127.3333 | 97.1839 | 606.0503 | 74.0005 | 23.4179 | 81.4942 | 317.5463 | 9413.439 | 353.6903 |  |  | 29.3952 | 0.87661 | 50.7959 | 4041.5014 | 2210.9339 | 1830.5675 | 703.2342 | 23.8073 | 11.4162 | 12.0531 | 14.5776 | 12.0786 | 2.0825 | 3760.7616 | 9658.883 | 11156.8239 | 2476.5334 | 5809.2333 | 10371.8845 | 0.094237 | 0.10419 | 0.026739 | 24.4054 | 12.8729 | 14.383 | 20.7843 | 71.021 | 102.4299 | 135.6046 | 101.6197 | 68.2732 | 99.05% | 98.6% | 96.94% | 99.16% | 98.78% | 99.01% | 127.3391 | 115.1689 | 448.7822 |  |  |  | 35 | 29 | 5 | 2730 | 1392 | 120 | 4242 | 112.5201 | 25 | 87 | 339 | 79 | 95.69% | 0.086624 | 0.095595 | 47.2766 | 51.6613 | 124.9697 | 64.6523 | 95.69% | 3793.4972 | 98.05% | 99.01% | 85% |  |  | 98.31% | 0.87661
2020-08-20 | 175.1401 | 150.9686 | 150.9686 | 139.4167 | 127.1101 | 13.5511 | 13.5511 | 3470.4081 | 1138.8044 | 98.1728 | 611.9473 | 74.9516 | 23.7189 | 82.5416 | 321.6276 | 9443.3008 | 359.6188 |  |  | 29.424 | 0.87587 | 51.4488 | 4082.3554 | 2233.4309 | 1848.9245 | 710.1201 | 24.1715 | 11.5519 | 12.2739 | 14.7259 | 12.2015 | 2.1037 | 3811.2228 | 9790.8287 | 11309.9429 | 2509.6456 | 5887.7763 | 10513.8926 | 0.094095 | 0.10415 | 0.026801 | 24.4086 | 12.8336 | 14.4346 | 20.9672 | 71.6353 | 103.2986 | 137.0736 | 102.6153 | 68.7509 | 99.05% | 98.6% | 96.94% | 99.16% | 98.78% | 99.02% | 127.5305 | 115.2239 | 447.7515 |  |  |  | 35 | 29 | 5 | 2730 | 1392 | 120 | 4242 | 113.5613 | 25 | 87 | 339 | 79 | 95.69% | 0.086544 | 0.095489 | 47.9972 | 51.6768 | 126.2951 | 65.2148 | 95.69% | 3844.5979 | 98.05% | 99.02% | 85.01% |  |  | 98.29% | 0.87587
2020-08-19 | 172.4445 | 148.6546 | 148.6546 | 137.1981 | 124.9607 | 13.5111 | 13.5111 | 3439.2821 | 1128.5904 | 97.2923 | 606.8502 | 75.1132 | 23.77 | 82.7196 | 322.3211 | 9236.1141 | 351.3239 |  |  | 29.4142 | 0.87612 | 51.5597 | 4046.1323 | 2213.3994 | 1832.733 | 704.1425 | 23.79 | 11.4564 | 12.1729 | 14.5938 | 12.092 | 2.0848 | 3741.3056 | 9605.2395 | 11093.5083 | 2463.983 | 5778.2458 | 10313.6674 | 0.094825 | 0.10496 | 0.027016 | 24.3453 | 12.8948 | 14.4976 | 21.216 | 72.5156 | 104.6149 | 134.8374 | 100.9376 | 67.6116 | 99.04% | 98.57% | 96.87% | 99.14% | 98.75% | 98.99% | 126.5485 | 114.3325 | 444.1871 |  |  |  | 35 | 29 | 5 | 2730 | 1392 | 120 | 4242 | 111.4657 | 25 | 87 | 339 | 79 | 95.6% | 0.087218 | 0.096232 | 47.4193 | 51.7377 | 124.2096 | 66.0069 | 95.6% | 3773.6049 | 98.01% | 98.99% | 85% |  |  | 98.27% | 0.87612
2020-08-18 | 172.4144 | 148.1346 | 148.1346 | 136.3221 | 124.0061 | 13.5104 | 13.5104 | 3459.1198 | 1137.9534 | 118.9679 | 610.7023 | 70.6932 | 22.3713 | 77.852 | 303.3545 | 8739.9784 | 352.8335 |  |  | 29.3107 | 0.8788 | 50.2866 | 4069.8221 | 2202.1985 | 1867.6235 | 729.6701 | 24.2798 | 11.8125 | 12.3627 | 14.52 | 12.1924 | 2.5493 | 3572.6896 | 9023.0463 | 10721.6859 | 2369.8986 | 5479.6367 | 9823.5824 | 0.094502 | 0.10535 | 0.032444 | 24.4798 | 12.8343 | 14.2423 | 20.7185 | 72.7868 | 126.7876 | 135.0265 | 101.709 | 69.0526 | 99.06% | 98.58% | 96.91% | 99.13% | 98.67% | 98.71% | 126.9819 | 113.9098 | 369.8676 |  |  |  | 32.75 | 27.5 | 5.75 | 2554.5 | 1320 | 138 | 4012.5 | 110.4659 | 25 | 87 | 339 | 79 | 95.72% | 0.088043 | 0.095935 | 48.4551 | 51.5564 | 124.6759 | 64.8078 | 95.72% | 3649.2662 | 98.06% | 98.91% | 84.99% |  |  | 98.3% | 0.8788
2020-08-17 | 170.4011 | 146.1551 | 146.1551 | 134.2094 | 121.6485 | 13.6477 | 13.6477 | 3444.0962 | 1134.0317 | 126.0035 | 612.4462 | 65.3133 | 20.6688 | 71.9273 | 280.2685 | 8126.6125 | 348.5145 |  |  | 29.0241 | 0.88628 | 47.0441 | 4056.5425 | 2184.061 | 1872.4814 | 738.4498 | 24.2459 | 11.9457 | 12.5268 | 14.4004 | 12.1503 | 2.7001 | 3346.3255 | 8374.7939 | 10040.1461 | 2226.8683 | 5112.6738 | 9157.1856 | 0.095531 | 0.10627 | 0.034237 | 24.4977 | 12.8775 | 14.2631 | 20.3754 | 72.4373 | 134.2279 | 133.5994 | 101.3308 | 69.8967 | 99.07% | 98.59% | 96.94% | 99.09% | 98.58% | 98.53% | 125.6141 | 112.9176 | 350.5008 |  |  |  | 32 | 27 | 6 | 2496 | 1296 | 144 | 3936 | 107.974 | 25 | 87 | 339 | 79 | 95.8% | 0.089161 | 0.096825 | 48.7185 | 51.6383 | 123.7871 | 63.955 | 95.8% | 3430.6207 | 98.1% | 98.84% | 84.9% |  |  | 98.33% | 0.88628
2020-08-16 | 170.7343 | 146.7693 | 146.7693 | 135.0041 | 122.6485 | 13.7679 | 13.7679 | 3424.6318 | 1127.6227 | 125.2914 | 604.6538 | 76.022 | 24.0576 | 83.7204 | 326.2208 | 8675.5617 | 345.0286 |  |  | 29.0757 | 0.88493 | 54.7574 | 4029.2856 | 2171.7177 | 1857.5678 | 729.9452 | 23.965 | 11.7652 | 12.4032 | 14.319 | 12.0817 | 2.6848 | 3410.9391 | 8550.8419 | 10255.0806 | 2269.5839 | 5215.1084 | 9351.3956 | 0.094735 | 0.10537 | 0.033974 | 24.4745 | 12.8555 | 14.3817 | 23.1029 | 82.0653 | 151.8941 | 133.7562 | 101.4618 | 69.9325 | 98.94% | 98.39% | 96.51% | 98.98% | 98.43% | 98.38% | 126.6696 | 113.88 | 353.2127 |  |  |  | 32 | 27 | 6 | 2496 | 1296 | 144 | 3936 | 108.876 | 25 | 87 | 339 | 79 | 95.21% | 0.088418 | 0.096015 | 48.1333 | 51.7117 | 123.7045 | 72.4724 | 95.21% | 3498.5424 | 97.83% | 98.71% | 84.99% |  |  | 98.1% | 0.88493
2020-08-15 | 177.2193 | 152.9886 | 152.9886 | 141.3351 | 128.9011 | 14.1061 | 14.1061 | 3465.4402 | 1141.0596 | 126.7844 | 611.6211 | 72.4163 | 22.9165 | 79.7496 | 310.7483 | 9306.9954 | 364.0247 |  |  | 28.9616 | 0.88792 | 52.1603 | 4077.0612 | 2197.5962 | 1879.465 | 738.4055 | 24.2307 | 11.6535 | 12.3182 | 14.4896 | 12.2256 | 2.7168 | 3627.8473 | 9110.7304 | 10934.8998 | 2412.6588 | 5550.9186 | 9967.3894 | 0.092526 | 0.1027 | 0.033169 | 24.313 | 12.5126 | 14.039 | 21.0196 | 74.5702 | 137.8299 | 139.0492 | 105.6999 | 72.7288 | 99.05% | 98.56% | 96.88% | 99.13% | 98.66% | 98.62% | 129.693 | 116.8447 | 361.7872 |  |  |  | 32 | 27 | 6 | 2496 | 1296 | 144 | 3936 | 114.8524 | 25 | 87 | 339 | 79 | 95.7% | 0.086285 | 0.093705 | 48.2024 | 50.8646 | 128.5024 | 65.8789 | 95.7% | 3722.3808 | 98.05% | 98.9% | 85% |  |  | 98.28% | 0.88792
2020-08-14 | 177.4797 | 153.5368 | 153.5368 | 142.0977 | 129.7274 | 13.7068 | 13.7068 | 3446.3872 | 1135.2236 | 125.7776 | 608.7952 | 72.6158 | 22.9326 | 79.9693 | 311.6046 | 9533.3807 | 362.0335 |  |  | 28.9269 | 0.88884 | 52.2554 | 4055.1825 | 2185.386 | 1869.7964 | 734.5729 | 23.9429 | 11.4391 | 12.1613 | 14.4091 | 12.1631 | 2.6952 | 3818.9966 | 9597.3641 | 11515.81 | 2539.5774 | 5845.0978 | 10498.3843 | 0.091995 | 0.10268 | 0.033613 | 24.2163 | 12.3781 | 13.9635 | 19.8925 | 70.7219 | 130.3113 | 139.2182 | 105.2848 | 71.2718 | 99.1% | 98.63% | 97.03% | 99.22% | 98.79% | 98.76% | 130.4418 | 116.8637 | 357.0097 |  |  |  | 32.0769 | 27.0769 | 6 | 2502 | 1299.6923 | 144 | 3945.6923 | 116.0687 | 24.9487 | 87 | 339 | 79 | 95.9% | 0.086074 | 0.093385 | 47.5434 | 50.5578 | 128.1478 | 62.4677 | 95.9% | 3918.8608 | 98.15% | 99.01% | 84.99% |  |  | 98.37% | 0.88884
2020-08-13 | 177.1227 | 153.6124 | 153.6124 | 142.328 | 130.1924 | 13.6928 | 13.6928 | 3416.8158 | 1140.5227 | 114.0523 | 603.262 | 74.085 | 21.569 | 81.5873 | 317.909 | 9728.486 | 357.6468 |  |  | 28.81 | 0.89192 | 51.4947 | 4020.0778 | 2162.2409 | 1857.8369 | 717.3143 | 23.5102 | 11.2845 | 11.9585 | 14.2565 | 12.2199 | 2.444 | 3846.159 | 9831.7911 | 11630.4785 | 2560.2192 | 5929.3281 | 10680.8165 | 0.091492 | 0.10376 | 0.030809 | 24.0649 | 12.4191 | 14.0876 | 18.4261 | 71.7077 | 118.906 | 138.9815 | 105.0387 | 70.7528 | 99.16% | 98.62% | 97.02% | 99.28% | 98.79% | 98.89% | 131.1588 | 115.6476 | 389.4944 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 116.5135 | 23 | 87 | 339 | 79 | 95.86% | 0.08571 | 0.093563 | 46.7532 | 50.5716 | 127.7869 | 62.8106 | 95.86% | 3955.8805 | 98.13% | 99.06% | 84.99% |  |  | 98.36% | 0.89192
2020-08-12 | 179.6832 | 155.5055 | 155.5055 | 143.9094 | 131.45 | 13.6324 | 13.6324 | 3466.9523 | 1157.2581 | 115.7258 | 612.4214 | 72.8679 | 21.2147 | 80.2469 | 312.6863 | 9672.725 | 369.3784 |  |  | 28.5682 | 0.89834 | 50.6487 | 4079.3738 | 2193.9684 | 1885.4053 | 728.1472 | 24.1778 | 11.5961 | 12.2777 | 14.4657 | 12.3992 | 2.4798 | 3825.433 | 9777.7275 | 11566.2827 | 2546.4439 | 5897.1004 | 10621.9765 | 0.091945 | 0.10411 | 0.030727 | 24.2095 | 12.4818 | 14.1413 | 18.6219 | 72.4736 | 120.185 | 141.3357 | 106.9907 | 72.5008 | 99.17% | 98.64% | 97.06% | 99.27% | 98.77% | 98.87% | 130.5122 | 115.2636 | 390.5339 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 117.8328 | 23 | 87 | 339 | 79 | 95.91% | 0.086043 | 0.093962 | 48.0516 | 50.8326 | 130.2155 | 63.4805 | 95.91% | 3934.4416 | 98.15% | 99.05% | 84.99% |  |  | 98.34% | 0.89834
2020-08-11 | 178.3354 | 154.2668 | 154.2668 | 142.6726 | 130.2049 | 13.6 | 13.6 | 3457.2526 | 1154.0203 | 115.402 | 610.6052 | 71.1809 | 20.7236 | 78.3891 | 305.4472 | 9419.5743 | 365.3877 |  |  | 28.497 | 0.90024 | 49.4761 | 4067.8578 | 2187.8302 | 1880.0276 | 726.0072 | 24.0686 | 11.5941 | 12.2582 | 14.4253 | 12.3645 | 2.4729 | 3741.2502 | 9563.5288 | 11313.2707 | 2490.3553 | 5767.5758 | 10389.4473 | 0.092526 | 0.10459 | 0.030741 | 24.2029 | 12.5338 | 14.1815 | 18.5877 | 72.336 | 119.9479 | 140.353 | 106.4238 | 72.4188 | 99.17% | 98.64% | 97.06% | 99.25% | 98.75% | 98.85% | 129.6937 | 114.7315 | 390.3599 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 116.6046 | 23 | 87 | 339 | 79 | 95.91% | 0.086501 | 0.094491 | 47.921 | 50.9183 | 129.4567 | 63.3612 | 95.91% | 3847.9508 | 98.15% | 99.03% | 84.99% |  |  | 98.34% | 0.90024
2020-08-10 | 174.4723 | 150.6169 | 150.6169 | 138.8726 | 126.7438 | 13.554 | 13.554 | 3430.6474 | 1145.1396 | 114.514 | 605.5216 | 66.9183 | 19.4826 | 73.6949 | 287.156 | 8743.4852 | 353.5397 |  |  | 28.4221 | 0.90225 | 46.5133 | 4036.1689 | 2170.9938 | 1865.1751 | 720.0355 | 23.8554 | 11.7443 | 12.1732 | 14.3142 | 12.2694 | 2.4539 | 3501.4504 | 8952.9293 | 10591.7677 | 2330.627 | 5398.5048 | 9726.4779 | 0.093972 | 0.10587 | 0.030725 | 24.2729 | 12.8499 | 14.2598 | 18.5698 | 72.2549 | 119.7905 | 137.4349 | 104.5668 | 72.0577 | 99.16% | 98.63% | 97.05% | 99.2% | 98.66% | 98.77% | 127.6977 | 113.3513 | 390.5556 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 113.1647 | 23 | 87 | 339 | 79 | 95.89% | 0.087658 | 0.095831 | 47.773 | 51.3825 | 127.1677 | 63.2931 | 95.89% | 3601.5465 | 98.14% | 98.96% | 85% |  |  | 98.34% | 0.90225
2020-08-09 | 174.9231 | 151.0086 | 151.0086 | 139.3367 | 127.1872 | 13.545 | 13.545 | 3439.5861 | 1148.1233 | 114.8123 | 607.2245 | 69.0371 | 20.0994 | 76.0281 | 296.2476 | 8954.7828 | 355.3106 |  |  | 28.5365 | 0.89919 | 47.986 | 4046.8106 | 2176.6505 | 1870.1601 | 722.0368 | 23.9145 | 11.6719 | 12.2276 | 14.3515 | 12.3013 | 2.4603 | 3574.4804 | 9137.4304 | 10809.0969 | 2379.376 | 5510.5329 | 9926.4985 | 0.093768 | 0.10589 | 0.030912 | 24.2367 | 12.719 | 14.2636 | 18.7502 | 72.9689 | 120.9964 | 137.6244 | 104.4551 | 71.5657 | 99.16% | 98.62% | 97.02% | 99.21% | 98.68% | 98.78% | 127.9758 | 113.3206 | 388.1986 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 113.577 | 23 | 87 | 339 | 79 | 95.85% | 0.087591 | 0.095717 | 47.814 | 51.2193 | 127.1613 | 63.9154 | 95.85% | 3676.4672 | 98.12% | 98.97% | 84.99% |  |  | 98.33% | 0.89919
2020-08-08 | 177.5842 | 153.4077 | 153.4077 | 141.6876 | 129.2579 | 13.5837 | 13.5837 | 3461.4253 | 1155.4132 | 115.5413 | 611.2574 | 71.851 | 20.9186 | 79.1271 | 308.3227 | 9346.4613 | 364.2957 |  |  | 28.5265 | 0.89945 | 49.9419 | 4072.6827 | 2190.4708 | 1882.2119 | 726.7987 | 24.1765 | 11.72 | 12.3142 | 14.4427 | 12.3794 | 2.4759 | 3708.778 | 9478.9402 | 11212.392 | 2468.8695 | 5717.1127 | 10297.1903 | 0.093007 | 0.10527 | 0.030954 | 24.2685 | 12.6482 | 14.2232 | 18.9322 | 73.6857 | 122.202 | 139.6725 | 105.7741 | 71.9448 | 99.15% | 98.62% | 97.01% | 99.23% | 98.71% | 98.81% | 129.0225 | 113.9936 | 387.6774 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 115.7537 | 23 | 87 | 339 | 79 | 95.84% | 0.087002 | 0.095029 | 48.2107 | 51.14 | 128.8485 | 64.5409 | 95.84% | 3814.4301 | 98.12% | 99% | 84.99% |  |  | 98.31% | 0.89945
2020-08-07 | 179.1004 | 154.9295 | 154.9295 | 143.3098 | 130.7856 | 13.8938 | 13.8938 | 3468.7493 | 1157.8579 | 115.7858 | 612.0724 | 74.756 | 21.7644 | 82.3262 | 320.7884 | 9640.7694 | 370.2647 |  |  | 28.5261 | 0.89947 | 51.9611 | 4080.8217 | 2195.1056 | 1885.7161 | 727.8582 | 24.1709 | 11.6197 | 12.3125 | 14.4732 | 12.4056 | 2.4811 | 3817.3924 | 9759.0389 | 11544.4737 | 2541.0804 | 5885.1804 | 10601.8072 | 0.09264 | 0.10506 | 0.031104 | 24.1919 | 12.5071 | 14.1914 | 19.1786 | 74.6339 | 123.7523 | 140.5245 | 106.2116 | 71.7488 | 99.14% | 98.6% | 96.97% | 99.25% | 98.73% | 98.83% | 129.534 | 114.2221 | 385.8008 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 116.9065 | 23 | 87 | 339 | 79 | 95.79% | 0.086768 | 0.094731 | 48.103 | 50.8904 | 129.401 | 65.3742 | 95.79% | 3926.3954 | 98.1% | 99.01% | 85% |  |  | 98.29% | 0.89947
2020-08-06 | 177.9886 | 154.0872 | 154.0872 | 142.5967 | 130.2843 | 13.639 | 13.639 | 3448.3743 | 1151.0568 | 115.1057 | 608.2496 | 77.5576 | 22.5801 | 85.4115 | 332.8104 | 9856.3906 | 363.2364 |  |  | 28.4417 | 0.90172 | 53.9084 | 4056.6239 | 2182.2118 | 1874.412 | 723.3553 | 23.9014 | 11.4905 | 12.2701 | 14.3882 | 12.3328 | 2.4666 | 3898.1384 | 9965.2334 | 11788.0815 | 2594.8895 | 6009.6059 | 10825.6698 | 0.09298 | 0.10583 | 0.031621 | 24.1373 | 12.4811 | 14.2754 | 19.4189 | 75.5717 | 125.3106 | 139.5374 | 105.082 | 70.3372 | 99.13% | 98.58% | 96.93% | 99.25% | 98.74% | 98.84% | 129.0598 | 113.3902 | 379.4916 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 116.6628 | 23 | 87 | 339 | 79 | 95.72% | 0.087274 | 0.095221 | 47.662 | 50.8938 | 128.1476 | 66.195 | 95.72% | 4009.4523 | 98.07% | 99.02% | 85.01% |  |  | 98.27% | 0.90172
2020-08-05 | 177.1902 | 153.1281 | 153.1281 | 141.3925 | 129.0141 | 13.7894 | 13.7894 | 3457.5449 | 1155.1932 | 116.2487 | 611.1599 | 75.5951 | 22.3549 | 84.5599 | 329.4921 | 9607.5918 | 362.9504 |  |  | 28.6369 | 0.89651 | 53.4646 | 4068.7048 | 2186.1029 | 1882.6018 | 727.4086 | 24.0621 | 11.7356 | 12.3095 | 14.4139 | 12.3771 | 2.491 | 3777.956 | 9643.4163 | 11415.018 | 2517.0303 | 5820.6045 | 10479.4663 | 0.093035 | 0.10589 | 0.031604 | 24.1755 | 12.6578 | 14.2097 | 19.7405 | 77.0771 | 128.6841 | 138.8963 | 104.7906 | 70.664 | 99.11% | 98.55% | 96.86% | 99.22% | 98.68% | 98.77% | 128.9839 | 113.3261 | 379.7013 |  |  |  | 34.7176 | 29.8118 | 6 | 2707.9765 | 1430.9647 | 144 | 4282.9412 | 115.2417 | 23 | 87 | 339 | 77.7765 | 95.71% | 0.087319 | 0.095264 | 48.1072 | 51.043 | 127.8155 | 66.3183 | 95.71% | 3888.4918 | 98.06% | 98.97% | 84.98% |  |  | 98.26% | 0.89651
2020-08-04 | 177.4295 | 153.1861 | 153.1861 | 141.311 | 129.0128 | 13.6515 | 13.6515 | 3468.5315 | 1170.107 | 125.3686 | 611.5295 | 68.6158 | 23.9116 | 90.4482 | 352.436 | 9313.6381 | 365.4833 |  |  | 28.4946 | 0.90031 | 58.232 | 4080.0609 | 2173.0559 | 1907.0051 | 736.8981 | 24.2434 | 11.8751 | 12.2869 | 14.3278 | 12.5369 | 2.6865 | 3653.3529 | 9310.8241 | 11147.3678 | 2448.6767 | 5624.9176 | 10174.0512 | 0.092448 | 0.10656 | 0.033406 | 24.1398 | 12.5627 | 14.0283 | 21.6664 | 86.7799 | 153.5471 | 139.5325 | 105.9247 | 72.4023 | 99.02% | 98.39% | 96.54% | 99.12% | 98.46% | 98.49% | 129.8028 | 112.6155 | 359.2197 |  |  |  | 32 | 28 | 6 | 2496 | 1344 | 144 | 3984 | 115.3251 | 23 | 87 | 339 | 66 | 96.01% | 0.087516 | 0.095074 | 48.4053 | 50.7307 | 128.633 | 62.0644 | 96.01% | 3799.41 | 98.19% | 98.8% | 85.01% |  |  | 98.38% | 0.90031
2020-08-03 | 175.336 | 151.157 | 151.157 | 139.2089 | 126.7355 | 13.6341 | 13.6341 | 3458.9496 | 1166.8746 | 125.0223 | 611.0843 | 62.3827 | 21.7394 | 82.2317 | 320.4201 | 8780.7105 | 359.8483 |  |  | 28.4233 | 0.90222 | 52.9421 | 4070.0339 | 2167.0528 | 1902.9812 | 736.1066 | 24.179 | 11.948 | 12.3479 | 14.2883 | 12.5022 | 2.679 | 3464.818 | 8826.8863 | 10567.2316 | 2322.3591 | 5333.7577 | 9644.9178 | 0.09334 | 0.10713 | 0.03324 | 24.1607 | 12.6745 | 14.1173 | 20.7562 | 83.1495 | 147.1617 | 138.1092 | 105.2912 | 72.7156 | 99.06% | 98.46% | 96.68% | 99.11% | 98.44% | 98.47% | 128.5622 | 112.0146 | 361.0079 |  |  |  | 32 | 28 | 6 | 2496 | 1344 | 144 | 3984 | 113.1052 | 23 | 87 | 339 | 66 | 96.18% | 0.088137 | 0.095819 | 48.475 | 50.9525 | 127.7412 | 59.4651 | 96.18% | 3602.9234 | 98.27% | 98.79% | 84.99% |  |  | 98.44% | 0.90222
2020-08-02 | 174.4645 | 150.675 | 150.675 | 138.917 | 126.5508 | 13.5922 | 13.5922 | 3434.4787 | 1158.6193 | 124.1378 | 606.1123 | 60.8549 | 21.207 | 80.2178 | 312.5728 | 8968.7791 | 355.5086 |  |  | 28.5382 | 0.89914 | 51.6456 | 4040.591 | 2151.7216 | 1888.8694 | 730.2501 | 23.7895 | 11.758 | 12.1748 | 14.1872 | 12.4138 | 2.6601 | 3529.8658 | 9003.0987 | 10783.0041 | 2365.3178 | 5436.576 | 9839.5929 | 0.092937 | 0.10689 | 0.033449 | 24.0339 | 12.6158 | 14.089 | 19.6722 | 78.7468 | 139.2457 | 137.257 | 104.4221 | 71.5066 | 99.1% | 98.52% | 96.82% | 99.17% | 98.55% | 98.58% | 129.1193 | 112.264 | 358.7578 |  |  |  | 32 | 28 | 6 | 2496 | 1344 | 144 | 3984 | 113.0189 | 23 | 87 | 339 | 66 | 96.34% | 0.087884 | 0.095494 | 47.7223 | 50.7387 | 126.6934 | 56.329 | 96.34% | 3671.5594 | 98.34% | 98.88% | 85% |  |  | 98.53% | 0.89914
2020-08-01 | 178.0055 | 153.8131 | 153.8131 | 141.9966 | 129.4354 | 13.6972 | 13.6972 | 3472.9785 | 1171.6072 | 125.5293 | 612.8114 | 63.252 | 22.0423 | 83.3776 | 324.8851 | 9461.3016 | 367.8882 |  |  | 28.4932 | 0.90035 | 53.6799 | 4085.7899 | 2175.842 | 1909.948 | 738.3407 | 24.1924 | 11.8165 | 12.4151 | 14.3462 | 12.5529 | 2.6899 | 3702.5965 | 9445.6129 | 11313.9185 | 2480.9395 | 5703.1094 | 10323.627 | 0.092315 | 0.10651 | 0.033625 | 24.0368 | 12.4697 | 14.1318 | 19.7391 | 79.0037 | 139.6777 | 139.9176 | 106.109 | 72.0251 | 99.11% | 98.54% | 96.85% | 99.2% | 98.61% | 98.65% | 129.989 | 112.6623 | 356.8755 |  |  |  | 32 | 28 | 6 | 2496 | 1344 | 144 | 3984 | 115.7561 | 23 | 87 | 339 | 66 | 96.37% | 0.087468 | 0.094984 | 48.4239 | 50.6382 | 128.8662 | 56.515 | 96.37% | 3851.4072 | 98.36% | 98.93% | 85% |  |  | 98.52% | 0.90035
2020-07-31 | 178.076 | 153.9228 | 153.9228 | 142.0695 | 129.4522 | 13.6336 | 13.6336 | 3471.6736 | 1171.167 | 125.4822 | 612.3568 | 67.7223 | 23.6002 | 89.2703 | 347.8465 | 9551.7444 | 367.9637 |  |  | 28.4574 | 0.9013 | 57.4737 | 4084.0304 | 2175.0244 | 1909.006 | 737.839 | 24.1532 | 11.8532 | 12.4533 | 14.3408 | 12.5482 | 2.6889 | 3729.7982 | 9508.3844 | 11385.5323 | 2499.6743 | 5743.3162 | 10390.6518 | 0.092334 | 0.1066 | 0.033701 | 24.0141 | 12.5186 | 14.1904 | 20.9902 | 84.053 | 148.6871 | 139.9854 | 106.0924 | 71.9133 | 99.06% | 98.45% | 96.65% | 99.16% | 98.54% | 98.57% | 129.9626 | 112.5672 | 356.0767 |  |  |  | 32 | 28 | 6 | 2496 | 1344 | 144 | 3984 | 115.8878 | 23 | 87 | 339 | 66 | 96.14% | 0.087519 | 0.095029 | 48.4597 | 50.7231 | 128.8088 | 60.1181 | 96.14% | 3879.131 | 98.25% | 98.87% | 85.01% |  |  | 98.43% | 0.9013
2020-07-30 | 177.6537 | 153.6571 | 153.6571 | 141.9326 | 129.505 | 13.6041 | 13.6041 | 3458.4689 | 1203.4988 | 138.0334 | 610.1467 | 68.7762 | 20.4687 | 65.4613 | 391.77 | 9630.3258 | 364.6075 |  |  | 28.3432 | 0.90437 | 50.9448 | 4068.6156 | 2116.9366 | 1951.679 | 748.1801 | 23.9966 | 11.7245 | 12.3723 | 13.9578 | 12.8946 | 2.9579 | 3661.4572 | 9445.8622 | 11494.1685 | 2488.1947 | 5666.5 | 10403.1001 | 0.09035 | 0.10982 | 0.037123 | 23.6965 | 12.0198 | 13.9716 | 17.8611 | 64.4138 | 184.6176 | 139.7127 | 106.1856 | 72.0581 | 99.18% | 98.84% | 96.23% | 99.28% | 98.86% | 98.23% | 132.8171 | 109.2678 | 323.2517 |  |  |  | 32 | 29.5625 | 6.7812 | 2496 | 1419 | 162.75 | 4077.75 | 115.8422 | 19.875 | 63.5625 | 380.4062 | 66.7812 | 96.11% | 0.088065 | 0.095001 | 48.0934 | 49.6879 | 128.3614 | 60.5449 | 96.11% | 3910.098 | 98.24% | 98.98% | 85% |  |  | 98.42% | 0.90437
2020-07-29 | 177.8371 | 153.8724 | 153.8724 | 142.0192 | 129.6278 | 13.7177 | 13.7177 | 3458.3387 | 1213.4522 | 141.5694 | 610.3842 | 71.3219 | 20.2256 | 60.6768 | 417.2862 | 9720.8423 | 365.2781 |  |  | 28.3388 | 0.90449 | 50.673 | 4068.7229 | 2103.3171 | 1965.4058 | 751.9536 | 23.9648 | 11.8532 | 12.4664 | 13.868 | 13.0013 | 3.0336 | 3663.853 | 9478.4163 | 11580.0089 | 2499.3587 | 5676.88 | 10459.1611 | 0.089762 | 0.11078 | 0.038164 | 23.5838 | 12.0345 | 14.0158 | 17.4593 | 60.0974 | 200.624 | 139.7414 | 106.147 | 71.8964 | 99.19% | 98.93% | 96.01% | 99.3% | 98.94% | 98.08% | 133.6873 | 108.3183 | 314.4302 |  |  |  | 32 | 30 | 7 | 2496 | 1440 | 168 | 4104 | 115.9311 | 19 | 57 | 392 | 67 | 95.99% | 0.088233 | 0.095026 | 48.2844 | 49.6341 | 128.2087 | 62.3132 | 95.99% | 3940.1183 | 98.19% | 98.99% | 85% |  |  | 98.37% | 0.90449
2020-07-28 | 178.3198 | 154.1595 | 154.1595 | 142.0689 | 129.518 | 13.6261 | 13.6261 | 3469.8962 | 1217.5074 | 142.0425 | 612.6839 | 72.4143 | 20.5354 | 61.6062 | 423.6775 | 9485.5199 | 367.8949 |  |  | 28.1873 | 0.90857 | 51.4491 | 4082.5801 | 2110.3462 | 1972.2339 | 754.7264 | 24.1602 | 12.0907 | 12.4536 | 13.9144 | 13.0447 | 3.0438 | 3562.6818 | 9210.537 | 11247.6525 | 2430.7872 | 5518.5681 | 10161.3451 | 0.08994 | 0.11056 | 0.037636 | 23.6544 | 12.2108 | 13.9235 | 18.3703 | 63.2626 | 211.3181 | 140.5622 | 107.2032 | 73.4789 | 99.16% | 98.88% | 95.83% | 99.24% | 98.85% | 97.92% | 133.4218 | 108.5413 | 318.8402 |  |  |  | 32 | 30 | 7 | 2496 | 1440 | 168 | 4104 | 115.944 | 19 | 57 | 392 | 67 | 95.82% | 0.088169 | 0.095033 | 48.7044 | 49.7887 | 129.3316 | 65.5877 | 95.82% | 3830.6747 | 98.11% | 98.91% | 84.99% |  |  | 98.28% | 0.90857
2020-07-27 | 176.1883 | 151.9254 | 151.9254 | 139.7911 | 127.2572 | 13.3492 | 13.3492 | 3469.7018 | 1217.4392 | 142.0346 | 612.8721 | 70.1793 | 19.9016 | 59.7047 | 410.601 | 9037.9877 | 362.0503 |  |  | 28.1548 | 0.90945 | 49.8611 | 4082.5739 | 2110.228 | 1972.3459 | 754.9067 | 24.2629 | 12.1343 | 12.4921 | 13.9136 | 13.044 | 3.0436 | 3407.605 | 8806.7692 | 10752.6012 | 2325.1602 | 5277.6345 | 9715.031 | 0.090915 | 0.11147 | 0.037582 | 23.7543 | 12.2529 | 13.961 | 18.6291 | 64.1674 | 214.3997 | 139.1814 | 106.4194 | 73.6528 | 99.14% | 98.87% | 95.77% | 99.2% | 98.78% | 97.79% | 131.9908 | 107.6495 | 319.3035 |  |  |  | 32 | 30 | 7 | 2496 | 1440 | 168 | 4104 | 113.9043 | 19 | 57 | 392 | 67 | 95.76% | 0.08896 | 0.095945 | 48.8893 | 49.9682 | 128.4394 | 66.5222 | 95.76% | 3663.6254 | 98.08% | 98.84% | 84.99% |  |  | 98.26% | 0.90945
2020-07-26 | 174.3908 | 150.6274 | 150.6274 | 138.6934 | 126.3008 | 13.4393 | 13.4393 | 3432.6689 | 1188.6774 | 141.513 | 606.5289 | 71.5485 | 20.4717 | 67.9521 | 373.1014 | 9142.4606 | 358.0292 |  |  | 28.2426 | 0.90708 | 51.4507 | 4039.1977 | 2102.4785 | 1936.7193 | 748.0419 | 23.7634 | 11.934 | 12.2998 | 13.8625 | 12.7358 | 3.0324 | 3472.5815 | 8882.7146 | 10868.1446 | 2359.7043 | 5354.913 | 9808.7669 | 0.091534 | 0.11025 | 0.038267 | 23.7281 | 12.3379 | 13.9476 | 18.7638 | 70.0934 | 191.7466 | 137.3736 | 104.7863 | 71.8795 | 99.13% | 98.73% | 96.2% | 99.2% | 98.69% | 98.05% | 131.0989 | 108.8465 | 313.583 |  |  |  | 32 | 29.3992 | 7 | 2496 | 1411.1625 | 168 | 4075.1625 | 112.9088 | 20.8125 | 69.0833 | 379.3125 | 72.7396 | 95.73% | 0.088999 | 0.095818 | 47.9972 | 50.0136 | 126.5207 | 66.1919 | 95.73% | 3703.9866 | 98.07% | 98.85% | 84.98% |  |  | 98.27% | 0.90708
2020-07-25 | 176.9844 | 153.1414 | 153.1414 | 141.2596 | 128.7175 | 13.618 | 13.618 | 3453.3471 | 1158.0086 | 144.7511 | 609.9241 | 76.5577 | 22.2551 | 86.3499 | 311.5718 | 9729.0796 | 372.8001 |  |  | 28.317 | 0.90507 | 55.875 | 4063.2712 | 2150.5874 | 1912.6837 | 754.6751 | 23.843 | 11.8818 | 12.5028 | 14.1797 | 12.4072 | 3.1018 | 3738.956 | 9343.6846 | 11487.2432 | 2514.9918 | 5708.9898 | 10341.7815 | 0.092341 | 0.10647 | 0.039419 | 23.8074 | 12.4044 | 14.0219 | 19.5336 | 81.2113 | 155.0042 | 138.9813 | 105.4693 | 71.2195 | 99.12% | 98.49% | 96.99% | 99.22% | 98.58% | 98.5% | 129.9531 | 112.7063 | 304.4256 |  |  |  | 32 | 28 | 7 | 2496 | 1344 | 168 | 4008 | 115.1294 | 25 | 97 | 350 | 86 | 95.68% | 0.088395 | 0.094861 | 48.2277 | 50.2336 | 127.5885 | 67.2788 | 95.68% | 3914.1021 | 98.04% | 98.9% | 84.99% |  |  | 98.24% | 0.90507
2020-07-24 | 176.6358 | 153.0869 | 153.0869 | 141.261 | 128.9752 | 13.6562 | 13.6562 | 3436.7569 | 1152.4454 | 144.0557 | 606.2501 | 76.3501 | 22.1948 | 86.1158 | 310.7272 | 9797.857 | 376.2664 |  |  | 28.2993 | 0.90555 | 55.7236 | 4043.0069 | 2140.2558 | 1902.7511 | 750.3057 | 23.5489 | 11.8259 | 12.2916 | 14.1116 | 12.3476 | 3.0869 | 3764.6967 | 9414.8783 | 11578.1847 | 2531.9254 | 5750.0747 | 10422.0643 | 0.092161 | 0.10629 | 0.039424 | 23.693 | 12.446 | 13.9077 | 19.2675 | 80.0681 | 152.7363 | 138.6565 | 105.198 | 70.9053 | 99.12% | 98.5% | 97.02% | 99.24% | 98.61% | 98.53% | 130.207 | 112.8999 | 304.3859 |  |  |  | 32 | 28 | 7 | 2496 | 1344 | 168 | 4008 | 115.2439 | 25 | 97 | 350 | 86 | 95.72% | 0.088244 | 0.094688 | 47.6663 | 50.0467 | 127.1764 | 66.3398 | 95.72% | 3941.7897 | 98.06% | 98.92% | 85% |  |  | 98.26% | 0.90555
2020-07-23 | 177.5925 | 153.9135 | 153.9135 | 142.0333 | 129.5509 | 13.5158 | 13.5158 | 3449.9018 | 1156.8533 | 144.6067 | 609.1706 | 77.6836 | 22.5824 | 87.6198 | 316.1541 | 9887.1877 | 379.6033 |  |  | 28.2198 | 0.90769 | 56.6968 | 4059.0724 | 2148.4418 | 1910.6306 | 753.7773 | 23.679 | 11.8802 | 12.4984 | 14.1656 | 12.3949 | 3.0987 | 3792.1537 | 9477.6557 | 11652.4392 | 2550.7227 | 5790.4842 | 10490.2765 | 0.092108 | 0.1062 | 0.03939 | 23.6808 | 12.4233 | 14.0424 | 19.5803 | 81.3998 | 155.3511 | 139.5964 | 105.9432 | 71.4057 | 99.11% | 98.49% | 96.99% | 99.23% | 98.59% | 98.52% | 130.2815 | 112.9987 | 304.6443 |  |  |  | 32 | 28 | 7 | 2496 | 1344 | 168 | 4008 | 116.0258 | 25 | 97 | 350 | 86 | 95.68% | 0.088181 | 0.094623 | 48.0576 | 50.1464 | 128.0029 | 67.4361 | 95.68% | 3969.9055 | 98.04% | 98.91% | 84.99% |  |  | 98.24% | 0.90769
2020-07-22 | 176.6075 | 153.0047 | 153.0047 | 141.1177 | 128.6802 | 13.6933 | 13.6933 | 3449.544 | 1156.7333 | 144.5917 | 608.7078 | 76.3861 | 22.2053 | 86.1564 | 310.8736 | 9773.1052 | 376.5745 |  |  | 28.2638 | 0.90651 | 55.7498 | 4058.2519 | 2148.219 | 1910.0328 | 753.2995 | 23.6028 | 11.887 | 12.4084 | 14.1641 | 12.3936 | 3.0984 | 3752.1994 | 9381.6127 | 11536.2643 | 2523.6344 | 5730.4649 | 10384.8006 | 0.092636 | 0.10685 | 0.039651 | 23.613 | 12.4379 | 13.9557 | 19.4324 | 80.7643 | 154.0899 | 138.6057 | 105.1464 | 70.8361 | 99.12% | 98.5% | 97.01% | 99.23% | 98.59% | 98.52% | 129.5399 | 112.3075 | 302.6418 |  |  |  | 32 | 28 | 7 | 2496 | 1344 | 168 | 4008 | 114.9198 | 25 | 97 | 350 | 86 | 95.7% | 0.088706 | 0.095181 | 47.8983 | 50.0066 | 127.1327 | 66.9142 | 95.7% | 3928.4887 | 98.06% | 98.91% | 85% |  |  | 98.25% | 0.90651
2020-07-21 | 176.2153 | 152.2171 | 152.2171 | 140.0611 | 127.3333 | 13.5687 | 13.5687 | 3470.96 | 1163.9147 | 145.4893 | 613.4634 | 73.0175 | 21.226 | 82.3569 | 297.1642 | 9374.4061 | 376.6814 |  |  | 28.2978 | 0.90559 | 53.2913 | 4084.4234 | 2161.5559 | 1922.8675 | 758.9527 | 23.9981 | 12.1561 | 12.633 | 14.252 | 12.4705 | 3.1176 | 3621.1942 | 9048.2844 | 11123.7053 | 2435.8008 | 5528.8913 | 10014.666 | 0.093137 | 0.10721 | 0.039464 | 23.775 | 12.5881 | 14.047 | 19.3452 | 80.4327 | 153.5314 | 138.5746 | 105.3377 | 71.5409 | 99.13% | 98.51% | 97.03% | 99.21% | 98.55% | 98.47% | 128.842 | 111.9308 | 304.0747 |  |  |  | 32 | 28 | 7 | 2496 | 1344 | 168 | 4008 | 113.806 | 25 | 97 | 350 | 86 | 95.74% | 0.089053 | 0.095606 | 48.7872 | 50.4102 | 127.4802 | 66.6327 | 95.74% | 3790.6818 | 98.07% | 98.88% | 84.98% |  |  | 98.26% | 0.90559
2020-07-20 | 173.5345 | 149.5173 | 149.5173 | 137.0606 | 124.3264 | 13.4707 | 13.4707 | 3471.3673 | 1186.7815 | 141.1035 | 612.8768 | 67.9469 | 19.752 | 76.6377 | 276.5279 | 8641.8392 | 370.5589 |  |  | 28.2434 | 0.90706 | 49.6373 | 4084.2441 | 2143.4823 | 1940.7618 | 753.9803 | 24.0171 | 12.4568 | 12.5846 | 14.1329 | 12.7155 | 3.0236 | 3342.0472 | 8481.8728 | 10371.0014 | 2259.7285 | 5136.506 | 9363.2106 | 0.09367 | 0.11035 | 0.038204 | 23.689 | 12.8069 | 14.0786 | 19.2733 | 82.2807 | 148.4435 | 136.8553 | 104.5189 | 71.7894 | 99.13% | 98.51% | 97.05% | 99.15% | 98.4% | 98.41% | 128.1088 | 108.7446 | 314.1058 |  |  |  | 32.7188 | 29.4375 | 7 | 2552.0625 | 1413 | 168 | 4133.0625 | 110.8989 | 25 | 97 | 350 | 86 | 95.75% | 0.090133 | 0.097118 | 49.0585 | 50.5744 | 126.3965 | 66.6629 | 95.75% | 3531.9744 | 98.08% | 98.79% | 84.99% |  |  | 98.26% | 0.90706
2020-07-19 | 173.9589 | 150.0033 | 150.0033 | 137.6627 | 125.006 | 13.475 | 13.475 | 3468.9191 | 1194.4628 | 139.354 | 611.7472 | 70.5432 | 20.5067 | 79.5661 | 287.0943 | 8951.5423 | 370.6143 |  |  | 28.3393 | 0.90447 | 51.5522 | 4080.6663 | 2135.1023 | 1945.564 | 751.1012 | 23.9557 | 12.3406 | 12.6677 | 14.0776 | 12.7978 | 2.9862 | 3431.0527 | 8760.8618 | 10691.158 | 2324.3099 | 5286.8878 | 9662.0335 | 0.092949 | 0.11096 | 0.038049 | 23.6212 | 12.6738 | 14.2342 | 19.3226 | 83.2941 | 147.0773 | 136.9871 | 104.3213 | 70.9846 | 99.12% | 98.5% | 97.03% | 99.17% | 98.42% | 98.48% | 129.1031 | 108.1491 | 315.3823 |  |  |  | 33 | 30 | 7 | 2574 | 1440 | 168 | 4182 | 111.5193 | 25 | 97 | 350 | 86 | 95.72% | 0.089928 | 0.096945 | 48.964 | 50.5292 | 126.1885 | 66.9324 | 95.72% | 3639.195 | 98.06% | 98.82% | 85.01% |  |  | 98.25% | 0.90447
2020-07-18 | 173.9806 | 150.4392 | 150.4392 | 138.3985 | 125.8177 | 13.5585 | 13.5585 | 3441.7348 | 1185.1024 | 138.2619 | 607.9898 | 75.7562 | 22.0221 | 85.4459 | 308.3101 | 9497.3994 | 367.4926 |  |  | 28.4908 | 0.90041 | 55.3618 | 4049.7246 | 2118.3705 | 1931.3541 | 746.2518 | 23.5414 | 12.0407 | 12.5138 | 13.9673 | 12.6975 | 2.9628 | 3618.052 | 9228.0886 | 11256.5205 | 2451.5353 | 5572.4143 | 10175.2194 | 0.092131 | 0.11054 | 0.038542 | 23.476 | 12.4981 | 14.1954 | 19.4317 | 83.8227 | 148.1361 | 136.5038 | 103.4255 | 69.215 | 99.1% | 98.47% | 96.97% | 99.21% | 98.5% | 98.54% | 130.249 | 108.555 | 311.3479 |  |  |  | 33 | 30 | 7 | 2574 | 1440 | 168 | 4182 | 112.2749 | 25 | 97 | 350 | 86 | 95.64% | 0.089449 | 0.096318 | 48.0958 | 50.1695 | 125.1442 | 67.3449 | 95.64% | 3836.4336 | 98.03% | 98.87% | 84.99% |  |  | 98.24% | 0.90041
2020-07-17 | 175.4582 | 151.7987 | 151.7987 | 139.7255 | 127.0892 | 13.5888 | 13.5888 | 3455.577 | 1189.8687 | 138.818 | 609.9265 | 77.9875 | 22.6708 | 87.9627 | 317.3911 | 9792.5301 | 372.7483 |  |  | 28.4628 | 0.90116 | 56.9925 | 4065.5035 | 2126.8903 | 1938.6132 | 748.7445 | 23.6595 | 12.0732 | 12.6739 | 14.0235 | 12.7486 | 2.9747 | 3727.2595 | 9510.6548 | 11603.0228 | 2525.3341 | 5741.6405 | 10487.5845 | 0.09189 | 0.11057 | 0.038868 | 23.4581 | 12.4637 | 14.3069 | 19.5138 | 84.1552 | 148.6761 | 137.5263 | 103.9049 | 68.9675 | 99.1% | 98.47% | 96.97% | 99.23% | 98.53% | 98.58% | 130.5902 | 108.5309 | 308.7348 |  |  |  | 33 | 30 | 7 | 2574 | 1440 | 168 | 4182 | 113.494 | 25 | 97 | 350 | 86 | 95.64% | 0.089384 | 0.096192 | 48.4066 | 50.2287 | 125.8093 | 67.6166 | 95.64% | 3952.6749 | 98.03% | 98.9% | 85% |  |  | 98.23% | 0.90116
2020-07-16 | 175.6956 | 151.8545 | 151.8545 | 139.698 | 126.8464 | 13.7365 | 13.7365 | 3469.6418 | 1181.9929 | 174.8365 | 613.1428 | 78.0697 | 19.0628 | 68.157 | 296.7938 | 9760.224 | 377.0198 |  |  | 28.4822 | 0.90064 | 49.7826 | 4082.7846 | 2112.8124 | 1969.9722 | 787.9793 | 23.8411 | 12.1565 | 12.73 | 13.9306 | 12.6642 | 3.7465 | 3693.4964 | 9131.616 | 11650.8479 | 2517.4667 | 5613.921 | 10289.1379 | 0.091216 | 0.10935 | 0.048499 | 23.3538 | 12.071 | 13.722 | 16.3412 | 66.2107 | 178.3748 | 137.5465 | 104.3109 | 69.5739 | 99.24% | 98.79% | 97.12% | 99.35% | 98.82% | 98.27% | 131.5556 | 109.7443 | 247.4297 |  |  |  | 33 | 30 | 8.875 | 2574 | 1440 | 213 | 4227 | 113.0968 | 20.3125 | 72.625 | 316.25 | 83.1875 | 95.64% | 0.090183 | 0.09524 | 48.7276 | 49.1468 | 125.7897 | 67.731 | 95.64% | 3963.9442 | 98.03% | 99.01% | 84.98% |  |  | 98.23% | 0.90064
2020-07-15 | 174.5547 | 150.7492 | 150.7492 | 138.5237 | 125.6727 | 13.6576 | 13.6576 | 3468.7579 | 1180.8538 | 177.1281 | 612.4333 | 77.5679 | 18.6911 | 66.3533 | 208.4053 | 9635.4809 | 374.0174 |  |  | 28.5069 | 0.89998 | 44.604 | 4081.1912 | 2110.7761 | 1970.4151 | 789.5614 | 23.8055 | 12.2255 | 12.6924 | 13.9172 | 12.652 | 3.7956 | 3651.5205 | 9013.432 | 11560.0234 | 2489.6411 | 5546.3487 | 10181.3309 | 0.091666 | 0.10993 | 0.049813 | 23.3256 | 12.1261 | 13.6688 | 16.1741 | 65.133 | 128.144 | 136.6396 | 103.5789 | 68.576 | 99.25% | 98.8% | 97.95% | 99.35% | 98.83% | 98.74% | 130.9103 | 109.1595 | 240.9023 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 112.0546 | 20 | 71 | 223 | 83 | 95.62% | 0.090814 | 0.095747 | 48.7234 | 49.1205 | 124.9816 | 67.931 | 95.62% | 3922.9895 | 98.02% | 99.09% | 84.99% |  |  | 98.22% | 0.89998
2020-07-14 | 173.0973 | 149.4203 | 149.4203 | 136.9694 | 124.0569 | 13.7873 | 13.7873 | 3465.9898 | 1179.9114 | 176.9867 | 610.6828 | 76.6505 | 18.47 | 65.5685 | 145.913 | 9379.803 | 369.9331 |  |  | 28.5993 | 0.89751 | 41.0113 | 4076.6727 | 2109.0917 | 1967.581 | 787.6696 | 23.6769 | 12.451 | 12.7144 | 13.9061 | 12.6419 | 3.7926 | 3569.4453 | 8818.1746 | 11331.5498 | 2433.3155 | 5423.605 | 9970.0329 | 0.09218 | 0.11057 | 0.050349 | 23.242 | 12.3815 | 13.7459 | 16.2949 | 65.5866 | 91.2964 | 135.3973 | 102.6174 | 67.6052 | 99.24% | 98.79% | 98.54% | 99.33% | 98.79% | 99.08% | 130.1803 | 108.5298 | 238.3347 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 110.3567 | 20 | 71 | 158 | 83 | 95.58% | 0.091371 | 0.096304 | 48.8423 | 49.3695 | 123.8902 | 68.4047 | 95.58% | 3836.1401 | 98% | 99.12% | 85.02% |  |  | 98.21% | 0.89751
2020-07-13 | 171.3387 | 147.4481 | 147.4481 | 134.8168 | 121.6945 | 13.4323 | 13.4323 | 3467.8147 | 1180.5327 | 177.0799 | 612.7266 | 72.3639 | 17.4371 | 61.9016 | 137.7529 | 8869.0857 | 365.6928 |  |  | 28.5038 | 0.90006 | 38.7177 | 4080.5413 | 2110.2021 | 1970.3392 | 789.8065 | 23.8906 | 12.6313 | 12.9515 | 13.9134 | 12.6486 | 3.7946 | 3393.5711 | 8373.4547 | 10753.5981 | 2313.9504 | 5153.6931 | 9464.4914 | 0.093122 | 0.11135 | 0.050086 | 23.4132 | 12.5275 | 13.9398 | 16.2317 | 65.3811 | 91.1004 | 134.4785 | 102.2412 | 68.1896 | 99.25% | 98.8% | 98.54% | 99.3% | 98.73% | 99.04% | 128.8629 | 107.7689 | 239.5877 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 108.4014 | 20 | 71 | 158 | 83 | 95.61% | 0.092069 | 0.09713 | 49.4734 | 49.8804 | 123.4819 | 68.1795 | 95.61% | 3645.8053 | 98.02% | 99.08% | 84.98% |  |  | 98.22% | 0.90006
2020-07-12 | 171.3813 | 147.6558 | 147.6558 | 135.1798 | 122.0908 | 13.5561 | 13.5561 | 3465.1101 | 1179.6119 | 176.9418 | 611.2763 | 73.4578 | 17.7007 | 62.8374 | 139.8353 | 9100.8094 | 365.9522 |  |  | 28.6178 | 0.89702 | 39.303 | 4076.3863 | 2108.5563 | 1967.83 | 788.2181 | 23.7255 | 12.476 | 12.8316 | 13.9026 | 12.6387 | 3.7916 | 3468.2674 | 8564.6818 | 11003.3621 | 2364.4996 | 5268.9439 | 9682.3977 | 0.092908 | 0.11133 | 0.050487 | 23.2898 | 12.4011 | 13.8557 | 16.0578 | 64.6478 | 90.0204 | 134.2284 | 101.8312 | 67.3664 | 99.25% | 98.81% | 98.56% | 99.32% | 98.77% | 99.07% | 129.1603 | 107.7849 | 237.6835 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 108.5903 | 20 | 71 | 158 | 83 | 95.64% | 0.092017 | 0.097014 | 49.0331 | 49.5466 | 123.0211 | 67.4223 | 95.64% | 3726.9265 | 98.03% | 99.11% | 85% |  |  | 98.24% | 0.89702
2020-07-11 | 172.9285 | 149.1291 | 149.1291 | 136.481 | 123.5161 | 13.7661 | 13.7661 | 3470.3381 | 1181.3917 | 177.2088 | 613.3718 | 76.6538 | 18.4708 | 65.5713 | 145.9193 | 9430.3861 | 371.4003 |  |  | 28.5542 | 0.89872 | 41.013 | 4083.7098 | 2111.7376 | 1971.9722 | 790.5805 | 23.7994 | 12.6482 | 12.9778 | 13.9235 | 12.6578 | 3.7973 | 3576.8161 | 8823.7899 | 11330.9066 | 2439.0064 | 5431.5058 | 9973.0679 | 0.092581 | 0.1113 | 0.050863 | 23.296 | 12.5278 | 13.9469 | 16.2998 | 65.6641 | 91.5095 | 135.16 | 102.2093 | 67.0967 | 99.24% | 98.79% | 98.54% | 99.33% | 98.79% | 99.08% | 129.6157 | 107.8182 | 235.9293 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 109.7313 | 20 | 71 | 158 | 83 | 95.59% | 0.091896 | 0.096823 | 49.4254 | 49.7708 | 123.5593 | 68.4727 | 95.59% | 3842.4476 | 98.01% | 99.12% | 84.98% |  |  | 98.21% | 0.89872
2020-07-10 | 174.0577 | 150.2743 | 150.2743 | 137.7388 | 124.7368 | 13.8208 | 13.8208 | 3470.9205 | 1181.5899 | 177.2385 | 612.4419 | 79.0223 | 19.0415 | 67.5974 | 150.4281 | 9749.5205 | 373.3479 |  |  | 28.3599 | 0.88055 | 42.2803 | 4083.3624 | 2112.092 | 1971.2704 | 789.6804 | 23.7834 | 12.5355 | 13.0257 | 13.9259 | 12.6599 | 3.798 | 3680.5095 | 9086.4693 | 11672.5276 | 2509.3521 | 5590.7684 | 10271.7766 | 0.090236 | 0.10868 | 0.050057 | 23.2865 | 12.427 | 14.0257 | 15.3878 | 69.4212 | 97.3981 | 135.8937 | 102.57 | 66.8103 | 99.24% | 98.79% | 98.54% | 99.39% | 98.76% | 99.05% | 132.9847 | 110.4117 | 239.7273 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 110.9004 | 20 | 71 | 158 | 83 | 95.58% | 0.089711 | 0.094464 | 49.3445 | 49.7392 | 123.9743 | 67.2097 | 95.58% | 3954.724 | 98% | 99.13% | 85% |  |  | 98.24% | 0.88055
2020-07-09 | 172.6247 | 149.2956 | 149.2956 | 136.9209 | 123.8594 | 13.628 | 13.628 | 3439.5979 | 1170.9269 | 175.639 | 607.9895 | 81.2393 | 19.5757 | 69.4938 | 154.6482 | 9914.3667 | 364.2721 |  |  | 28.2902 | 0.88286 | 43.4664 | 4047.5874 | 2093.0319 | 1954.5555 | 783.6285 | 23.3291 | 12.3747 | 12.8944 | 13.8002 | 12.5456 | 3.7637 | 3739.6758 | 9223.7985 | 11843.7399 | 2550.1857 | 5678.353 | 10424.8264 | 0.090464 | 0.10919 | 0.050799 | 23.142 | 12.4209 | 14.0419 | 15.466 | 69.8158 | 98.0256 | 134.6791 | 101.4359 | 65.4112 | 99.23% | 98.78% | 98.52% | 99.39% | 98.77% | 99.06% | 132.6496 | 109.8981 | 236.227 |  |  |  | 33 | 30 | 9 | 2574 | 1440 | 216 | 4230 | 110.3199 | 20 | 71 | 158 | 83 | 95.53% | 0.09011 | 0.094814 | 48.5982 | 49.6048 | 122.5404 | 67.5829 | 95.53% | 4017.203 | 97.98% | 99.14% | 84.98% |  |  | 98.23% | 0.88286
2020-07-08 | 172.4195 | 148.9226 | 148.9226 | 136.3848 | 123.264 | 13.7609 | 13.7609 | 3450.8565 | 1170.6905 | 183.0743 | 610.2328 | 80.4557 | 19.7336 | 70.0544 | 155.8958 | 9776.5498 | 366.2548 |  |  | 28.2549 | 0.88402 | 44.0284 | 4061.0893 | 2097.0917 | 1963.9976 | 793.3071 | 23.4968 | 12.5378 | 13.0042 | 13.827 | 12.5431 | 3.923 | 3688.0836 | 9027.2421 | 11688.7112 | 2517.251 | 5581.796 | 10243.6208 | 0.090932 | 0.10942 | 0.052846 | 23.1753 | 12.454 | 13.9814 | 15.8464 | 71.6767 | 104.9603 | 134.4226 | 101.3341 | 65.6249 | 99.22% | 98.74% | 98.48% | 99.37% | 98.72% | 98.98% | 131.9661 | 109.6649 | 227.073 |  |  |  | 32.7492 | 29.7083 | 9.2917 | 2554.435 | 1426 | 223 | 4203.435 | 109.5092 | 20 | 71 | 158 | 81.5417 | 95.51% | 0.090756 | 0.095185 | 49.0388 | 49.6107 | 122.3921 | 68.0936 | 95.51% | 3966.7849 | 97.97% | 99.1% | 84.97% |  |  | 98.22% | 0.88402
2020-07-07 | 171.1535 | 147.2499 | 147.2499 | 134.2743 | 120.9689 | 13.7055 | 13.7055 | 3472.2492 | 1167.7855 | 201.3423 | 613.4154 | 75.5928 | 19.3828 | 68.8089 | 153.1239 | 9429.9335 | 366.032 |  |  | 28.189 | 0.88621 | 43.7609 | 4085.6647 | 2103.1213 | 1982.5433 | 814.7578 | 23.9035 | 12.9756 | 13.2662 | 13.8667 | 12.512 | 4.3145 | 3460.6874 | 8322.2387 | 11003.6003 | 2366.7962 | 5198.2481 | 9538.4296 | 0.091873 | 0.10934 | 0.057077 | 23.3256 | 12.6134 | 13.8957 | 16.6427 | 75.5957 | 122.0647 | 133.7591 | 101.4094 | 66.9896 | 99.18% | 98.68% | 98.39% | 99.3% | 98.55% | 98.72% | 130.6154 | 109.7481 | 210.2441 |  |  |  | 32.14 | 29 | 10 | 2506.92 | 1392 | 240 | 4138.92 | 107.2295 | 20 | 71 | 158 | 78 | 95.53% | 0.091895 | 0.09573 | 50.1454 | 49.8347 | 122.2974 | 68.5399 | 95.53% | 3734.9244 | 97.98% | 98.96% | 84.99% |  |  | 98.21% | 0.88621
2020-07-06 | 169.3798 | 145.3694 | 145.3694 | 132.3097 | 118.9342 | 13.5561 | 13.5561 | 3471.0398 | 1167.3788 | 201.2722 | 613.2985 | 76.1529 | 19.5264 | 69.3187 | 154.2585 | 9394.2749 | 362.9112 |  |  | 28.0582 | 0.89056 | 44.0851 | 4084.3383 | 2102.3888 | 1981.9495 | 814.5707 | 24.0105 | 13.0596 | 13.3989 | 13.8619 | 12.5076 | 4.313 | 3312.1433 | 7959.5051 | 10521.0297 | 2265.6304 | 4973.6479 | 9121.4608 | 0.093107 | 0.11055 | 0.057132 | 23.4411 | 12.7004 | 14.0391 | 17.5946 | 79.9581 | 129.1774 | 132.5879 | 100.7618 | 67.2298 | 99.14% | 98.61% | 98.31% | 99.22% | 98.39% | 98.58% | 128.8835 | 108.5517 | 210.0396 |  |  |  | 32.14 | 29 | 10 | 2506.92 | 1392 | 240 | 4138.92 | 105.2974 | 20 | 71 | 158 | 78 | 95.29% | 0.092932 | 0.096886 | 50.469 | 50.1806 | 121.5567 | 72.4874 | 95.29% | 3573.933 | 97.87% | 98.86% | 84.98% |  |  | 98.1% | 0.89056
2020-07-05 | 168.4027 | 144.4944 | 144.4944 | 131.3784 | 117.7271 | 13.484 | 13.484 | 3464.3087 | 1165.115 | 200.8819 | 611.5865 | 77.1821 | 19.7903 | 70.2555 | 156.3433 | 9356.1965 | 357.243 |  |  | 28.125 | 0.88834 | 44.6809 | 4075.8952 | 2098.3118 | 1977.5834 | 812.4684 | 23.9082 | 13.116 | 13.404 | 13.835 | 12.4834 | 4.3046 | 3298.7317 | 7928.5066 | 10481.3537 | 2256.4251 | 4953.8376 | 9086.4737 | 0.093262 | 0.11086 | 0.057574 | 23.4154 | 12.7996 | 14.1009 | 17.8257 | 81.0019 | 130.8443 | 131.7814 | 100.0345 | 66.4181 | 99.12% | 98.58% | 98.28% | 99.21% | 98.36% | 98.56% | 128.6703 | 108.2485 | 208.4282 |  |  |  | 32.14 | 29 | 10 | 2506.92 | 1392 | 240 | 4138.92 | 104.3079 | 20 | 71 | 158 | 78 | 95.21% | 0.093182 | 0.09711 | 50.4282 | 50.3159 | 120.7445 | 73.4343 | 95.21% | 3559.6661 | 97.83% | 98.84% | 85% |  |  | 98.08% | 0.88834
2020-07-04 | 170.2016 | 146.4559 | 146.4559 | 133.5091 | 119.8196 | 13.6214 | 13.6214 | 3449.8928 | 1152.7505 | 221.0984 | 609.7858 | 74.5866 | 19.6465 | 69.3875 | 170.2194 | 9812.9914 | 361.2824 |  |  | 28.0255 | 0.89166 | 45.917 | 4059.6786 | 2076.0439 | 1983.6347 | 830.8843 | 23.7458 | 12.9468 | 13.3238 | 13.6882 | 12.3509 | 4.7378 | 3392.877 | 8003.8129 | 10844.1464 | 2329.581 | 5054.5746 | 9280.6485 | 0.09166 | 0.10857 | 0.062594 | 23.315 | 12.4701 | 13.7748 | 17.022 | 77.8649 | 154.0878 | 133.1577 | 101.4352 | 67.4908 | 99.16% | 98.63% | 98.17% | 99.27% | 98.46% | 98.34% | 130.9188 | 110.5279 | 191.7114 |  |  |  | 32.14 | 29 | 11.1244 | 2506.92 | 1392 | 266.9867 | 4165.9066 | 106.3541 | 21.8333 | 77.1111 | 189.1667 | 82.8889 | 95.53% | 0.092421 | 0.095447 | 50.0164 | 49.5599 | 121.7517 | 68.5102 | 95.53% | 3685.5964 | 97.98% | 98.86% | 84.98% |  |  | 98.21% | 0.89166
2020-07-03 | 172.7418 | 148.8845 | 148.8845 | 135.8685 | 122.6153 | 13.6479 | 13.6479 | 3463.4963 | 1152.5448 | 235.2781 | 611.9989 | 72.0983 | 19.2821 | 67.9065 | 175.2155 | 10324.2259 | 368.914 |  |  | 27.8841 | 0.8964 | 46.0555 | 4075.4953 | 2075.6735 | 1999.8218 | 847.277 | 23.8574 | 13.016 | 13.3673 | 13.6858 | 12.3487 | 5.0417 | 3566.1092 | 8324.6888 | 11457.6888 | 2453.7169 | 5288.754 | 9724.9556 | 0.090878 | 0.10786 | 0.066613 | 23.2397 | 12.3222 | 13.5563 | 15.9426 | 73.2031 | 161.9282 | 134.9931 | 102.6243 | 67.8453 | 99.21% | 98.72% | 98.2% | 99.35% | 98.62% | 98.33% | 132.0446 | 111.2518 | 180.1453 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 108.8635 | 23 | 81 | 209 | 86 | 95.9% | 0.092431 | 0.094882 | 50.2407 | 49.1182 | 122.9781 | 63.3098 | 95.9% | 3891.0709 | 98.15% | 98.95% | 84.98% |  |  | 98.34% | 0.8964
2020-07-02 | 172.668 | 149.1827 | 149.1827 | 136.368 | 123.2249 | 13.7184 | 13.7184 | 3432.7278 | 1142.3059 | 233.188 | 606.2866 | 83.6428 | 22.3696 | 78.7798 | 203.2714 | 10738.9338 | 362.1553 |  |  | 27.8307 | 0.8982 | 53.43 | 4039.0144 | 2057.2339 | 1981.7805 | 839.4746 | 23.4853 | 12.8147 | 13.2953 | 13.5642 | 12.239 | 4.9969 | 3694.3143 | 8614.1134 | 11849.0639 | 2542.7803 | 5476.195 | 10060.2601 | 0.090512 | 0.1077 | 0.067196 | 23.1887 | 12.2987 | 13.6728 | 17.7245 | 81.4523 | 180.3434 | 134.605 | 102.07 | 66.7932 | 99.12% | 98.56% | 97.98% | 99.3% | 98.51% | 98.21% | 132.5789 | 111.419 | 178.5828 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 109.3929 | 23 | 81 | 209 | 86 | 95.41% | 0.092282 | 0.094648 | 49.5953 | 49.1602 | 122.1304 | 70.4333 | 95.41% | 4029.5987 | 97.92% | 98.87% | 84.99% |  |  | 98.16% | 0.8982
2020-07-01 | 173.096 | 149.1507 | 149.1507 | 136.0301 | 122.4106 | 13.7623 | 13.7623 | 3469.3896 | 1154.5058 | 235.6784 | 612.0029 | 80.8102 | 21.612 | 76.1119 | 196.3875 | 10400.7328 | 363.4535 |  |  | 27.7105 | 0.90227 | 51.6205 | 4081.3924 | 2079.2053 | 2002.1872 | 847.6813 | 23.9453 | 13.1207 | 13.5809 | 13.709 | 12.3697 | 5.0503 | 3591.6056 | 8379.5583 | 11530.8456 | 2471.7694 | 5325.2958 | 9788.1049 | 0.091549 | 0.1088 | 0.067507 | 23.2778 | 12.4031 | 13.7672 | 17.885 | 82.1583 | 181.8126 | 135.1103 | 102.5822 | 67.4994 | 99.13% | 98.57% | 97.99% | 99.28% | 98.46% | 98.14% | 131.0769 | 110.2954 | 177.7591 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 108.6388 | 23 | 81 | 209 | 86 | 95.44% | 0.093222 | 0.095656 | 50.6468 | 49.4481 | 122.9272 | 71.0478 | 95.44% | 3918.3396 | 97.94% | 98.83% | 85.01% |  |  | 98.14% | 0.90227
2020-06-30 | 171.0535 | 147.0009 | 147.0009 | 133.5732 | 119.7482 | 13.5717 | 13.5717 | 3472.1417 | 1155.4217 | 235.8654 | 613.3102 | 76.9189 | 20.5713 | 72.4469 | 186.9308 | 9829.7492 | 360.0771 |  |  | 27.6357 | 0.90481 | 49.1349 | 4085.4518 | 2080.8546 | 2004.5972 | 849.1755 | 24.0526 | 13.4276 | 13.794 | 13.7199 | 12.3795 | 5.0543 | 3412.0411 | 7956.0244 | 10943.8443 | 2348.4781 | 5057.7984 | 9291.6939 | 0.092769 | 0.11004 | 0.067685 | 23.3449 | 12.6673 | 13.943 | 17.9822 | 82.6357 | 182.9624 | 133.8159 | 101.7886 | 67.5652 | 99.12% | 98.57% | 97.99% | 99.23% | 98.37% | 98.03% | 129.3536 | 109.048 | 177.2914 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 106.0766 | 23 | 81 | 209 | 86 | 95.43% | 0.094283 | 0.096813 | 51.2742 | 49.9552 | 122.1096 | 71.4568 | 95.43% | 3721.7146 | 97.93% | 98.76% | 84.99% |  |  | 98.13% | 0.90481
2020-06-29 | 169.3704 | 145.2964 | 145.2964 | 131.6876 | 117.7284 | 13.5843 | 13.5843 | 3465.5806 | 1153.2383 | 235.4197 | 613.0421 | 72.6512 | 19.43 | 68.4273 | 176.5593 | 9350.144 | 355.3652 |  |  | 27.5157 | 0.90891 | 46.4087 | 4078.6226 | 2076.9226 | 2001.7001 | 848.4618 | 24.0741 | 13.6088 | 13.8899 | 13.694 | 12.3561 | 5.0447 | 3262.0905 | 7602.9517 | 10454.8261 | 2245.4551 | 4834.5838 | 8877.9992 | 0.093852 | 0.11111 | 0.067812 | 23.4219 | 12.8626 | 14.0541 | 17.8105 | 81.8691 | 181.339 | 132.619 | 101.0769 | 67.6165 | 99.13% | 98.58% | 98.01% | 99.21% | 98.31% | 97.96% | 127.8606 | 108.0017 | 176.9611 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 104.1703 | 23 | 81 | 209 | 86 | 95.49% | 0.095208 | 0.097826 | 51.5728 | 50.3386 | 121.3367 | 70.7914 | 95.49% | 3557.5914 | 97.96% | 98.72% | 84.97% |  |  | 98.15% | 0.90891
2020-06-28 | 168.1504 | 144.1649 | 144.1649 | 130.5588 | 116.7898 | 13.4954 | 13.4954 | 3457.1491 | 1150.4326 | 234.8469 | 610.5687 | 71.3908 | 19.0929 | 67.2402 | 173.4963 | 9314.4459 | 351.0332 |  |  | 27.774 | 0.90012 | 45.6036 | 4067.7178 | 2071.8696 | 1995.8482 | 845.4156 | 23.9855 | 13.6061 | 13.861 | 13.6607 | 12.3261 | 5.0324 | 3255.017 | 7592.9098 | 10446.6862 | 2240.1596 | 4825.8633 | 8868.5521 | 0.093467 | 0.11087 | 0.067909 | 23.4325 | 12.9205 | 14.1047 | 17.3309 | 79.6205 | 176.2279 | 131.5569 | 100.0733 | 66.7036 | 99.15% | 98.61% | 98.04% | 99.23% | 98.35% | 98.01% | 128.3875 | 108.2369 | 176.7065 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 103.2562 | 23 | 81 | 209 | 86 | 95.56% | 0.094946 | 0.097521 | 51.4527 | 50.4577 | 120.2793 | 68.8529 | 95.56% | 3550.8741 | 97.99% | 98.75% | 84.99% |  |  | 98.2% | 0.90012
2020-06-27 | 170.5388 | 146.5074 | 146.5074 | 132.9573 | 118.9247 | 13.5542 | 13.5542 | 3467.4112 | 1153.8475 | 235.544 | 612.6754 | 78.5899 | 21.0182 | 74.0208 | 190.9918 | 10037.4196 | 358.2565 |  |  | 27.8184 | 0.89862 | 50.2023 | 4080.0866 | 2078.0196 | 2002.067 | 848.2195 | 24.0315 | 13.55 | 13.9546 | 13.7012 | 12.3627 | 5.0474 | 3472.2509 | 8094.9215 | 11133.5998 | 2390.0206 | 5146.6401 | 9453.3853 | 0.092487 | 0.1102 | 0.068644 | 23.3698 | 12.8062 | 14.1284 | 17.9055 | 82.2932 | 182.2334 | 133.1239 | 100.815 | 66.0748 | 99.12% | 98.56% | 97.98% | 99.25% | 98.4% | 98.07% | 129.7484 | 108.8978 | 174.814 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 105.394 | 23 | 81 | 209 | 86 | 95.42% | 0.094339 | 0.09676 | 51.5361 | 50.3045 | 121.1495 | 71.1593 | 95.42% | 3787.1587 | 97.92% | 98.79% | 84.98% |  |  | 98.14% | 0.89862
2020-06-26 | 172.0707 | 148.0981 | 148.0981 | 134.6501 | 120.4487 | 13.8228 | 13.8228 | 3469.3448 | 1154.4909 | 235.6754 | 611.8882 | 83.4932 | 22.3296 | 78.6389 | 202.9079 | 10560.5557 | 362.9317 |  |  | 27.8397 | 0.8979 | 53.3344 | 4081.2329 | 2079.1784 | 2002.0545 | 847.5635 | 23.9726 | 13.448 | 14.0763 | 13.7089 | 12.3695 | 5.0502 | 3643.6983 | 8499.7693 | 11695.3959 | 2507.7427 | 5402.1714 | 9928.1736 | 0.091973 | 0.11004 | 0.069655 | 23.3061 | 12.7143 | 14.2728 | 18.1253 | 83.2719 | 184.2998 | 133.8345 | 100.9336 | 65.1002 | 99.11% | 98.54% | 97.96% | 99.28% | 98.46% | 98.14% | 130.4726 | 109.0523 | 172.2772 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 106.8232 | 23 | 81 | 209 | 86 | 95.36% | 0.094183 | 0.096469 | 51.4969 | 50.2931 | 121.2811 | 72.0092 | 95.36% | 3974.9952 | 97.9% | 98.83% | 85.01% |  |  | 98.12% | 0.8979
2020-06-25 | 170.0739 | 146.5274 | 146.5274 | 133.3107 | 119.2244 | 13.7794 | 13.7794 | 3432.9995 | 1142.3964 | 233.2064 | 607.2964 | 84.0111 | 22.4681 | 79.1267 | 204.1665 | 10596.5643 | 352.8503 |  |  | 27.7568 | 0.9007 | 53.6652 | 4040.2959 | 2057.3967 | 1982.8992 | 840.5029 | 23.5465 | 13.2167 | 13.8602 | 13.5653 | 12.24 | 4.9973 | 3661.1087 | 8529.6742 | 11726.7323 | 2520.3872 | 5425.0544 | 9959.1595 | 0.09254 | 0.1109 | 0.070646 | 23.2353 | 12.67 | 14.2237 | 18.0121 | 82.8185 | 183.5 | 132.0317 | 99.41 | 63.7132 | 99.11% | 98.54% | 97.95% | 99.29% | 98.47% | 98.16% | 129.6732 | 108.2057 | 169.8619 |  |  |  | 32.14 | 29 | 11.84 | 2506.92 | 1392 | 284.16 | 4183.08 | 105.5448 | 23 | 81 | 209 | 86 | 95.35% | 0.094912 | 0.097162 | 50.6234 | 50.1289 | 119.4412 | 71.6088 | 95.35% | 3992.2927 | 97.9% | 98.85% | 84.97% |  |  | 98.13% | 0.9007
2020-06-24 | 168.8714 | 144.9604 | 144.9604 | 131.2774 | 117.0452 | 13.6886 | 13.6886 | 3457.4572 | 1167.5838 | 261.6998 | 609.8326 | 79.7249 | 21.3218 | 75.0897 | 193.7501 | 10113.3549 | 352.8189 |  |  | 27.7836 | 0.8998 | 52.5306 | 4067.2898 | 2028.1736 | 2039.1162 | 871.5324 | 23.9109 | 13.6831 | 14.1721 | 13.3726 | 12.5098 | 5.6079 | 3426.6345 | 7916.6675 | 11230.8327 | 2386.9069 | 5059.2873 | 9381.3775 | 0.091573 | 0.11312 | 0.078189 | 23.1142 | 12.5318 | 14.0522 | 17.7748 | 86.0466 | 207.2408 | 131.3994 | 99.5093 | 64.5345 | 99.11% | 98.52% | 97.93% | 99.26% | 98.3% | 97.79% | 131.0436 | 106.084 | 153.4733 |  |  |  | 31 | 29 | 13 | 2418 | 1392 | 312 | 4122 | 103.3692 | 23 | 81 | 209 | 86 | 95.39% | 0.096326 | 0.097835 | 51.7661 | 49.6982 | 119.0899 | 71.477 | 95.39% | 3818.7915 | 97.91% | 98.72% | 85.01% |  |  | 98.13% | 0.8998
2020-06-23 | 168.4418 | 144.2504 | 144.2504 | 130.2856 | 115.8528 | 13.6189 | 13.6189 | 3472.0563 | 1172.5139 | 262.8048 | 613.2059 | 76.0982 | 20.3518 | 71.6738 | 184.9362 | 9732.3797 | 352.9702 |  |  | 27.6314 | 0.90496 | 50.1409 | 4085.2622 | 2036.7375 | 2048.5247 | 876.0108 | 24.1914 | 13.9648 | 14.3799 | 13.429 | 12.5626 | 5.6315 | 3314.05 | 7653.8724 | 10854.8731 | 2308.6268 | 4892.3205 | 9068.7218 | 0.092567 | 0.11421 | 0.078367 | 23.2289 | 12.6988 | 14.1456 | 17.7166 | 85.7833 | 206.6763 | 131.2858 | 99.5459 | 65.0314 | 99.12% | 98.53% | 97.96% | 99.23% | 98.25% | 97.72% | 129.6359 | 105.0738 | 153.126 |  |  |  | 31 | 29 | 13 | 2418 | 1392 | 312 | 4122 | 102.192 | 23 | 81 | 209 | 86 | 95.45% | 0.097219 | 0.098799 | 52.5361 | 50.0734 | 119.3043 | 71.2572 | 95.45% | 3692.8217 | 97.94% | 98.68% | 84.99% |  |  | 98.14% | 0.90496
2020-06-22 | 166.4814 | 142.2234 | 142.2234 | 128.1144 | 113.6581 | 13.2838 | 13.2838 | 3470.6372 | 1172.0347 | 262.6974 | 612.8813 | 73.4999 | 19.6569 | 69.2266 | 178.6217 | 9323.0702 | 347.3174 |  |  | 27.714 | 0.90215 | 48.4289 | 4083.5185 | 2035.9051 | 2047.6134 | 875.5787 | 24.2579 | 14.1091 | 14.5178 | 13.4235 | 12.5575 | 5.6292 | 3189.0914 | 7365.2891 | 10445.6883 | 2221.5842 | 4707.8552 | 8726.828 | 0.093112 | 0.11479 | 0.078297 | 23.308 | 12.8388 | 14.2922 | 17.7198 | 85.7987 | 206.7122 | 130.059 | 98.692 | 64.8614 | 99.12% | 98.53% | 97.95% | 99.2% | 98.18% | 97.63% | 128.8767 | 104.5393 | 153.2635 |  |  |  | 31 | 29 | 13 | 2418 | 1392 | 312 | 4122 | 100.271 | 23 | 81 | 209 | 86 | 95.43% | 0.097678 | 0.099311 | 52.8848 | 50.439 | 118.435 | 71.2698 | 95.43% | 3553.5894 | 97.93% | 98.62% | 84.99% |  |  | 98.13% | 0.90215
2020-06-21 | 166.1787 | 142.2653 | 142.2653 | 128.3933 | 113.8816 | 13.2989 | 13.2989 | 3440.1283 | 1161.7318 | 260.3882 | 607.5306 | 76.0677 | 20.3437 | 71.6452 | 184.8623 | 9656.4256 | 342.845 |  |  | 27.496 | 0.90958 | 50.1209 | 4047.6588 | 2018.0083 | 2029.6506 | 867.9188 | 23.9134 | 13.872 | 14.4683 | 13.3055 | 12.4471 | 5.5797 | 3290.5976 | 7599.2492 | 10777.0621 | 2292.3303 | 4857.5726 | 9003.8662 | 0.09341 | 0.11541 | 0.07962 | 23.2828 | 12.7909 | 14.4323 | 17.7617 | 86.0056 | 207.222 | 129.5632 | 98.1008 | 63.7436 | 99.11% | 98.53% | 97.95% | 99.23% | 98.23% | 97.7% | 128.4657 | 103.9781 | 150.7164 |  |  |  | 31 | 29 | 13 | 2418 | 1392 | 312 | 4122 | 100.5782 | 23 | 81 | 209 | 86 | 95.42% | 0.098243 | 0.099795 | 52.2536 | 50.506 | 117.5892 | 71.4413 | 95.42% | 3666.6186 | 97.93% | 98.66% | 84.99% |  |  | 98.13% | 0.90958
2020-06-20 | 167.688 | 143.9121 | 143.9121 | 130.1286 | 115.7908 | 13.546 | 13.546 | 3438.479 | 1161.1749 | 260.2633 | 606.8565 | 80.9926 | 21.6608 | 76.2837 | 196.8308 | 10249.4843 | 347.3086 |  |  | 27.4758 | 0.91027 | 53.3658 | 4045.3355 | 2017.0408 | 2028.2947 | 867.1198 | 23.7758 | 13.7835 | 14.4269 | 13.2992 | 12.4412 | 5.5771 | 3468.4269 | 8010.9035 | 11362.135 | 2416.1699 | 5120.3534 | 9492.1109 | 0.092921 | 0.11526 | 0.080662 | 23.1699 | 12.7236 | 14.4125 | 17.9474 | 86.8984 | 209.3476 | 130.2815 | 98.254 | 62.9373 | 99.1% | 98.51% | 97.93% | 99.26% | 98.3% | 97.79% | 129.142 | 104.1115 | 148.7685 |  |  |  | 31 | 29 | 13 | 2418 | 1392 | 312 | 4122 | 102.1314 | 23 | 81 | 209 | 86 | 95.37% | 0.098108 | 0.099537 | 51.9862 | 50.306 | 117.7133 | 72.1831 | 95.37% | 3864.961 | 97.9% | 98.72% | 85% |  |  | 98.11% | 0.91027
2020-06-19 | 169.427 | 145.1736 | 145.1736 | 131.0585 | 116.1905 | 13.7203 | 13.7203 | 3470.674 | 1170.3436 | 267.363 | 613.803 | 82.189 | 22.0128 | 77.4036 | 197.756 | 10394.3715 | 353.6848 |  |  | 27.5331 | 0.90831 | 54.2294 | 4084.477 | 2032.9675 | 2051.5095 | 881.166 | 24.2534 | 14.1151 | 14.8254 | 13.4042 | 12.5394 | 5.7292 | 3510.812 | 8070.983 | 11500.4374 | 2448.0848 | 5172.4884 | 9584.1518 | 0.092622 | 0.11514 | 0.082638 | 23.276 | 12.782 | 14.4998 | 18.1043 | 87.7849 | 213.5328 | 131.4496 | 98.9203 | 62.9722 | 99.1% | 98.5% | 97.94% | 99.26% | 98.3% | 97.77% | 129.5584 | 104.221 | 145.2115 |  |  |  | 31 | 29 | 13.25 | 2418 | 1392 | 318 | 4128 | 102.5652 | 23 | 80.875 | 206.625 | 85.875 | 95.37% | 0.09823 | 0.099446 | 53.1939 | 50.5578 | 118.6627 | 72.8049 | 95.37% | 3916.5051 | 97.9% | 98.72% | 84.97% |  |  | 98.09% | 0.90831
2020-06-18 | 166.4468 | 142.8154 | 142.8154 | 129.1055 | 114.5113 | 13.5225 | 13.5225 | 3416.907 | 1140.6078 | 294.9848 | 602.796 | 84.9654 | 22.9906 | 79.9674 | 189.9227 | 10455.8412 | 343.5083 |  |  | 27.3386 | 0.91499 | 56.4216 | 4019.7031 | 1981.3144 | 2038.3886 | 897.7808 | 23.6314 | 13.7099 | 14.6013 | 13.0636 | 12.2208 | 6.3211 | 3496.8729 | 7837.9649 | 11580.6174 | 2451.614 | 5095.8538 | 9467.0282 | 0.092685 | 0.11485 | 0.093437 | 23.1178 | 12.393 | 14.2007 | 18.5369 | 90.3776 | 230.7456 | 128.9655 | 97.3585 | 61.9004 | 99.06% | 98.43% | 97.99% | 99.24% | 98.23% | 97.56% | 129.4713 | 104.4811 | 128.4292 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 100.9767 | 23 | 80 | 190 | 85 | 95.24% | 0.099899 | 0.10015 | 51.9426 | 49.7115 | 116.0381 | 74.1995 | 95.24% | 3939.9427 | 97.84% | 98.65% | 85% |  |  | 98.06% | 0.91499
2020-06-17 | 167.8551 | 143.445 | 143.445 | 129.2732 | 114.2815 | 13.6437 | 13.6437 | 3472.9123 | 1159.3031 | 299.8198 | 612.2273 | 85.6648 | 23.1799 | 80.6257 | 191.486 | 10373.1905 | 352.9532 |  |  | 27.4451 | 0.91133 | 56.8861 | 4085.1395 | 2013.7894 | 2071.3501 | 912.047 | 24.4101 | 14.1718 | 15.1633 | 13.2777 | 12.4211 | 6.4247 | 3428.737 | 7684.5218 | 11354.0093 | 2403.9437 | 4996.3587 | 9281.7331 | 0.093006 | 0.11535 | 0.093407 | 23.3094 | 12.5075 | 14.4046 | 19.2949 | 94.0808 | 240.212 | 130.1026 | 98.1368 | 62.6824 | 99.04% | 98.39% | 97.94% | 99.2% | 98.12% | 97.41% | 129.0236 | 104.0349 | 128.4694 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 100.4816 | 23 | 80 | 190 | 85 | 95.1% | 0.10022 | 0.1005 | 53.7452 | 50.2216 | 117.3335 | 77.2382 | 95.1% | 3863.0914 | 97.78% | 98.57% | 85.01% |  |  | 97.98% | 0.91133
2020-06-16
2020-06-15 | 165.2716 | 140.948 | 140.948 | 126.4395 | 111.3681 | 13.3809 | 13.3809 | 3475.2305 | 1160.0769 | 300.0199 | 613.2655 | 72.8416 | 19.7101 | 68.5568 | 162.8223 | 9295.5656 | 344.2201 |  |  | 27.3824 | 0.91348 | 48.3707 | 4088.4959 | 2015.1336 | 2073.3623 | 913.2854 | 24.3236 | 14.5085 | 15.187 | 13.2866 | 12.4294 | 6.429 | 3159.2879 | 7085.2084 | 10471.7574 | 2214.5902 | 4605.0073 | 8559.0933 | 0.094265 | 0.1163 | 0.092424 | 23.1964 | 12.7838 | 14.3949 | 17.8635 | 87.0598 | 222.1721 | 128.7544 | 97.6306 | 63.5415 | 99.11% | 98.51% | 98.1% | 99.19% | 98.11% | 97.4% | 127.3002 | 103.185 | 129.8359 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 97.9571 | 23 | 80 | 190 | 85 | 95.48% | 0.10102 | 0.10146 | 54.019 | 50.3751 | 116.8007 | 71.4789 | 95.48% | 3560.2693 | 97.95% | 98.56% | 85% |  |  | 98.13% | 0.91348
2020-06-14 | 164.2664 | 140.3465 | 140.3465 | 126.1201 | 110.84 | 13.3465 | 13.3465 | 3440.024 | 1148.3246 | 296.9805 | 606.7031 | 74.3483 | 20.1178 | 69.9749 | 166.1904 | 9447.4846 | 337.6509 |  |  | 27.3905 | 0.9132 | 49.3713 | 4046.7271 | 1994.719 | 2052.0082 | 903.6836 | 23.9199 | 14.2264 | 15.1512 | 13.152 | 12.3035 | 6.3639 | 3196.1381 | 7168.6014 | 10596.2735 | 2240.3851 | 4658.9319 | 8660.3167 | 0.093935 | 0.1159 | 0.092742 | 23.1665 | 12.7327 | 14.5921 | 17.835 | 86.9157 | 221.7788 | 127.8586 | 96.9421 | 62.6629 | 99.1% | 98.5% | 98.08% | 99.2% | 98.13% | 97.44% | 127.7476 | 103.5377 | 129.3909 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 97.556 | 23 | 80 | 190 | 85 | 95.44% | 0.10077 | 0.10116 | 53.2975 | 50.4913 | 115.7555 | 71.3605 | 95.44% | 3601.966 | 97.94% | 98.58% | 85.01% |  |  | 98.13% | 0.9132
2020-06-13 | 165.6737 | 141.7326 | 141.7326 | 127.4917 | 112.1556 | 13.5703 | 13.5703 | 3449.9266 | 1151.6302 | 297.8354 | 608.8737 | 78.5197 | 21.2465 | 73.9009 | 175.5145 | 9912.0928 | 342.7858 |  |  | 27.3542 | 0.91446 | 52.1413 | 4058.8003 | 2000.461 | 2058.3392 | 906.7091 | 23.9412 | 14.2409 | 15.1881 | 13.1899 | 12.3389 | 6.3822 | 3340.2522 | 7488.9135 | 11066.3207 | 2341.6181 | 4868.1807 | 9045.9748 | 0.093841 | 0.11624 | 0.094283 | 23.0826 | 12.6854 | 14.5525 | 18.098 | 88.2203 | 225.19 | 128.5311 | 97.0705 | 61.9011 | 99.09% | 98.48% | 98.06% | 99.23% | 98.19% | 97.51% | 127.8754 | 103.2356 | 127.2763 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 98.6109 | 23 | 80 | 190 | 85 | 95.39% | 0.10108 | 0.10136 | 53.3701 | 50.3204 | 115.9371 | 72.4303 | 95.39% | 3763.8108 | 97.91% | 98.62% | 85% |  |  | 98.1% | 0.91446
2020-06-12 | 167.5619 | 143.505 | 143.505 | 129.3928 | 113.9528 | 13.6154 | 13.6154 | 3463.1413 | 1156.0414 | 298.9762 | 610.8116 | 83.7458 | 22.6606 | 78.8196 | 187.1965 | 10533.8324 | 350.6223 |  |  | 27.4609 | 0.91078 | 55.6117 | 4073.9529 | 2008.1237 | 2065.8292 | 909.7878 | 24.0569 | 14.1122 | 15.2386 | 13.2404 | 12.3862 | 6.4066 | 3533.1867 | 7922.5526 | 11708.8065 | 2476.8135 | 5149.6722 | 9570.4239 | 0.093015 | 0.11573 | 0.095436 | 23.066 | 12.5038 | 14.5288 | 18.2453 | 88.9311 | 226.9714 | 129.6473 | 97.4792 | 61.1413 | 99.09% | 98.47% | 98.04% | 99.26% | 98.27% | 97.63% | 129.0117 | 103.6911 | 125.7391 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 100.3294 | 23 | 80 | 190 | 85 | 95.35% | 0.10067 | 0.10081 | 53.4078 | 50.0986 | 116.4488 | 73.0138 | 95.35% | 3981.4464 | 97.9% | 98.68% | 85.01% |  |  | 98.09% | 0.91078
2020-06-11 | 165.6746 | 142.0685 | 142.0685 | 128.1429 | 113.1119 | 13.6476 | 13.6476 | 3425.0274 | 1143.3185 | 295.6858 | 604.0336 | 86.3996 | 23.3787 | 81.3173 | 193.1285 | 10709.0173 | 341.2166 |  |  | 27.6923 | 0.90289 | 57.374 | 4029.0611 | 1986.0231 | 2043.0379 | 899.7194 | 23.6061 | 13.9256 | 15.1103 | 13.0947 | 12.2498 | 6.3361 | 3582.1555 | 8030.8458 | 11867.5559 | 2511.2748 | 5220.6193 | 9700.7458 | 0.092523 | 0.1155 | 0.096243 | 23.0132 | 12.5457 | 14.6492 | 18.2017 | 88.7306 | 226.4954 | 127.7844 | 95.7616 | 59.4417 | 99.07% | 98.44% | 98.01% | 99.28% | 98.3% | 97.67% | 129.6971 | 103.898 | 124.6849 |  |  |  | 31 | 29 | 15 | 2418 | 1392 | 360 | 4170 | 99.4084 | 23 | 80 | 190 | 85 | 95.27% | 0.10047 | 0.10051 | 52.642 | 50.2081 | 114.383 | 72.848 | 95.27% | 4036.3628 | 97.86% | 98.71% | 85.01% |  |  | 98.09% | 0.90289
2020-06-10 | 165.2332 | 141.3958 | 141.3958 | 127.1972 | 111.8726 | 13.6831 | 13.6831 | 3436.3149 | 1175.4164 | 302.6944 | 605.6118 | 81.2713 | 21.991 | 76.4906 | 181.6652 | 10393.8595 | 341.3939 |  |  | 27.6177 | 0.90542 | 54.6982 | 4041.9267 | 1958.2041 | 2083.7226 | 908.3062 | 23.8374 | 14.1985 | 15.3723 | 12.9112 | 12.5937 | 6.4863 | 3434.6268 | 7780.3068 | 11578.2285 | 2429.6021 | 5028.123 | 9428.954 | 0.09162 | 0.11896 | 0.098513 | 22.9347 | 12.4769 | 14.7533 | 17.498 | 89.3422 | 225.0181 | 127.5933 | 95.8552 | 59.6153 | 99.09% | 98.48% | 98.07% | 99.28% | 98.22% | 97.61% | 130.9752 | 100.8764 | 121.8118 |  |  |  | 30.5 | 29.75 | 15.3225 | 2379 | 1428 | 367.74 | 4174.74 | 98.2226 | 23 | 80 | 190 | 85 | 95.44% | 0.10147 | 0.10158 | 53.4082 | 50.1649 | 114.3345 | 70.7189 | 95.44% | 3934.9963 | 97.93% | 98.68% | 85.02% |  |  | 98.15% | 0.90542
2020-06-09 | 166.3868 | 141.9361 | 141.9361 | 127.1861 | 111.2758 | 13.5785 | 13.5785 | 3472.3539 | 1273.2362 | 324.0784 | 612.5019 | 74.3908 | 20.1293 | 70.0149 | 166.2854 | 9964.8233 | 348.9971 |  |  | 27.4831 | 0.91002 | 52.0621 | 4084.8557 | 1875.0392 | 2209.8165 | 936.5803 | 24.4507 | 14.75 | 16.0268 | 12.3629 | 13.6418 | 6.9445 | 3147.4288 | 7331.0261 | 11121.9334 | 2285.7615 | 4663.3674 | 8964.6513 | 0.087041 | 0.12666 | 0.10249 | 22.5836 | 12.0195 | 14.8607 | 16.3843 | 95.9982 | 233.1183 | 129.2548 | 98.0158 | 61.6606 | 99.12% | 98.5% | 98.15% | 99.28% | 97.94% | 97.4% | 137.8653 | 94.7442 | 117.0827 |  |  |  | 29 | 32 | 16.29 | 2262 | 1536 | 390.96 | 4188.96 | 97.6667 | 23 | 80 | 190 | 85 | 95.65% | 0.10219 | 0.10301 | 55.2275 | 49.4638 | 116.0733 | 68.422 | 95.65% | 3780.9253 | 98.03% | 98.55% | 85.01% |  |  | 98.21% | 0.91002
2020-06-08 | 164.881 | 140.3609 | 140.3609 | 125.3273 | 108.8902 | 13.5098 | 13.5098 | 3452.3392 | 1265.8973 | 322.2104 | 614.5068 | 112.5252 | 30.448 | 105.9061 | 251.527 | 9187.5587 | 342.9898 |  |  | 27.1498 | 0.92153 | 78.7504 | 4066.846 | 1864.2315 | 2202.6145 | 936.7172 | 24.5201 | 15.0336 | 16.4592 | 12.2916 | 13.5632 | 6.9045 | 2973.4147 | 6848.6197 | 10307.7388 | 2164.588 | 4384.3467 | 8343.7759 | 0.08819 | 0.12762 | 0.10078 | 22.7844 | 12.2919 | 15.23 | 26.3488 | 155.5014 | 381.4378 | 128.4404 | 97.9421 | 63.1377 | 98.59% | 97.58% | 96.99% | 98.78% | 96.45% | 95.43% | 136.0704 | 94.0328 | 119.0769 |  |  |  | 29 | 32 | 16.29 | 2262 | 1536 | 390.96 | 4188.96 | 95.6897 | 23 | 80 | 190 | 85 | 93.07% | 0.10282 | 0.10382 | 56.0128 | 50.3064 | 115.6711 | 110.8159 | 93.07% | 3555.235 | 96.83% | 97.5% | 84.89% |  |  | 97.1% | 0.92153
2020-06-07 | 162.6066 | 138.696 | 138.696 | 124.1151 | 108.2394 | 13.3899 | 13.3899 | 3420.4245 | 1254.1948 | 319.2318 | 603.6986 | 70.7229 | 19.1368 | 66.5627 | 158.0865 | 9462.9948 | 331.931 |  |  | 27.0858 | 0.92376 | 49.4952 | 4024.1231 | 1846.9978 | 2177.1252 | 922.9304 | 23.9106 | 14.5809 | 15.8392 | 12.178 | 13.4378 | 6.8407 | 3012.6675 | 7016.2082 | 10642.7373 | 2187.9391 | 4463.4445 | 8579.086 | 0.088987 | 0.12926 | 0.10413 | 22.5857 | 12.1491 | 15.0119 | 16.2715 | 95.3445 | 231.5644 | 126.4174 | 96.0312 | 60.6823 | 99.13% | 98.51% | 98.16% | 99.26% | 97.86% | 97.3% | 134.8505 | 92.8339 | 115.2351 |  |  |  | 29 | 32 | 16.29 | 2262 | 1536 | 390.96 | 4188.96 | 94.9104 | 23 | 80 | 190 | 85 | 95.68% | 0.1043 | 0.10517 | 54.3307 | 49.7467 | 113.6906 | 67.9565 | 95.68% | 3618.8096 | 98.05% | 98.5% | 85% |  |  | 98.22% | 0.92376
2020-06-06 | 165.8387 | 141.6115 | 141.6115 | 126.8875 | 110.9242 | 13.649 | 13.649 | 3457.9868 | 1267.9681 | 322.7375 | 609.5344 | 75.6451 | 20.4687 | 71.1953 | 169.0889 | 10058.3705 | 343.635 |  |  | 27.1498 | 0.92153 | 52.9399 | 4067.5213 | 1867.2812 | 2200.2401 | 932.272 | 24.2272 | 14.724 | 16.0386 | 12.3117 | 13.5854 | 6.9158 | 3180.7654 | 7410.0418 | 11243.9962 | 2309.9006 | 4713.1348 | 9062.0952 | 0.088204 | 0.12855 | 0.10484 | 22.5214 | 12.0781 | 14.977 | 16.6258 | 97.4024 | 236.482 | 128.6289 | 97.3908 | 60.7918 | 99.11% | 98.49% | 98.13% | 99.28% | 97.93% | 97.39% | 136.0476 | 93.3508 | 114.4654 |  |  |  | 29 | 32 | 16.29 | 2262 | 1536 | 390.96 | 4188.96 | 97.2743 | 23 | 80 | 190 | 85 | 95.63% | 0.10378 | 0.10455 | 54.9897 | 49.5766 | 115.2676 | 69.4223 | 95.63% | 3821.3034 | 98.02% | 98.55% | 85.01% |  |  | 98.18% | 0.92153
2020-06-05 | 167.2602 | 143.1923 | 143.1923 | 128.7005 | 112.7117 | 13.6288 | 13.6288 | 3450.2955 | 1265.1479 | 322.0197 | 609.7193 | 80.6639 | 21.8267 | 75.919 | 180.3075 | 10654.1785 | 347.2846 |  |  | 27.0785 | 0.92401 | 56.4523 | 4060.0148 | 1863.1279 | 2196.8868 | 931.739 | 24.0679 | 14.4918 | 15.907 | 12.2844 | 13.5552 | 6.9004 | 3342.2335 | 7777.35 | 11789.6838 | 2427.6928 | 4949.9672 | 9506.9173 | 0.087606 | 0.12788 | 0.10549 | 22.4316 | 11.9099 | 14.8591 | 16.8765 | 98.9414 | 240.4849 | 129.5681 | 97.9474 | 60.4442 | 99.1% | 98.47% | 98.1% | 99.3% | 98% | 97.47% | 136.9772 | 93.8406 | 113.758 |  |  |  | 29 | 32 | 16.29 | 2262 | 1536 | 390.96 | 4188.96 | 99.0683 | 23 | 80 | 190 | 85 | 95.56% | 0.10335 | 0.10404 | 54.4666 | 49.2006 | 115.6723 | 70.5202 | 95.56% | 4013.2671 | 97.99% | 98.59% | 84.98% |  |  | 98.15% | 0.92401
2020-06-04 | 166.5473 | 142.7707 | 142.7707 | 128.5916 | 112.804 | 13.6614 | 13.6614 | 3430.131 | 1157.416 | 319.2939 | 605.9427 | 84.0543 | 23.3183 | 73.7509 | 263.0087 | 10908.7766 | 343.0218 |  |  | 27.0513 | 0.92496 | 62.6472 | 4036.0738 | 1953.4211 | 2082.6526 | 925.2367 | 23.7765 | 14.1792 | 15.6142 | 12.8797 | 12.4009 | 6.842 | 3562.9741 | 7927.7845 | 11966.6421 | 2521.8689 | 5175.6937 | 9671.6041 | 0.092707 | 0.11885 | 0.10549 | 22.9149 | 12.3615 | 14.7327 | 18.2164 | 84.1827 | 342.2467 | 128.5048 | 96.51 | 59.9934 | 99.08% | 98.58% | 97.28% | 99.28% | 98.37% | 96.46% | 129.4406 | 100.9664 | 113.7566 |  |  |  | 30.665 | 29.525 | 16.29 | 2391.87 | 1417.2 | 390.96 | 4200.03 | 99.1072 | 21.5 | 68 | 242.5 | 77.5 | 95.46% | 0.10312 | 0.10272 | 53.5698 | 50.0092 | 114.7293 | 71.8831 | 95.46% | 4082.8723 | 97.94% | 98.54% | 84.99% |  |  | 98.12% | 0.92496
2020-06-03 | 166.7379 | 142.4051 | 142.4051 | 127.7957 | 111.7797 | 13.623 | 13.623 | 3472.9802 | 1138.1295 | 322.9988 | 611.7422 | 82.9783 | 23.2339 | 70.8081 | 287.6581 | 10628.2321 | 346.9553 |  |  | 27.3742 | 0.91376 | 63.4168 | 4084.7224 | 2011.8519 | 2072.8705 | 934.741 | 24.3329 | 14.6094 | 16.04 | 13.265 | 12.1942 | 6.9214 | 3537.0049 | 7757.4046 | 11701.4171 | 2480.734 | 5105.89 | 9460.7179 | 0.094209 | 0.11571 | 0.10489 | 23.2294 | 12.7383 | 14.9105 | 18.7733 | 79.588 | 382.4196 | 128.661 | 96.302 | 60.2994 | 99.06% | 98.61% | 96.96% | 99.24% | 98.44% | 95.96% | 127.3762 | 103.7116 | 114.4106 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 98.2087 | 21 | 64 | 260 | 75 | 95.41% | 0.1028 | 0.10225 | 54.9823 | 50.8782 | 115.1662 | 72.6282 | 95.41% | 3990.1851 | 97.92% | 98.46% | 85.02% |  |  | 98.1% | 0.91376
2020-06-02 | 163.7782 | 139.9266 | 139.9266 | 125.4737 | 109.5317 | 13.4999 | 13.4999 | 3427.995 | 1123.3874 | 318.815 | 604.4918 | 80.0953 | 22.4267 | 68.348 | 277.6638 | 10206.6256 | 336.1011 |  |  | 27.0369 | 0.92547 | 61.2135 | 4032.4869 | 1985.7926 | 2046.6942 | 923.3068 | 23.8516 | 14.4529 | 15.853 | 13.0931 | 12.0363 | 6.8318 | 3421.0328 | 7500.2443 | 11309.5051 | 2399.5913 | 4937.6723 | 9145.583 | 0.095814 | 0.11744 | 0.10597 | 23.2119 | 12.842 | 15.0078 | 18.728 | 79.4154 | 381.7338 | 126.4666 | 94.8536 | 59.6632 | 99.07% | 98.62% | 96.96% | 99.22% | 98.39% | 95.83% | 125.2426 | 102.1836 | 113.2387 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 96.0375 | 21 | 64 | 260 | 75 | 95.42% | 0.10436 | 0.10384 | 54.1575 | 51.0617 | 113.3336 | 72.4703 | 95.42% | 3858.745 | 97.92% | 98.41% | 85.01% |  |  | 98.1% | 0.92547
2020-06-01 | 162.2712 | 138.0297 | 138.0297 | 123.1425 | 106.9157 | 13.48 | 13.48 | 3443.7498 | 1128.5504 | 320.2803 | 607.1232 | 71.4616 | 20.0092 | 60.9806 | 247.7335 | 9286.2496 | 334.491 |  |  | 26.9272 | 0.92931 | 54.6151 | 4050.873 | 1994.9192 | 2055.9539 | 927.4035 | 24.2415 | 14.8872 | 16.3266 | 13.1533 | 12.0916 | 6.8631 | 3149.2758 | 6907.3993 | 10420.6226 | 2208.6931 | 4546.2837 | 8424.5906 | 0.097223 | 0.11868 | 0.10513 | 23.4313 | 13.1392 | 15.3546 | 18.3125 | 77.6295 | 372.9747 | 125.727 | 94.6796 | 60.6648 | 99.09% | 98.66% | 97.06% | 99.17% | 98.29% | 95.57% | 123.4281 | 101.1097 | 114.139 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 93.3994 | 21 | 64 | 260 | 75 | 95.56% | 0.10536 | 0.10499 | 55.4553 | 51.9251 | 113.3847 | 70.8412 | 95.56% | 3552.8436 | 97.99% | 98.31% | 85.01% |  |  | 98.15% | 0.92931
2020-05-31 | 164.3795 | 139.8783 | 139.8783 | 124.8686 | 108.4466 | 13.6283 | 13.6283 | 3471.1372 | 1137.5255 | 322.8274 | 611.9137 | 73.1893 | 20.493 | 62.4549 | 253.7229 | 9548.3743 | 340.9433 |  |  | 26.7404 | 0.9359 | 55.9355 | 4083.0509 | 2010.7843 | 2072.2666 | 934.7411 | 24.5012 | 15.0097 | 16.4245 | 13.2579 | 12.1878 | 6.9177 | 3230.0195 | 7084.7615 | 10688.6133 | 2265.2993 | 4662.9209 | 8641.0677 | 0.097489 | 0.11914 | 0.10598 | 23.4031 | 13.0913 | 15.2653 | 18.5627 | 78.688 | 378.0455 | 127.2766 | 95.7428 | 61.0926 | 99.1% | 98.66% | 97.06% | 99.18% | 98.31% | 95.63% | 123.0908 | 100.7243 | 113.2341 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 94.8072 | 21 | 64 | 260 | 75 | 95.56% | 0.10577 | 0.10537 | 55.9354 | 51.7597 | 114.6724 | 71.8072 | 95.56% | 3643.991 | 97.99% | 98.33% | 85.01% |  |  | 98.12% | 0.9359
2020-05-30 | 165.1667 | 140.9226 | 140.9226 | 126.1793 | 110.098 | 13.5774 | 13.5774 | 3458.3527 | 1133.3359 | 321.6384 | 609.286 | 80.7882 | 22.6207 | 68.9392 | 280.0656 | 10241.6876 | 340.0315 |  |  | 26.7876 | 0.93423 | 61.743 | 4067.6387 | 2003.3784 | 2064.2603 | 930.9244 | 24.2441 | 14.7433 | 16.1372 | 13.2091 | 12.1429 | 6.8923 | 3433.3394 | 7529.2636 | 11356.0711 | 2408.09 | 4956.0188 | 9182.0262 | 0.096757 | 0.11874 | 0.10722 | 23.2903 | 12.9352 | 15.0925 | 19.1698 | 81.2748 | 390.5669 | 127.5399 | 95.5381 | 60.0515 | 99.06% | 98.61% | 96.95% | 99.2% | 98.36% | 95.75% | 124.0226 | 101.0607 | 111.9154 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 96.5198 | 21 | 64 | 260 | 75 | 95.39% | 0.10547 | 0.10493 | 55.1246 | 51.3181 | 114.3146 | 74.1673 | 95.39% | 3873.0698 | 97.91% | 98.38% | 85.02% |  |  | 98.06% | 0.93423
2020-05-29 | 166.4531 | 142.199 | 142.199 | 127.5265 | 111.425 | 13.5996 | 13.5996 | 3462.3623 | 1134.6499 | 322.0113 | 611.974 | 86.6896 | 24.2731 | 73.9752 | 300.5241 | 10737.5004 | 345.4562 |  |  | 26.7925 | 0.93406 | 66.2532 | 4074.3363 | 2005.7011 | 2068.6352 | 933.9853 | 24.2541 | 14.6725 | 16.0883 | 13.2244 | 12.157 | 6.9002 | 3580.4378 | 7840.2557 | 11807.5459 | 2512.1689 | 5165.0321 | 9554.659 | 0.096287 | 0.11852 | 0.10813 | 23.2369 | 12.8253 | 14.9629 | 19.7371 | 83.7643 | 403.1454 | 128.2869 | 95.8078 | 59.6055 | 99.03% | 98.57% | 96.85% | 99.21% | 98.38% | 95.78% | 124.6275 | 101.2473 | 110.9761 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 97.8044 | 21 | 64 | 260 | 75 | 95.26% | 0.1053 | 0.10468 | 55.0149 | 51.0251 | 114.6074 | 76.4372 | 95.26% | 4036.5132 | 97.85% | 98.4% | 84.98% |  |  | 98% | 0.93406
2020-05-28 | 165.0308 | 140.9174 | 140.9174 | 126.3222 | 110.3812 | 13.7374 | 13.7374 | 3449.9864 | 1130.5942 | 320.8603 | 609.2281 | 87.0628 | 24.3776 | 74.2936 | 301.8178 | 10228.7945 | 340.9366 |  |  | 26.7852 | 0.93432 | 66.5384 | 4059.2145 | 1998.5319 | 2060.6825 | 930.0883 | 24.1133 | 14.5952 | 15.9401 | 13.1771 | 12.1135 | 6.8756 | 3557.0671 | 7790.6473 | 11734.7663 | 2495.6874 | 5131.7679 | 9494.9311 | 0.097033 | 0.11965 | 0.10953 | 23.2329 | 12.8337 | 14.9211 | 19.8872 | 84.3908 | 406.0834 | 126.8802 | 94.5951 | 58.6488 | 99.02% | 98.55% | 96.82% | 99.2% | 98.36% | 95.72% | 123.6689 | 100.2966 | 109.5563 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 96.6279 | 21 | 64 | 260 | 75 | 95.21% | 0.10627 | 0.10561 | 54.6486 | 50.9877 | 113.2936 | 77.009 | 95.21% | 4010.5098 | 97.83% | 98.38% | 84.99% |  |  | 97.98% | 0.93432
2020-05-27 | 162.8656 | 138.7872 | 138.7872 | 124.1119 | 108.0771 | 13.6805 | 13.6805 | 3444.5478 | 1128.8119 | 320.3545 | 609.0558 | 78.3261 | 21.9313 | 66.8382 | 271.5303 | 9389.1661 | 335.6624 |  |  | 26.7828 | 0.9344 | 59.8613 | 4053.6036 | 1995.3814 | 2058.2221 | 929.4102 | 24.0783 | 14.6753 | 16.0679 | 13.1564 | 12.0944 | 6.8647 | 3443.3679 | 7544.32 | 11369.7014 | 2415.5382 | 4968.5072 | 9196.9671 | 0.098207 | 0.12118 | 0.111 | 23.2451 | 12.9244 | 15.0533 | 18.4576 | 78.3003 | 376.608 | 125.1779 | 93.2608 | 57.7869 | 99.09% | 98.65% | 97.05% | 99.24% | 98.42% | 95.91% | 122.1914 | 99.0292 | 108.1071 |  |  |  | 31.22 | 28.7 | 16.29 | 2435.1599 | 1377.6 | 390.96 | 4203.72 | 94.3293 | 21 | 64 | 260 | 75 | 95.55% | 0.1076 | 0.10692 | 54.8215 | 51.2228 | 111.9357 | 71.4522 | 95.55% | 3882.8666 | 97.98% | 98.44% | 84.97% |  |  | 98.13% | 0.9344
2020-05-26 | 160.0683 | 135.7127 | 135.7127 | 120.6694 | 104.1781 | 13.5531 | 13.5531 | 3456.0842 | 1190.0126 | 126.3972 | 610.0707 | 78.2712 | 24.7468 | 90.0068 | 492.8942 | 8563.1954 | 330.7025 |  |  | 26.7426 | 0.93582 | 64.3386 | 4066.1549 | 2139.6744 | 1926.4805 | 736.4679 | 24.3556 | 15.0433 | 16.3922 | 14.1077 | 12.7501 | 2.7085 | 3394.7034 | 8734.5572 | 10442.1021 | 2293.544 | 5247.8056 | 9537.5675 | 0.10734 | 0.13429 | 0.047247 | 24.2178 | 15.7439 | 18.7548 | 23.557 | 105.403 | 260.4952 | 122.9935 | 88.849 | 53.6473 | 98.92% | 98.28% | 94.83% | 98.97% | 97.99% | 97.27% | 111.7924 | 89.3563 | 253.9832 |  |  |  | 32.4392 | 29.3175 | 6.2279 | 2530.2549 | 1407.24 | 149.47 | 4086.9649 | 90.6589 | 20.2083 | 73.5 | 402.5 | 63.9167 | 95.17% | 0.10635 | 0.11442 | 55.7911 | 58.7165 | 110.8567 | 77.9141 | 95.17% | 3575.6982 | 97.81% | 98.39% | 85% |  |  | 97.96% | 0.93582
2020-05-25 | 161.1167 | 136.5338 | 136.5338 | 121.268 | 104.5746 | 13.4945 | 13.4945 | 3481.1514 | 1214.4174 | 73.7384 | 613.9755 | 93.2962 | 30.5889 | 116.2379 | 672.956 | 8843.903 | 334.5698 |  |  | 26.6315 | 0.93977 | 74.0747 | 4095.127 | 2192.9956 | 1902.1314 | 687.7139 | 24.5829 | 15.2658 | 16.6333 | 14.4593 | 13.0116 | 1.5801 | 3460.1133 | 9364.9824 | 10408.8935 | 2314.552 | 5463.9297 | 9868.5575 | 0.10966 | 0.13791 | 0.027782 | 24.4155 | 16.658 | 20.0226 | 29.6977 | 133.9802 | 201.372 | 123.9109 | 88.668 | 53.4488 | 98.68% | 97.87% | 93.18% | 98.72% | 97.55% | 97.96% | 109.4267 | 87.0155 | 431.9289 |  |  |  | 32.76 | 29.48 | 3.58 | 2555.2799 | 1415.04 | 85.92 | 4056.2398 | 91.0232 | 20 | 76 | 440 | 61 | 94.25% | 0.1056 | 0.11778 | 56.482 | 61.0961 | 111.7563 | 94.0031 | 94.25% | 3573.2388 | 97.39% | 98.22% | 85.01% |  |  | 97.54% | 0.93977
2020-05-24 | 184.093 | 161.0797 | 161.0797 | 149.6961 | 137.1956 | 13.8128 | 13.8128 | 3431.6127 | 1198.9025 | 82.1808 | 606.3401 | 54.1348 | 16.9569 | 61.2143 | 257.066 | 8771.9103 | 377.7104 |  |  | 26.5104 | 0.94409 | 38.1692 | 4037.9528 | 2150.5293 | 1887.4234 | 688.5209 | 23.0134 | 11.3835 | 12.5199 | 14.1793 | 12.8454 | 1.761 | 3516.7738 | 9533.8448 | 10791.1812 | 2354.6185 | 5557.1863 | 10136.5662 | 0.091012 | 0.10629 | 0.020721 | 23.2738 | 12.5223 | 15.1905 | 15.9423 | 68.8025 | 83.8473 | 147.0853 | 114.0953 | 80.2356 | 99.28% | 98.9% | 97.46% | 99.32% | 98.76% | 99.17% | 131.8509 | 112.8989 | 579.1252 |  |  |  | 32.038 | 29.024 | 3.979 | 2498.964 | 1393.152 | 95.496 | 3987.612 | 123.3801 | 20 | 72.2 | 303.2 | 63.85 | 96.72% | 0.084654 | 0.094666 | 46.9168 | 50.9866 | 136.4254 | 52.7375 | 96.72% | 3659.863 | 98.52% | 99.12% | 84.98% |  |  | 98.62% | 0.94409
2020-05-23 | 186.9059 | 163.9563 | 163.9563 | 152.6616 | 140.1571 | 13.9757 | 13.9757 | 3436.3956 | 1184.1363 | 92.6422 | 607.1148 | 58.0659 | 18.1456 | 65.3241 | 268.5546 | 9317.4992 | 384.6143 |  |  | 26.3074 | 0.95139 | 41.1535 | 4043.5104 | 2159.617 | 1883.8933 | 699.757 | 22.9496 | 11.2947 | 12.5575 | 14.2392 | 12.6872 | 1.9852 | 3716.2212 | 9894.3086 | 11363.1437 | 2483.7597 | 5828.108 | 10594.8629 | 0.090842 | 0.10449 | 0.023374 | 23.1974 | 12.3691 | 15.0265 | 16.3667 | 69.681 | 95.2041 | 149.1273 | 115.5194 | 80.8021 | 99.27% | 98.88% | 97.47% | 99.34% | 98.8% | 99.1% | 132.0977 | 114.8456 | 513.3874 |  |  |  | 32.875 | 29.2917 | 4.5833 | 2564.25 | 1406 | 110 | 4080.25 | 126.1399 | 20 | 72 | 296 | 64 | 96.66% | 0.084414 | 0.093725 | 46.8018 | 50.593 | 137.9219 | 54.1965 | 96.66% | 3854.846 | 98.49% | 99.13% | 84.99% |  |  | 98.58% | 0.95139
2020-05-22 | 187.8447 | 164.7773 | 164.7773 | 153.507 | 140.9107 | 14.0922 | 14.0922 | 3449.9237 | 1151.574 | 115.1574 | 609.1231 | 60.3848 | 18.8703 | 67.933 | 279.2799 | 9609.7653 | 389.3633 |  |  | 26.4752 | 0.94535 | 43.9396 | 4059.0468 | 2183.1924 | 1875.8545 | 724.2805 | 23.0674 | 11.2703 | 12.5437 | 14.3947 | 12.3383 | 2.4677 | 3845.9185 | 9852.7487 | 11662.6552 | 2558.8959 | 5934.4547 | 10706.8793 | 0.091012 | 0.1008 | 0.028808 | 23.2723 | 12.2252 | 14.5642 | 16.595 | 68.7691 | 121.0077 | 149.5186 | 115.7173 | 80.9786 | 99.26% | 98.86% | 97.39% | 99.35% | 98.84% | 98.87% | 131.8508 | 119.0509 | 416.5572 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 126.7642 | 20 | 72 | 296 | 64 | 96.62% | 0.084191 | 0.092202 | 46.8814 | 50.0617 | 138.0985 | 54.7636 | 96.62% | 3957.6243 | 98.47% | 99.11% | 84.99% |  |  | 98.57% | 0.94535
2020-05-21 | 189.3158 | 166.0873 | 166.0873 | 154.7302 | 142.0259 | 14.1378 | 14.1378 | 3466.3754 | 1157.0655 | 115.7066 | 612.3541 | 62.2154 | 19.4423 | 69.9924 | 287.7463 | 9817.4734 | 394.8702 |  |  | 26.5796 | 0.94162 | 45.2717 | 4078.7295 | 2193.6033 | 1885.1261 | 728.0606 | 23.2285 | 11.3571 | 12.6973 | 14.4633 | 12.3971 | 2.4794 | 3916.357 | 10029.1664 | 11869.8435 | 2605.9958 | 6042.1171 | 10897.8604 | 0.090412 | 0.10028 | 0.028756 | 23.2644 | 12.2272 | 14.6271 | 16.8025 | 69.6472 | 122.5895 | 150.631 | 116.4103 | 81.1897 | 99.25% | 98.84% | 97.36% | 99.36% | 98.85% | 98.88% | 132.7253 | 119.6679 | 417.3083 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 127.8678 | 20 | 72 | 296 | 64 | 96.58% | 0.083704 | 0.091647 | 47.2829 | 50.1187 | 138.9853 | 55.4584 | 96.58% | 4029.7425 | 98.46% | 99.12% | 84.99% |  |  | 98.55% | 0.94162
2020-05-20 | 189.4466 | 166.3311 | 166.3311 | 155.0585 | 142.2859 | 14.1333 | 14.1333 | 3458.7201 | 1154.5102 | 115.451 | 609.8156 | 61.051 | 19.0784 | 68.6823 | 282.3607 | 9794.3338 | 393.3917 |  |  | 26.3059 | 0.95144 | 44.4243 | 4068.5357 | 2188.7589 | 1879.7768 | 725.2666 | 23.1155 | 11.2725 | 12.6641 | 14.4314 | 12.3698 | 2.474 | 3910.3418 | 10025.6589 | 11870.2719 | 2601.3564 | 6035.8655 | 10896.0921 | 0.091025 | 0.10083 | 0.028892 | 23.2421 | 12.1931 | 14.6763 | 16.6529 | 68.9754 | 121.3011 | 150.8441 | 116.7255 | 81.4702 | 99.27% | 98.86% | 97.41% | 99.36% | 98.86% | 98.89% | 131.832 | 119.0159 | 415.3443 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 128.1663 | 20 | 72 | 296 | 64 | 96.64% | 0.08422 | 0.092223 | 47.0521 | 50.1114 | 139.2121 | 54.936 | 96.64% | 4024.6608 | 98.48% | 99.12% | 85.01% |  |  | 98.56% | 0.95144
2020-05-19 | 190.2653 | 166.8236 | 166.8236 | 155.1972 | 142.3825 | 14.2249 | 14.2249 | 3471.3555 | 1158.7278 | 115.8728 | 612.9374 | 58.8758 | 18.3987 | 66.2353 | 272.3007 | 9554.101 | 397.6265 |  |  | 26.1745 | 0.9562 | 42.8416 | 4084.2929 | 2196.7549 | 1887.538 | 728.8102 | 23.4418 | 11.6264 | 12.7574 | 14.4841 | 12.4149 | 2.483 | 3826.7181 | 9805.4715 | 11607.6704 | 2545.9695 | 5905.3143 | 10655.9395 | 0.091307 | 0.10095 | 0.028727 | 23.431 | 12.4944 | 14.6743 | 16.5512 | 68.5781 | 120.6531 | 151.6817 | 117.5901 | 82.6467 | 99.28% | 98.88% | 97.44% | 99.35% | 98.84% | 98.87% | 131.4242 | 118.8666 | 417.7195 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 128.2119 | 20 | 72 | 296 | 64 | 96.69% | 0.084381 | 0.092438 | 47.8255 | 50.5997 | 140.2728 | 54.6139 | 96.69% | 3938.0168 | 98.5% | 99.11% | 84.99% |  |  | 98.57% | 0.9562
2020-05-18 | 186.1644 | 162.702 | 162.702 | 150.9036 | 138.1202 | 14.0719 | 14.0719 | 3470.7573 | 1158.5282 | 115.8528 | 613.5341 | 54.0021 | 16.8757 | 60.7524 | 249.7598 | 8594.3987 | 388.4803 |  |  | 26.251 | 0.95342 | 39.2952 | 4084.2914 | 2196.3763 | 1887.9151 | 729.3869 | 23.4624 | 11.7984 | 12.8596 | 14.4816 | 12.4128 | 2.4826 | 3489.6175 | 8935.8857 | 10576.0751 | 2321.9931 | 5383.6282 | 9709.9568 | 0.092767 | 0.10192 | 0.028469 | 23.4494 | 12.6723 | 14.7726 | 16.5943 | 68.7844 | 121.0736 | 148.8357 | 116.1165 | 83.139 | 99.27% | 98.87% | 97.43% | 99.29% | 98.72% | 98.75% | 129.3561 | 117.739 | 421.5038 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 124.0001 | 20 | 72 | 296 | 64 | 96.67% | 0.085409 | 0.093676 | 48.1204 | 50.8943 | 138.3511 | 54.7715 | 96.67% | 3590.5655 | 98.5% | 99.02% | 84.98% |  |  | 98.57% | 0.95342
2020-05-17 | 185.7471 | 162.4626 | 162.4626 | 150.9247 | 138.1946 | 13.9348 | 13.9348 | 3459.5138 | 1154.7751 | 115.4775 | 610.6146 | 56.7711 | 17.741 | 63.8675 | 262.5662 | 8995.7877 | 384.6693 |  |  | 26.4822 | 0.9451 | 41.31 | 4070.1284 | 2189.2612 | 1880.8672 | 726.0921 | 23.2845 | 11.5379 | 12.6932 | 14.4347 | 12.3726 | 2.4745 | 3626.6278 | 9292.8335 | 11000.6094 | 2412.8893 | 5596.5561 | 10098.7479 | 0.092056 | 0.1016 | 0.028715 | 23.3962 | 12.4663 | 14.6833 | 16.5875 | 68.7296 | 120.9201 | 148.1943 | 115.0954 | 81.444 | 99.26% | 98.86% | 97.4% | 99.31% | 98.77% | 98.8% | 130.3552 | 118.1141 | 417.9001 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 124.2411 | 20 | 72 | 296 | 64 | 96.63% | 0.084975 | 0.093126 | 47.5156 | 50.5457 | 137.3639 | 54.7342 | 96.63% | 3732.1392 | 98.48% | 99.06% | 85% |  |  | 98.57% | 0.9451
2020-05-16 | 188.0864 | 164.7758 | 164.7758 | 153.219 | 140.3009 | 14.2316 | 14.2316 | 3467.8964 | 1157.5732 | 115.7573 | 612.8821 | 59.6915 | 18.6536 | 67.153 | 276.0733 | 9478.0388 | 391.8737 |  |  | 26.5926 | 0.94115 | 43.4351 | 4080.7785 | 2194.5659 | 1886.2127 | 728.6394 | 23.3106 | 11.5568 | 12.8326 | 14.4697 | 12.4026 | 2.4805 | 3794.5431 | 9716.1646 | 11499.1497 | 2524.9635 | 5853.9148 | 10557.6376 | 0.090989 | 0.10077 | 0.028779 | 23.3282 | 12.4303 | 14.7646 | 16.6373 | 68.9663 | 121.3999 | 149.668 | 115.832 | 81.1206 | 99.26% | 98.85% | 97.39% | 99.34% | 98.82% | 98.85% | 131.884 | 119.08 | 416.976 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 126.015 | 20 | 72 | 296 | 64 | 96.62% | 0.084166 | 0.092178 | 47.7 | 50.5231 | 138.3184 | 54.9154 | 96.62% | 3904.2855 | 98.47% | 99.1% | 84.98% |  |  | 98.56% | 0.94115
2020-05-15 | 188.4293 | 165.322 | 165.322 | 153.8327 | 140.9678 | 14.1899 | 14.1899 | 3457.7509 | 1154.1867 | 115.4187 | 610.2487 | 62.7691 | 19.6153 | 70.6152 | 290.307 | 9814.9161 | 390.6501 |  |  | 26.3819 | 0.9487 | 45.6746 | 4067.9996 | 2188.1455 | 1879.8541 | 725.6674 | 23.1073 | 11.4893 | 12.7671 | 14.4273 | 12.3663 | 2.4733 | 3924.5685 | 10054.3485 | 11901.0588 | 2611.2751 | 6055.8435 | 10925.8534 | 0.091414 | 0.10161 | 0.029318 | 23.2364 | 12.4241 | 14.7818 | 17.0026 | 70.4594 | 123.9823 | 149.7274 | 115.4613 | 80.0326 | 99.25% | 98.83% | 97.34% | 99.35% | 98.84% | 98.87% | 131.2707 | 118.0999 | 409.3078 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 126.8427 | 20 | 72 | 296 | 64 | 96.56% | 0.084741 | 0.092744 | 47.3637 | 50.4424 | 137.9714 | 56.1093 | 96.56% | 4038.5995 | 98.45% | 99.11% | 85% |  |  | 98.53% | 0.9487
2020-05-14 | 188.2555 | 165.197 | 165.197 | 153.7802 | 140.6672 | 14.1104 | 14.1104 | 3453.76 | 1152.8545 | 115.2855 | 609.3716 | 64.0116 | 20.0036 | 72.013 | 296.0536 | 9938.051 | 390.0287 |  |  | 26.4988 | 0.9445 | 46.5787 | 4063.1317 | 2185.62 | 1877.5116 | 724.6571 | 23.0585 | 11.4168 | 12.864 | 14.4107 | 12.352 | 2.4704 | 3956.0583 | 10135.1728 | 11996.6104 | 2632.2549 | 6104.4725 | 11013.6309 | 0.09101 | 0.10126 | 0.02934 | 23.2296 | 12.3696 | 14.9256 | 17.1051 | 70.8844 | 124.7296 | 149.5545 | 115.2159 | 79.5254 | 99.24% | 98.82% | 97.31% | 99.35% | 98.84% | 98.87% | 131.8541 | 118.5095 | 408.9938 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 126.6056 | 20 | 72 | 296 | 64 | 96.52% | 0.084422 | 0.092372 | 47.3393 | 50.5248 | 137.6847 | 56.4476 | 96.52% | 4071.0383 | 98.43% | 99.11% | 85% |  |  | 98.52% | 0.9445
2020-05-13 | 185.0579 | 162.3504 | 162.3504 | 150.8407 | 138.3291 | 13.4622 | 13.4622 | 3418.7494 | 1141.1681 | 114.1168 | 603.6214 | 64.9848 | 20.3077 | 73.1078 | 300.5545 | 10101.0977 | 376.6548 |  |  | 26.2925 | 0.95192 | 47.2868 | 4022.3708 | 2163.4645 | 1858.9063 | 717.7382 | 22.7076 | 11.5097 | 12.7562 | 14.2646 | 12.2268 | 2.4454 | 3958.5466 | 10136.2014 | 11995.6661 | 2634.2182 | 6106.9506 | 11013.7842 | 0.092264 | 0.10303 | 0.030014 | 23.2233 | 12.6559 | 15.0139 | 17.3112 | 71.7631 | 126.3253 | 147.1724 | 112.9642 | 77.5566 | 99.23% | 98.8% | 97.27% | 99.34% | 98.82% | 98.85% | 130.0609 | 116.4683 | 399.8119 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 124.8612 | 20 | 72 | 296 | 64 | 96.47% | 0.08575 | 0.093781 | 46.9734 | 50.8931 | 135.2115 | 57.1414 | 96.47% | 4073.113 | 98.4% | 99.1% | 84.99% |  |  | 98.5% | 0.95192
2020-05-12 | 186.901 | 163.5674 | 163.5674 | 151.6498 | 138.2262 | 12.9318 | 12.9318 | 3473.5026 | 1159.4445 | 115.9445 | 613.1041 | 62.6238 | 19.5699 | 70.4518 | 289.635 | 9751.1278 | 383.0289 |  |  | 26.0883 | 0.95933 | 45.5688 | 4086.6067 | 2198.1136 | 1888.4931 | 729.0485 | 23.3336 | 11.9176 | 13.2682 | 14.4931 | 12.4226 | 2.4845 | 3825.2985 | 9796.8304 | 11594.7413 | 2545.4501 | 5901.8495 | 10645.3444 | 0.092894 | 0.10316 | 0.029709 | 23.3037 | 12.7986 | 15.255 | 17.6772 | 73.2713 | 128.9627 | 149.673 | 115.5198 | 80.2276 | 99.23% | 98.81% | 97.28% | 99.31% | 98.76% | 98.79% | 129.1797 | 116.3199 | 403.9166 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 125.3958 | 20 | 72 | 296 | 64 | 96.48% | 0.086071 | 0.094213 | 48.5194 | 51.3574 | 138.0273 | 58.3445 | 96.48% | 3936.1779 | 98.41% | 99.05% | 85% |  |  | 98.47% | 0.95933
2020-05-11 | 179.8089 | 157.6207 | 157.6207 | 146.0771 | 133.5831 | 12.4962 | 12.4962 | 3346.5194 | 1117.0579 | 111.7058 | 590.2912 | 59.8343 | 18.6982 | 67.3136 | 276.7337 | 9015.2708 | 352.1145 |  |  | 25.8491 | 0.9681 | 43.539 | 3936.8106 | 2117.7557 | 1819.055 | 701.997 | 22.1882 | 11.5437 | 12.7733 | 13.9632 | 11.9685 | 2.3937 | 3670.0482 | 9402.9261 | 11129.9525 | 2441.9485 | 5663.2646 | 10217.9504 | 0.093807 | 0.10404 | 0.029852 | 23.4378 | 13.1155 | 15.5442 | 17.117 | 70.9322 | 124.8096 | 144.1024 | 111.373 | 77.6279 | 99.23% | 98.81% | 97.29% | 99.3% | 98.75% | 98.78% | 127.922 | 115.3455 | 401.9837 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 120.8783 | 20 | 72 | 296 | 64 | 96.49% | 0.086847 | 0.095086 | 46.5052 | 52.0975 | 132.8395 | 56.4861 | 96.49% | 3776.7745 | 98.42% | 99.04% | 85.01% |  |  | 98.52% | 0.9681
2020-05-10
2020-05-09
2020-05-08
2020-05-07
2020-05-06
2020-05-05
2020-05-04
2020-05-03
2020-05-02
2020-05-01
2020-04-30
2020-04-29
2020-04-28
2020-04-27
2020-04-26
2020-04-25
2020-04-24 | 192.8591 | 169.6119 | 169.6119 | 158.0164 | 145.2492 | 12.8283 | 12.8283 | 3470.336 | 1190.369 | 95.4861 | 612.243 | 58.2604 | 18.0078 | 62.4975 | 274.3534 | 10294.299 | 394.1419 |  |  | 25.7621 | 0.97132 | 40.3216 | 4082.579 | 2184.481 | 1898.098 | 707.7291 | 23.2472 | 11.5956 | 12.7316 | 14.4032 | 12.754 | 2.0461 | 3992.2262 | 10601.856 | 12212.5442 | 2664.4668 | 6254.2067 | 11369.2576 | 0.090157 | 0.10321 | 0.02385 | 23.185 | 12.5368 | 15.0086 | 15.636 | 63.7593 | 95.3744 | 155.175 | 120.0273 | 83.33 | 99.32% | 99% | 97.59% | 99.41% | 98.98% | 99.16% | 133.1017 | 116.2667 | 503.1395 |  |  |  | 32.75 | 29 | 4.6525 | 2554.5 | 1392 | 111.66 | 4058.16 | 132.2995 | 17 | 59 | 259 | 55 | 96.88% | 0.083725 | 0.09281 | 47.5744 | 50.7304 | 143.1505 | 52.2632 | 96.88% | 4135.3045 | 98.59% | 99.23% | 85% |  |  | 98.63% | 0.97132
2020-04-23 | 189.9484 | 167.3109 | 167.3109 | 155.9137 | 143.2936 | 12.7344 | 12.7344 | 3427.8246 | 1191.4294 | 100.039 | 605.2336 | 59.279 | 18.3226 | 63.5902 | 279.15 | 10239.9467 | 383.3981 |  |  | 25.4941 | 0.98129 | 41.6686 | 4033.0582 | 2136.3562 | 1896.702 | 705.2726 | 22.6376 | 11.3972 | 12.6115 | 14.0859 | 12.7653 | 2.1437 | 3919.5311 | 10433.44 | 12111.8412 | 2632.9824 | 6146.4191 | 11230.9444 | 0.090447 | 0.10574 | 0.025619 | 22.8684 | 12.3497 | 15.0284 | 15.9066 | 66.7489 | 103.978 | 152.8219 | 118.4637 | 82.1102 | 99.3% | 98.97% | 97.51% | 99.4% | 98.91% | 99.07% | 132.6738 | 113.4846 | 468.401 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 130.4917 | 17 | 59 | 259 | 55 | 96.8% | 0.084969 | 0.093871 | 46.6463 | 50.2465 | 140.7418 | 53.4554 | 96.8% | 4105.0949 | 98.56% | 99.19% | 84.99% |  |  | 98.6% | 0.98129
2020-04-22 | 191.6414 | 168.9321 | 168.9321 | 157.5098 | 144.7333 | 13.2285 | 13.2285 | 3429.2699 | 1191.9318 | 100.0812 | 605.4182 | 58.0056 | 17.929 | 62.2242 | 273.1535 | 10164.5394 | 388.6482 |  |  | 25.2051 | 0.99218 | 40.7735 | 4034.6881 | 2137.257 | 1897.4311 | 705.4994 | 22.7093 | 11.4222 | 12.5652 | 14.0918 | 12.7707 | 2.1446 | 3900.4406 | 10385.0563 | 12056.6463 | 2620.0007 | 6117.0839 | 11179.3019 | 0.090762 | 0.10584 | 0.025525 | 22.9272 | 12.37 | 14.9662 | 15.8224 | 66.3848 | 103.3927 | 154.0478 | 119.7181 | 83.3623 | 99.32% | 98.98% | 97.56% | 99.4% | 98.91% | 99.08% | 132.214 | 113.3793 | 470.1242 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 131.4742 | 17 | 59 | 259 | 55 | 96.85% | 0.085149 | 0.094099 | 46.6968 | 50.2635 | 142.0507 | 53.1664 | 96.85% | 4085.3008 | 98.58% | 99.19% | 84.99% |  |  | 98.61% | 0.99218
2020-04-21 | 191.8102 | 169.1394 | 169.1394 | 157.6186 | 145.0007 | 13.5298 | 13.5298 | 3425.2768 | 1190.5439 | 99.9646 | 603.8265 | 56.7728 | 17.548 | 60.9018 | 267.3485 | 9947.6503 | 391.1122 |  |  | 24.9243 | 1.0029 | 39.907 | 4029.1033 | 2134.7683 | 1894.335 | 703.7912 | 22.6708 | 11.5208 | 12.633 | 14.0754 | 12.7558 | 2.1421 | 3840.2798 | 10233.5334 | 11883.4542 | 2579.1896 | 6024.8727 | 11017.4202 | 0.091583 | 0.10658 | 0.025566 | 22.9386 | 12.5114 | 15.1039 | 15.8825 | 66.6034 | 103.6705 | 154.1369 | 120.0294 | 84.0295 | 99.32% | 98.99% | 97.57% | 99.38% | 98.89% | 99.06% | 131.0293 | 112.5905 | 469.3697 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 131.363 | 17 | 59 | 259 | 55 | 96.87% | 0.085819 | 0.094869 | 46.8246 | 50.5539 | 142.2632 | 53.3497 | 96.87% | 4023.0908 | 98.59% | 99.18% | 85.01% |  |  | 98.6% | 1.0029
2020-04-20 | 193.9636 | 170.6431 | 170.6431 | 158.726 | 145.7541 | 14.0619 | 14.0619 | 3469.0711 | 1205.7657 | 101.2427 | 611.7476 | 53.6247 | 16.5749 | 57.5247 | 252.5236 | 9488.9302 | 405.0556 |  |  | 24.6117 | 1.015 | 37.6941 | 4080.8187 | 2162.0627 | 1918.7561 | 712.9904 | 23.3205 | 11.9172 | 12.8298 | 14.2554 | 12.9189 | 2.1695 | 3678.3444 | 9801.6534 | 11382.0111 | 2470.4089 | 5770.7303 | 10552.4888 | 0.092767 | 0.10743 | 0.025405 | 23.1482 | 12.6946 | 15.0428 | 16.054 | 67.3227 | 104.792 | 155.9723 | 122.0566 | 86.6783 | 99.33% | 99% | 97.61% | 99.35% | 98.83% | 99.01% | 129.3558 | 111.6996 | 472.3566 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 131.755 | 17 | 59 | 259 | 55 | 96.92% | 0.086682 | 0.095898 | 48.0674 | 50.8857 | 144.6015 | 53.9258 | 96.92% | 3853.3919 | 98.61% | 99.13% | 85.01% |  |  | 98.59% | 1.015
2020-04-19 | 196.3055 | 172.9817 | 172.9817 | 161.0482 | 148.1204 | 14.0692 | 14.0692 | 3473.3328 | 1207.247 | 101.3671 | 612.6509 | 56.2052 | 17.3725 | 60.2929 | 264.6756 | 10063.3831 | 410.7025 |  |  | 24.6432 | 1.0138 | 39.508 | 4085.9837 | 2164.7187 | 1921.265 | 714.018 | 23.3238 | 11.9335 | 12.8986 | 14.2729 | 12.9348 | 2.1722 | 3875.9027 | 10327.2574 | 11992.1777 | 2603.1123 | 6080.4628 | 11118.2731 | 0.091785 | 0.10674 | 0.025532 | 23.1072 | 12.6864 | 15.0905 | 15.9691 | 66.9694 | 104.2478 | 157.6457 | 122.8449 | 86.2471 | 99.33% | 99.01% | 97.62% | 99.39% | 98.9% | 99.06% | 130.7409 | 112.4187 | 469.997 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 134.1356 | 17 | 59 | 259 | 55 | 96.93% | 0.085971 | 0.095051 | 48.1559 | 50.8842 | 145.665 | 53.6422 | 96.93% | 4060.2655 | 98.62% | 99.18% | 85.01% |  |  | 98.6% | 1.0138
2020-04-18 | 197.6884 | 174.4981 | 174.4981 | 162.6885 | 149.7533 | 14.1009 | 14.1009 | 3474.4936 | 1207.6504 | 101.401 | 612.55 | 58.5587 | 18.0999 | 62.8175 | 275.7581 | 10431.7553 | 412.8843 |  |  | 24.7515 | 1.0096 | 41.1623 | 4087.0436 | 2165.4422 | 1921.6014 | 713.9509 | 23.1903 | 11.8096 | 12.9526 | 14.2776 | 12.9391 | 2.1729 | 4009.2015 | 10684.5234 | 12407.5815 | 2692.5664 | 6290.0975 | 11503.1483 | 0.090873 | 0.1059 | 0.025513 | 22.9669 | 12.5528 | 15.1566 | 16.0236 | 67.1907 | 104.5782 | 158.62 | 123.356 | 85.983 | 99.33% | 99% | 97.6% | 99.4% | 98.93% | 99.09% | 132.0529 | 113.3189 | 470.3529 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 135.6164 | 17 | 59 | 259 | 55 | 96.91% | 0.085223 | 0.094187 | 47.9525 | 50.6763 | 146.2207 | 53.8212 | 96.91% | 4200.1132 | 98.61% | 99.2% | 85.01% |  |  | 98.59% | 1.0096
2020-04-17 | 195.3873 | 172.6251 | 172.6251 | 161.1182 | 148.3577 | 14.1174 | 14.1174 | 3424.1896 | 1190.166 | 99.9329 | 605.5045 | 59.5352 | 18.4018 | 63.865 | 280.3565 | 10518.4687 | 402.3416 |  |  | 24.5842 | 1.0161 | 41.8487 | 4029.6941 | 2134.0907 | 1895.6034 | 705.4374 | 22.7622 | 11.5069 | 12.5496 | 14.0709 | 12.7518 | 2.1414 | 4019.4658 | 10693.0864 | 12411.6109 | 2700.3336 | 6301.5564 | 11509.6935 | 0.091367 | 0.10658 | 0.025757 | 23.0203 | 12.4753 | 14.9471 | 16.1119 | 67.6326 | 105.3977 | 156.4792 | 121.5658 | 84.4739 | 99.32% | 98.99% | 97.56% | 99.4% | 98.93% | 99.08% | 131.3384 | 112.5897 | 465.8852 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 134.2456 | 17 | 59 | 259 | 55 | 96.87% | 0.085738 | 0.09474 | 46.8187 | 50.4427 | 144.1298 | 54.1576 | 96.87% | 4209.1279 | 98.59% | 99.2% | 84.97% |  |  | 98.58% | 1.0161
2020-04-16 | 196.894 | 173.7381 | 173.7381 | 162.0143 | 149.1513 | 14.1042 | 14.1042 | 3465.755 | 1204.6131 | 101.146 | 611.9585 | 58.7155 | 18.1484 | 62.9857 | 276.4966 | 10499.484 | 411.8439 |  |  | 24.7106 | 1.0112 | 41.2725 | 4077.7135 | 2159.9959 | 1917.7176 | 713.1045 | 23.1558 | 11.7238 | 12.8607 | 14.2417 | 12.9066 | 2.1674 | 3968.8075 | 10566.7245 | 12267.5178 | 2665.9246 | 6224.2149 | 11374.8467 | 0.091159 | 0.10613 | 0.025488 | 23.0087 | 12.4953 | 15.0735 | 16.2117 | 68.0194 | 105.9407 | 157.9729 | 122.9659 | 85.9868 | 99.32% | 98.99% | 97.57% | 99.39% | 98.91% | 99.07% | 131.6387 | 113.0674 | 470.8189 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 134.988 | 17 | 59 | 259 | 55 | 96.87% | 0.085443 | 0.094446 | 47.7404 | 50.5775 | 145.7351 | 54.4753 | 96.87% | 4156.8654 | 98.59% | 99.19% | 84.99% |  |  | 98.57% | 1.0112
2020-04-15 | 192.6888 | 170.2781 | 170.2781 | 158.8641 | 146.0619 | 13.9739 | 13.9739 | 3402.4305 | 1182.603 | 99.2979 | 600.0665 | 57.4182 | 17.7474 | 61.594 | 270.3873 | 10219.2793 | 392.887 |  |  | 24.8141 | 1.0071 | 40.3606 | 4002.4969 | 2120.5296 | 1881.9674 | 699.3643 | 22.4107 | 11.414 | 12.4469 | 13.9815 | 12.6707 | 2.1278 | 3878.8548 | 10333.7222 | 11998.984 | 2605.216 | 6084.7479 | 11124.9163 | 0.091099 | 0.10592 | 0.025447 | 22.9011 | 12.5166 | 15.0222 | 15.8634 | 66.5331 | 103.5797 | 154.5721 | 120.4814 | 84.2164 | 99.32% | 98.99% | 97.57% | 99.39% | 98.91% | 99.07% | 131.7243 | 113.2939 | 471.5768 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 132.1793 | 17 | 59 | 259 | 55 | 96.87% | 0.085337 | 0.094334 | 46.2715 | 50.4399 | 142.5929 | 53.291 | 96.87% | 4063.2599 | 98.59% | 99.18% | 85.01% |  |  | 98.61% | 1.0071
2020-04-14 | 197.2434 | 173.9003 | 173.9003 | 161.8802 | 148.9049 | 14.1618 | 14.1618 | 3471.8196 | 1206.721 | 101.323 | 612.5453 | 54.1391 | 16.7339 | 58.0765 | 254.9459 | 9903.1947 | 411.8991 |  |  | 24.4411 | 1.0217 | 38.0557 | 4084.3649 | 2163.7756 | 1920.5893 | 713.8683 | 23.3431 | 12.0201 | 12.9925 | 14.2667 | 12.9292 | 2.1712 | 3782.1624 | 10077.347 | 11702.0997 | 2540.1254 | 5933.3694 | 10849.276 | 0.091791 | 0.10623 | 0.025133 | 23.1396 | 12.7845 | 15.2047 | 15.8793 | 66.5927 | 103.6617 | 158.7931 | 124.352 | 88.2591 | 99.34% | 99.02% | 97.65% | 99.37% | 98.88% | 99.04% | 130.7316 | 112.9675 | 477.4515 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 134.7544 | 17 | 59 | 259 | 55 | 96.97% | 0.085745 | 0.094863 | 48.3557 | 51.1288 | 147.056 | 53.3406 | 96.97% | 3962.033 | 98.63% | 99.16% | 85% |  |  | 98.6% | 1.0217
2020-04-13 | 196.6041 | 173.1064 | 173.1064 | 160.9471 | 147.9504 | 14.1467 | 14.1467 | 3471.3957 | 1206.5737 | 101.3106 | 612.6478 | 50.6939 | 15.669 | 54.3807 | 238.7221 | 9301.5697 | 410.9817 |  |  | 23.9645 | 1.0406 | 35.6339 | 4084.0434 | 2163.5114 | 1920.532 | 713.9584 | 23.4977 | 12.1593 | 13.0159 | 14.2649 | 12.9276 | 2.1709 | 3573.1602 | 9519.8189 | 11054.5887 | 2399.7642 | 5605.3299 | 10248.9986 | 0.093482 | 0.10751 | 0.025031 | 23.295 | 12.9324 | 15.2288 | 16.028 | 67.2181 | 104.6398 | 158.7881 | 125.1253 | 90.2507 | 99.35% | 99.03% | 97.67% | 99.33% | 98.8% | 98.98% | 128.3666 | 111.6172 | 479.4081 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 133.759 | 17 | 59 | 259 | 55 | 97% | 0.087019 | 0.09636 | 48.6729 | 51.4562 | 147.6771 | 53.8411 | 97% | 3743.0169 | 98.65% | 99.11% | 85% |  |  | 98.59% | 1.0406
2020-04-12 | 197.411 | 174.061 | 174.061 | 161.8442 | 148.7765 | 14.2207 | 14.2207 | 3472.6845 | 1207.0217 | 101.3482 | 613.5017 | 50.3474 | 15.5619 | 54.009 | 237.0906 | 9458.9808 | 412.3557 |  |  | 23.9499 | 1.0412 | 35.3904 | 4086.1862 | 2164.3147 | 1921.8715 | 714.8499 | 23.35 | 12.2168 | 13.0005 | 14.2702 | 12.9324 | 2.1717 | 3628.3972 | 9663.7396 | 11220.987 | 2436.9483 | 5691.1801 | 10403.6153 | 0.093205 | 0.10725 | 0.025052 | 23.1285 | 12.977 | 15.1808 | 15.6902 | 65.813 | 102.4757 | 159.4083 | 125.546 | 90.257 | 99.36% | 99.05% | 97.72% | 99.36% | 98.84% | 99.01% | 128.7478 | 111.888 | 478.9947 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 134.5565 | 17 | 59 | 259 | 55 | 97.06% | 0.086795 | 0.096098 | 48.5673 | 51.2862 | 148.0924 | 52.7128 | 97.06% | 3800.5434 | 98.68% | 99.14% | 84.99% |  |  | 98.62% | 1.0412
2020-04-11 | 197.9328 | 174.8219 | 174.8219 | 162.7239 | 149.5485 | 14.0298 | 14.0298 | 3446.6709 | 1197.9799 | 100.589 | 608.8388 | 49.6938 | 15.3599 | 53.3078 | 234.0124 | 9444.1007 | 410.1813 |  |  | 23.7133 | 1.0507 | 34.9309 | 4055.5098 | 2148.102 | 1907.4078 | 709.4279 | 23.1109 | 12.0981 | 12.8388 | 14.1633 | 12.8355 | 2.1555 | 3621.5155 | 9646.9926 | 11202.1534 | 2432.2282 | 5680.777 | 10385.8628 | 0.092858 | 0.10652 | 0.024793 | 23.1521 | 12.9977 | 15.1644 | 15.5415 | 65.1825 | 101.4816 | 160.2632 | 126.6057 | 91.3471 | 99.37% | 99.06% | 97.75% | 99.36% | 98.85% | 99.02% | 129.2297 | 112.6507 | 483.9987 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 135.533 | 17 | 59 | 259 | 55 | 97.1% | 0.086341 | 0.095622 | 48.0478 | 51.3141 | 148.9794 | 52.2096 | 97.1% | 3793.4677 | 98.69% | 99.14% | 84.99% |  |  | 98.63% | 1.0507
2020-04-10 | 197.3545 | 174.1509 | 174.1509 | 161.9045 | 149.0577 | 14.0584 | 14.0584 | 3443.0745 | 1196.7299 | 100.484 | 607.1937 | 46.9276 | 14.5049 | 50.3405 | 220.9861 | 8989.6281 | 407.9578 |  |  | 23.3455 | 1.0658 | 32.9865 | 4050.2682 | 2145.8605 | 1904.4076 | 707.6777 | 23.2036 | 12.2463 | 12.8619 | 14.1485 | 12.8221 | 2.1532 | 3446.8763 | 9190.6434 | 10675.0255 | 2314.5292 | 5409.0218 | 9895.8216 | 0.09413 | 0.10745 | 0.024663 | 23.2932 | 13.1929 | 15.2505 | 15.6273 | 65.5041 | 101.9123 | 160.1942 | 127.1759 | 93.0486 | 99.37% | 99.07% | 97.77% | 99.32% | 98.79% | 98.97% | 127.4832 | 111.6769 | 486.5608 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 135.0103 | 17 | 59 | 259 | 55 | 97.12% | 0.087279 | 0.096733 | 48.3119 | 51.7366 | 149.4074 | 52.4765 | 97.12% | 3611.3559 | 98.7% | 99.1% | 85.01% |  |  | 98.63% | 1.0658
2020-04-09 | 196.6914 | 173.3896 | 173.3896 | 161.1821 | 148.0765 | 14.157 | 14.157 | 3465.468 | 1204.5134 | 101.1376 | 612.837 | 50.2881 | 15.5436 | 53.9454 | 236.811 | 9284.3388 | 410.0722 |  |  | 23.6727 | 1.0524 | 35.3487 | 4078.305 | 2159.8171 | 1918.4879 | 713.9746 | 23.3018 | 12.2075 | 12.9824 | 14.2406 | 12.9055 | 2.1672 | 3551.7402 | 9452.7076 | 10973.6236 | 2385.8181 | 5569.2454 | 10175.3752 | 0.094234 | 0.10817 | 0.025124 | 23.1458 | 12.9986 | 15.1861 | 16.146 | 67.756 | 105.5564 | 159.0322 | 125.5524 | 90.7795 | 99.35% | 99.03% | 97.67% | 99.32% | 98.78% | 98.96% | 127.3419 | 110.9337 | 477.6342 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 133.8932 | 17 | 59 | 259 | 55 | 97% | 0.087637 | 0.097062 | 48.4916 | 51.3304 | 147.9411 | 54.2615 | 97% | 3719.6344 | 98.65% | 99.09% | 84.97% |  |  | 98.58% | 1.0524
2020-04-08 | 195.8377 | 172.4144 | 172.4144 | 160.2772 | 147.0608 | 14.1752 | 14.1752 | 3468.1531 | 1205.4466 | 101.2159 | 611.2802 | 50.0218 | 15.4613 | 53.6597 | 235.5572 | 9093.9672 | 408.7614 |  |  | 23.8505 | 1.0452 | 35.1615 | 4079.4332 | 2161.4905 | 1917.9427 | 712.4961 | 23.4234 | 12.1371 | 13.0605 | 14.2516 | 12.9155 | 2.1689 | 3478.5083 | 9272.8867 | 10769.2903 | 2335.9973 | 5458.142 | 9983.805 | 0.094067 | 0.10786 | 0.024979 | 23.2632 | 12.9386 | 15.3299 | 16.3035 | 68.3518 | 106.3628 | 158.3481 | 125.1481 | 90.7525 | 99.34% | 99.02% | 97.64% | 99.3% | 98.75% | 98.93% | 127.5684 | 111.2517 | 480.4077 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 132.9416 | 17 | 59 | 259 | 55 | 96.96% | 0.087428 | 0.096846 | 48.621 | 51.5317 | 147.4889 | 54.7545 | 96.96% | 3644.3764 | 98.63% | 99.07% | 85.02% |  |  | 98.57% | 1.0452
2020-04-07 | 194.3877 | 170.9839 | 170.9839 | 158.6396 | 145.5194 | 14.1101 | 14.1101 | 3471.5538 | 1206.6286 | 101.3152 | 612.7949 | 48.4402 | 14.9724 | 51.9631 | 228.1094 | 8806.5809 | 406.3637 |  |  | 23.8941 | 1.0434 | 34.0498 | 4084.3487 | 2163.61 | 1920.7387 | 714.1101 | 23.4038 | 12.3443 | 13.0236 | 14.2656 | 12.9282 | 2.171 | 3380.2466 | 9004.0324 | 10454.9818 | 2270.3065 | 5302.2518 | 9693.4039 | 0.094628 | 0.10839 | 0.024991 | 23.199 | 13.1264 | 15.2326 | 16.2335 | 68.0888 | 106.011 | 157.2991 | 124.4503 | 90.643 | 99.34% | 99.02% | 97.65% | 99.28% | 98.72% | 98.91% | 126.8125 | 110.7092 | 480.1656 |  |  |  | 32 | 29 | 4.87 | 2496 | 1392 | 116.88 | 4004.88 | 131.4194 | 17 | 59 | 259 | 55 | 96.97% | 0.087891 | 0.09738 | 48.7717 | 51.558 | 146.693 | 54.5363 | 96.97% | 3540.7764 | 98.63% | 99.04% | 85% |  |  | 98.57% | 1.0434
2020-04-06 | 193.0163 | 169.5329 | 169.5329 | 157.1224 | 144.1613 | 14.1595 | 14.1595 | 3473.202 | 1225.3804 | 97.1474 | 613.7527 | 47.7852 | 14.77 | 51.2604 | 225.0247 | 8564.2767 | 402.341 |  |  | 24.0325 | 1.0379 | 33.5251 | 4086.9546 | 2150.6742 | 1936.2804 | 710.9 | 23.4834 | 12.4105 | 13.0266 | 14.1803 | 13.1291 | 2.0817 | 3277.5848 | 8838.8089 | 10202.2353 | 2210.5678 | 5167.8368 | 9487.9461 | 0.094258 | 0.11026 | 0.023961 | 23.1728 | 13.1047 | 15.275 | 16.2614 | 69.6136 | 101.9016 | 156.1361 | 123.5853 | 90.1677 | 99.33% | 99.01% | 97.63% | 99.26% | 98.65% | 98.93% | 127.3095 | 108.8365 | 500.8052 |  |  |  | 33.1733 | 30.7142 | 4.87 | 2587.5199 | 1474.28 | 116.88 | 4178.6799 | 130.0152 | 17 | 59 | 259 | 55 | 96.94% | 0.088131 | 0.097937 | 48.9205 | 51.5525 | 145.7365 | 54.8278 | 96.94% | 3457.4742 | 98.62% | 99.01% | 84.98% |  |  | 98.57% | 1.0379
2020-04-05 | 190.6851 | 167.5374 | 167.5374 | 155.3643 | 142.5543 | 13.9324 | 13.9324 | 3455.657 | 1219.7391 | 119.7702 | 609.4724 | 49.7706 | 17.3315 | 61.8873 | 274.6202 | 8753.6152 | 395.5196 |  |  | 24.3727 | 1.0244 | 41.9757 | 4065.1294 | 2116.1478 | 1948.9816 | 729.2425 | 23.1477 | 12.1732 | 12.7818 | 13.9526 | 13.0686 | 2.5665 | 3304.9872 | 8729.432 | 10390.9251 | 2244.8266 | 5165.8219 | 9511.9796 | 0.092784 | 0.10973 | 0.029593 | 22.8935 | 12.6313 | 14.7525 | 18.2482 | 82.6024 | 150.944 | 154.0414 | 121.9988 | 88.8401 | 99.23% | 98.8% | 97.11% | 99.19% | 98.4% | 98.41% | 129.3331 | 109.3587 | 405.5043 |  |  |  | 32.1067 | 30.0725 | 5.9058 | 2504.32 | 1443.48 | 141.74 | 4089.54 | 128.5513 | 18.8333 | 67.25 | 298.4167 | 54.0833 | 96.88% | 0.088096 | 0.096575 | 48.1027 | 50.2772 | 143.3834 | 54.9617 | 96.88% | 3527.7202 | 98.59% | 98.81% | 85.01% |  |  | 98.56% | 1.0244
2020-04-04 | 190.9727 | 167.9311 | 167.9311 | 155.8347 | 143.0021 | 14.0481 | 14.0481 | 3448.9543 | 1217.278 | 121.7278 | 609.1711 | 51.3584 | 18.0706 | 64.6736 | 287.2267 | 9018.273 | 395.1715 |  |  | 24.5415 | 1.0177 | 44.0183 | 4058.1254 | 2109.9485 | 1948.1769 | 730.8989 | 23.0416 | 12.0964 | 12.7069 | 13.9117 | 13.0423 | 2.6085 | 3391.1065 | 8931.1257 | 10658.3955 | 2305.1131 | 5294.0123 | 9743.9151 | 0.091957 | 0.10908 | 0.030137 | 22.833 | 12.5456 | 14.6438 | 18.355 | 83.5173 | 155.6211 | 153.9685 | 121.6881 | 88.0869 | 99.22% | 98.78% | 97.05% | 99.2% | 98.42% | 98.4% | 130.4958 | 110.0123 | 398.1755 |  |  |  | 32 | 30 | 6 | 2496 | 1440 | 144 | 4080 | 128.919 | 19 | 68 | 302 | 54 | 96.86% | 0.087545 | 0.095818 | 47.8448 | 50.0223 | 143.0425 | 54.7665 | 96.86% | 3622.5647 | 98.58% | 98.83% | 84.99% |  |  | 98.57% | 1.0177
2020-04-03 | 192.3495 | 169.0897 | 169.0897 | 156.8038 | 143.7782 | 14.1293 | 14.1293 | 3473.5839 | 1216.5147 | 116.4378 | 613.2551 | 52.6237 | 18.1097 | 63.0185 | 278.4672 | 9164.622 | 400.5446 |  |  | 24.5229 | 1.0185 | 42.5651 | 4086.839 | 2140.6314 | 1946.2076 | 729.6929 | 23.2598 | 12.2859 | 12.8974 | 14.1141 | 13.0341 | 2.4951 | 3461.1914 | 9126.4884 | 10806.4491 | 2342.1252 | 5406.1112 | 9919.2054 | 0.092758 | 0.10872 | 0.028891 | 22.8962 | 12.7648 | 14.8156 | 18.3805 | 79.6998 | 141.8698 | 154.9702 | 122.102 | 87.958 | 99.23% | 98.83% | 97.19% | 99.22% | 98.53% | 98.57% | 129.3694 | 110.3767 | 415.3586 |  |  |  | 31.5833 | 29.1667 | 5.5833 | 2463.5 | 1400 | 134 | 3997.5 | 129.7627 | 18.5833 | 64.6667 | 285.75 | 54 | 96.83% | 0.087646 | 0.096207 | 48.4431 | 50.4766 | 143.9126 | 55.8385 | 96.83% | 3669.1819 | 98.57% | 98.89% | 84.99% |  |  | 98.54% | 1.0185
2020-04-02 | 192.3512 | 169.0971 | 169.0971 | 156.8841 | 143.5992 | 14.1663 | 14.1663 | 3472.9126 | 1202.3685 | 107.3543 | 612.9386 | 51.6999 | 17.2333 | 57.4443 | 251.7975 | 9168.4221 | 401.4701 |  |  | 24.5187 | 1.0186 | 38.4057 | 4085.8512 | 2163.1898 | 1922.6614 | 720.2929 | 23.2541 | 12.213 | 12.9488 | 14.2628 | 12.8825 | 2.3004 | 3498.93 | 9243.7237 | 10818.6323 | 2351.5799 | 5469.4673 | 9989.9166 | 0.093801 | 0.10777 | 0.026816 | 23.0309 | 12.9271 | 15.0375 | 17.6071 | 70.9849 | 117.4568 | 154.8862 | 121.7642 | 87.3848 | 99.27% | 98.95% | 97.48% | 99.25% | 98.7% | 98.82% | 127.9302 | 111.3484 | 447.4949 |  |  |  | 31 | 28 | 5 | 2418 | 1344 | 120 | 3882 | 129.6455 | 18 | 60 | 263 | 54 | 96.88% | 0.087553 | 0.096567 | 48.4159 | 50.9955 | 143.9109 | 54.8868 | 96.88% | 3667.1495 | 98.59% | 99.01% | 85% |  |  | 98.56% | 1.0186
2020-04-01 | 191.6368 | 168.4573 | 168.4573 | 156.3107 | 143.3559 | 14.0643 | 14.0643 | 3464.1891 | 1199.3483 | 107.0847 | 611.4925 | 52.6764 | 17.5588 | 58.5294 | 256.5537 | 9233.1611 | 399.4516 |  |  | 24.564 | 1.0169 | 39.1312 | 4075.6816 | 2157.7561 | 1917.9254 | 718.5771 | 23.1795 | 12.1466 | 12.8499 | 14.227 | 12.8502 | 2.2947 | 3520.9114 | 9299.8346 | 10883.4956 | 2366.479 | 5503.3405 | 10050.1939 | 0.093795 | 0.1079 | 0.026882 | 23.0427 | 12.904 | 14.9758 | 17.751 | 71.5752 | 118.4523 | 154.2381 | 121.0956 | 86.8007 | 99.26% | 98.94% | 97.45% | 99.25% | 98.7% | 98.82% | 127.9384 | 111.2094 | 446.4003 |  |  |  | 31 | 28 | 5 | 2418 | 1344 | 120 | 3882 | 129.406 | 18 | 60 | 263 | 54 | 96.84% | 0.087604 | 0.096612 | 48.1759 | 50.9225 | 143.218 | 55.3409 | 96.84% | 3690.0204 | 98.57% | 99.01% | 85% |  |  | 98.55% | 1.0169
2020-03-31 | 192.2438 | 168.999 | 168.999 | 156.6952 | 143.525 | 14.0837 | 14.0837 | 3474.4474 | 1219.2317 | 108.86 | 614.4098 | 51.0172 | 17.0057 | 56.6858 | 248.4728 | 9103.8658 | 403.2795 |  |  | 24.4531 | 1.0212 | 38.1823 | 4088.8572 | 2146.3557 | 1942.5014 | 723.2698 | 23.2448 | 12.3038 | 13.0145 | 14.1518 | 13.0632 | 2.3327 | 3444.9886 | 9156.7247 | 10735.072 | 2327.635 | 5398.9185 | 9904.1001 | 0.093247 | 0.1093 | 0.027148 | 22.891 | 12.8564 | 15.0385 | 17.4606 | 72.1396 | 118.8488 | 154.9846 | 122.0523 | 87.7483 | 99.27% | 98.95% | 97.49% | 99.25% | 98.66% | 98.8% | 128.691 | 109.7912 | 442.0267 |  |  |  | 30.3333 | 28 | 5 | 2366 | 1344 | 120 | 3830 | 129.5643 | 18 | 60 | 263 | 54 | 96.9% | 0.087807 | 0.096808 | 48.5632 | 50.7859 | 143.9968 | 54.6862 | 96.9% | 3642.7736 | 98.6% | 98.99% | 84.97% |  |  | 98.57% | 1.0212
2020-03-30 | 192.0418 | 168.7743 | 168.7743 | 156.3692 | 143.3697 | 14.1284 | 14.1284 | 3472.7055 | 1226.9496 | 109.5491 | 612.4894 | 49.8816 | 16.6272 | 55.424 | 242.9419 | 8766.612 | 402.9342 |  |  | 24.2739 | 1.0283 | 37.4739 | 4085.1949 | 2136.2068 | 1948.9881 | 722.0385 | 23.2675 | 12.4052 | 13.0695 | 14.0849 | 13.1459 | 2.3475 | 3314.7496 | 8853.2744 | 10393.3074 | 2245.0118 | 5205.3656 | 9582.1624 | 0.093355 | 0.11017 | 0.027108 | 22.8972 | 12.9241 | 15.1556 | 17.7384 | 74.1286 | 121.7033 | 155.1377 | 122.6936 | 89.0449 | 99.26% | 98.94% | 97.46% | 99.21% | 98.58% | 98.73% | 128.5415 | 108.9209 | 442.6762 |  |  |  | 30 | 28 | 5 | 2340 | 1344 | 120 | 3804 | 129.1621 | 18 | 60 | 263 | 54 | 96.86% | 0.088137 | 0.097207 | 48.7422 | 50.9769 | 144.4304 | 55.6506 | 96.86% | 3522.3971 | 98.58% | 98.93% | 85.01% |  |  | 98.54% | 1.0283
2020-03-29 | 192.8511 | 169.5888 | 169.5888 | 157.2678 | 144.1906 | 14.0443 | 14.0443 | 3471.7269 | 1226.6038 | 109.5182 | 613.0387 | 49.9872 | 16.6624 | 55.5413 | 243.4561 | 8952.0398 | 403.6713 |  |  | 24.0639 | 1.0366 | 37.5532 | 4084.7656 | 2135.6049 | 1949.1607 | 722.5569 | 23.2624 | 12.321 | 13.029 | 14.0809 | 13.1422 | 2.3468 | 3380.5302 | 9024.991 | 10593.7956 | 2289.6877 | 5307.6847 | 9767.5235 | 0.09368 | 0.11065 | 0.027314 | 22.8937 | 12.8313 | 15.0905 | 17.5656 | 73.4243 | 120.5839 | 155.8106 | 123.1233 | 89.0646 | 99.27% | 98.95% | 97.51% | 99.23% | 98.62% | 98.77% | 128.0953 | 108.4526 | 439.3318 |  |  |  | 30 | 28 | 5 | 2340 | 1344 | 120 | 3804 | 130.121 | 18 | 60 | 263 | 54 | 96.92% | 0.088491 | 0.097581 | 48.6124 | 50.8155 | 144.9392 | 55.1181 | 96.92% | 3591.877 | 98.61% | 98.96% | 84.99% |  |  | 98.56% | 1.0366
2020-03-28 | 193.7732 | 170.7056 | 170.7056 | 158.4365 | 145.4273 | 14.0698 | 14.0698 | 3454.3594 | 1220.4677 | 108.9703 | 608.79 | 51.7554 | 17.2518 | 57.5061 | 252.0682 | 9260.9813 | 405.2367 |  |  | 24.0021 | 1.0391 | 38.8816 | 4063.1493 | 2124.9214 | 1938.228 | 717.7603 | 23.0676 | 12.2691 | 12.8744 | 14.0105 | 13.0764 | 2.3351 | 3493.5503 | 9336.143 | 10962.1465 | 2365.8329 | 5487.4583 | 10105.6716 | 0.093066 | 0.11015 | 0.027387 | 22.887 | 12.891 | 15.0642 | 17.5554 | 73.3378 | 120.3546 | 156.4267 | 123.3515 | 88.5941 | 99.27% | 98.95% | 97.51% | 99.26% | 98.66% | 98.81% | 128.9408 | 108.94 | 438.1631 |  |  |  | 30 | 28 | 5 | 2340 | 1344 | 120 | 3804 | 131.3989 | 18 | 60 | 263 | 54 | 96.91% | 0.088025 | 0.097031 | 48.2111 | 50.8421 | 145.204 | 55.0626 | 96.91% | 3712.9005 | 98.61% | 99% | 85.02% |  |  | 98.56% | 1.0391
2020-03-27 | 195.7702 | 172.5448 | 172.5448 | 160.1755 | 146.9783 | 14.1414 | 14.1414 | 3471.4825 | 1225.7373 | 109.1161 | 613.0423 | 52.4161 | 17.472 | 58.2401 | 255.2856 | 9382.9249 | 415.007 |  |  | 23.7003 | 1.0513 | 39.3417 | 4084.5248 | 2136.6292 | 1947.8956 | 722.1584 | 23.2254 | 12.3693 | 13.0683 | 14.0877 | 13.1329 | 2.3382 | 3558.264 | 9498.941 | 11144.2294 | 2409.2528 | 5586.6055 | 10277.819 | 0.093698 | 0.11082 | 0.027519 | 22.8658 | 12.8937 | 15.1427 | 17.7608 | 74.1289 | 121.4152 | 158.0571 | 124.5769 | 89.3228 | 99.27% | 98.96% | 97.52% | 99.26% | 98.67% | 98.82% | 128.0708 | 108.2809 | 436.0691 |  |  |  | 30.125 | 28.0833 | 5 | 2349.75 | 1348 | 120 | 3817.75 | 132.8872 | 18 | 60 | 263 | 54 | 96.93% | 0.088589 | 0.097665 | 48.663 | 50.9023 | 146.6211 | 55.7144 | 96.93% | 3778.4623 | 98.61% | 99% | 84.99% |  |  | 98.54% | 1.0513
2020-03-26 | 194.5873 | 171.4214 | 171.4214 | 159.0502 | 145.9755 | 14.1542 | 14.1542 | 3471.609 | 1209.2687 | 100.7724 | 613.2712 | 46.9598 | 15.6533 | 52.1775 | 228.7116 | 9335.2276 | 414.3862 |  |  | 23.9188 | 1.0424 | 34.5604 | 4084.8803 | 2161.5679 | 1923.3124 | 714.0436 | 23.1659 | 12.3712 | 13.0188 | 14.2521 | 12.9565 | 2.1594 | 3614.2067 | 9646.6819 | 11194.2376 | 2428.9271 | 5674.0428 | 10382.1125 | 0.094759 | 0.10983 | 0.025699 | 22.9453 | 13.1363 | 15.22 | 15.8332 | 63.9686 | 98.6142 | 156.7837 | 122.9722 | 87.5916 | 99.36% | 99.08% | 97.8% | 99.35% | 98.87% | 99.05% | 126.637 | 109.2596 | 466.9456 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 131.7336 | 18 | 60 | 263 | 54 | 97.25% | 0.088532 | 0.098004 | 48.5559 | 51.3016 | 145.402 | 49.3445 | 97.25% | 3790.1629 | 98.76% | 99.15% | 84.99% |  |  | 98.71% | 1.0424
2020-03-25 | 192.8518 | 169.7754 | 169.7754 | 157.5253 | 144.5145 | 14.0323 | 14.0323 | 3463.1248 | 1206.3134 | 100.5261 | 611.3115 | 48.8599 | 16.2866 | 54.2888 | 237.966 | 9232.1728 | 408.5953 |  |  | 23.9947 | 1.0394 | 35.9588 | 4074.4363 | 2156.2853 | 1918.1511 | 711.8376 | 23.0764 | 12.2501 | 12.8478 | 14.2173 | 12.9248 | 2.1541 | 3572.6866 | 9535.1285 | 11063.9852 | 2401.1969 | 5608.6786 | 10261.6914 | 0.095117 | 0.11025 | 0.025774 | 22.946 | 13.0624 | 15.0911 | 16.5749 | 66.9719 | 103.2524 | 155.3567 | 121.846 | 86.8689 | 99.32% | 99.03% | 97.68% | 99.31% | 98.81% | 98.99% | 126.1602 | 108.842 | 465.587 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 130.3961 | 18 | 60 | 263 | 54 | 97.11% | 0.088865 | 0.098376 | 48.1743 | 51.0995 | 144.1387 | 51.6595 | 97.11% | 3746.6331 | 98.7% | 99.1% | 85% |  |  | 98.65% | 1.0394
2020-03-24 | 192.5694 | 169.3684 | 169.3684 | 156.9941 | 144.1283 | 14.1566 | 14.1566 | 3463.9362 | 1206.5961 | 100.5497 | 612.2999 | 49.772 | 16.5907 | 55.3022 | 242.4081 | 9061.5727 | 408.1087 |  |  | 23.8372 | 1.0457 | 36.63 | 4076.2361 | 2156.7905 | 1919.4456 | 712.8495 | 23.201 | 12.3744 | 12.9512 | 14.2206 | 12.9278 | 2.1546 | 3512.1642 | 9363.3795 | 10861.1925 | 2361.0708 | 5511.1428 | 10075.2698 | 0.095884 | 0.11104 | 0.025827 | 23.0521 | 13.1776 | 15.1781 | 17.2799 | 69.8689 | 107.804 | 155.0899 | 121.7454 | 87.2402 | 99.3% | 99% | 97.59% | 99.27% | 98.73% | 98.93% | 125.1515 | 108.0682 | 464.6364 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 129.8437 | 18 | 60 | 263 | 54 | 97.01% | 0.089525 | 0.09913 | 48.5266 | 51.4077 | 144.0275 | 53.8826 | 97.01% | 3682.2628 | 98.65% | 99.04% | 84.98% |  |  | 98.59% | 1.0457
2020-03-23 | 191.2967 | 167.9345 | 167.9345 | 155.3644 | 142.3881 | 14.1209 | 14.1209 | 3472.6714 | 1209.6388 | 100.8032 | 611.8823 | 47.3055 | 15.7685 | 52.5617 | 230.3954 | 8554.3694 | 405.5228 |  |  | 23.8477 | 1.0453 | 34.8148 | 4084.5538 | 2162.2294 | 1922.3244 | 712.6856 | 23.3622 | 12.5701 | 13.0423 | 14.2565 | 12.9604 | 2.1601 | 3320.6576 | 8867.5858 | 10290.5011 | 2231.6943 | 5214.2813 | 9543.7768 | 0.096507 | 0.1113 | 0.025603 | 23.1474 | 13.3653 | 15.2949 | 17.4125 | 70.3357 | 108.3966 | 154.415 | 121.7199 | 88.1884 | 99.29% | 98.99% | 97.59% | 99.22% | 98.65% | 98.86% | 124.3438 | 107.8174 | 468.6945 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 128.2557 | 18 | 60 | 263 | 54 | 96.99% | 0.089896 | 0.099601 | 48.9746 | 51.8076 | 143.8824 | 54.2588 | 96.99% | 3482.8736 | 98.64% | 98.98% | 85.02% |  |  | 98.58% | 1.0453
2020-03-22 | 189.1261 | 166.2213 | 166.2213 | 153.908 | 141.2106 | 13.9538 | 13.9538 | 3437.285 | 1197.3126 | 99.7761 | 606.0442 | 51.2265 | 17.0755 | 56.9184 | 249.4923 | 8983.6834 | 394.6017 |  |  | 24.2278 | 1.0301 | 37.7005 | 4043.3291 | 2140.1963 | 1903.1328 | 705.8202 | 22.9048 | 12.3133 | 12.8295 | 14.1112 | 12.8283 | 2.1381 | 3485.5875 | 9301.7836 | 10792.1072 | 2342.9028 | 5471.725 | 10010.06 | 0.095573 | 0.11101 | 0.025971 | 23.041 | 13.2888 | 15.2644 | 17.5192 | 70.7978 | 109.1624 | 152.0908 | 119.0368 | 84.8027 | 99.27% | 98.96% | 97.51% | 99.25% | 98.71% | 98.91% | 125.5588 | 108.0981 | 462.0592 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 127.2841 | 18 | 60 | 263 | 54 | 96.89% | 0.089376 | 0.09893 | 48.0476 | 51.5942 | 141.0634 | 54.6079 | 96.89% | 3655.3273 | 98.6% | 99.02% | 85.01% |  |  | 98.57% | 1.0301
2020-03-21 | 191.2936 | 168.3017 | 168.3017 | 156.1104 | 143.1434 | 13.9629 | 13.9629 | 3452.3294 | 1202.5531 | 100.2128 | 608.9735 | 56.9671 | 18.989 | 63.2968 | 277.4509 | 9727.0614 | 399.4944 |  |  | 24.212 | 1.0307 | 41.9253 | 4061.3029 | 2149.5636 | 1911.7393 | 709.1862 | 22.9919 | 12.1913 | 12.8925 | 14.1729 | 12.8845 | 2.1474 | 3730.3496 | 9948.4986 | 11539.9674 | 2507.8327 | 5854.3598 | 10704.9009 | 0.095235 | 0.11133 | 0.026499 | 22.9744 | 13.0671 | 15.2296 | 18.2919 | 73.9527 | 114.0818 | 153.3905 | 119.2878 | 83.5268 | 99.24% | 98.92% | 97.41% | 99.27% | 98.74% | 98.93% | 126.0035 | 107.7886 | 452.8492 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 129.2576 | 18 | 60 | 263 | 54 | 96.77% | 0.089388 | 0.098846 | 48.0757 | 51.2711 | 141.6594 | 57.0336 | 96.77% | 3911.4726 | 98.54% | 99.05% | 85.01% |  |  | 98.51% | 1.0307
2020-03-20 | 194.5604 | 171.1984 | 171.1984 | 158.7325 | 145.841 | 13.8467 | 13.8467 | 3471.772 | 1209.3255 | 100.7771 | 611.3002 | 65.5895 | 21.8632 | 72.8772 | 319.4452 | 10497.8689 | 409.4561 |  |  | 24.0788 | 1.036 | 48.271 | 4083.0722 | 2161.6694 | 1921.4028 | 712.0773 | 23.3619 | 12.4659 | 13.1387 | 14.2528 | 12.9571 | 2.1595 | 3862.855 | 10299.3988 | 11944.6641 | 2597.4038 | 6061.6997 | 11081.4234 | 0.09456 | 0.11078 | 0.026436 | 23.161 | 13.2661 | 15.4288 | 20.5539 | 83.1219 | 128.2566 | 156.155 | 121.1747 | 84.6302 | 99.16% | 98.8% | 97.12% | 99.21% | 98.63% | 98.84% | 126.9035 | 108.3234 | 453.9281 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 131.926 | 18 | 60 | 263 | 54 | 96.41% | 0.08885 | 0.098232 | 48.9665 | 51.8558 | 143.9581 | 64.0988 | 96.41% | 4050.3957 | 98.38% | 98.96% | 85.03% |  |  | 98.32% | 1.036
2020-03-19
2020-03-18 | 197.0573 | 173.9464 | 173.9464 | 161.6843 | 148.9367 | 14.102 | 14.102 | 3477.1669 | 1211.2047 | 100.9337 | 611.6735 | 54.9983 | 18.3328 | 61.1092 | 267.862 | 10169.989 | 414.3105 |  |  | 23.8613 | 1.0447 | 40.4764 | 4088.8404 | 2165.0284 | 1923.8119 | 712.6072 | 23.1109 | 12.262 | 12.902 | 14.2749 | 12.9772 | 2.1629 | 3910.1609 | 10452.3198 | 12132.8819 | 2627.3764 | 6142.5424 | 11250.8711 | 0.094178 | 0.10995 | 0.026185 | 22.8654 | 13.0273 | 15.1354 | 17.2085 | 69.4693 | 106.9845 | 158.3546 | 123.3062 | 86.2935 | 99.3% | 99.01% | 97.62% | 99.35% | 98.87% | 99.05% | 127.4183 | 109.1386 | 458.2715 |  |  |  | 33 | 30 | 5 | 2574 | 1440 | 120 | 4134 | 134.5828 | 18 | 60 | 263 | 54 | 97.03% | 0.088347 | 0.097699 | 48.275 | 51.0281 | 146.0963 | 53.6005 | 97.03% | 4102.1366 | 98.66% | 99.15% | 85.04% |  |  | 98.6% | 1.0447
2020-03-17 | 195.5359 | 172.3384 | 172.3384 | 160.0074 | 147.1076 | 13.8264 | 13.8264 | 3471.4884 | 1207.1827 | 106.4668 | 612.3992 | 53.6312 | 17.8771 | 59.5902 | 261.2038 | 9809.8549 | 410.5556 |  |  | 23.8765 | 1.0441 | 39.845 | 4083.8877 | 2157.839 | 1926.0487 | 718.8661 | 23.1975 | 12.331 | 12.8851 | 14.2275 | 12.9341 | 2.2814 | 3741.5196 | 9924.5371 | 11604.5264 | 2517.523 | 5858.592 | 10720.7799 | 0.094252 | 0.10948 | 0.027245 | 22.9667 | 13.0375 | 14.9967 | 17.4446 | 70.7483 | 115.4174 | 157.6125 | 123.3514 | 87.4332 | 99.29% | 98.98% | 97.56% | 99.31% | 98.79% | 98.92% | 127.3185 | 109.6069 | 440.4522 |  |  |  | 33 | 30 | 5.2917 | 2574 | 1440 | 127 | 4141 | 133.312 | 18 | 60 | 263 | 54 | 96.98% | 0.088404 | 0.097493 | 48.4136 | 51.0009 | 145.8468 | 54.4234 | 96.98% | 3930.9383 | 98.64% | 99.08% | 85% |  |  | 98.58% | 1.0441
2020-03-16 | 191.4353 | 168.2075 | 168.2075 | 155.8542 | 142.9846 | 13.7547 | 13.7547 | 3471.1813 | 1202.1407 | 120.2141 | 613.7971 | 49.1438 | 16.3813 | 54.6043 | 239.3487 | 8979.4315 | 402.2837 |  |  | 24.1763 | 1.0321 | 37.3405 | 4084.9783 | 2148.8265 | 1936.1518 | 734.0111 | 23.2278 | 12.3532 | 12.8936 | 14.1681 | 12.8801 | 2.576 | 3437.5782 | 8978.1081 | 10689.6214 | 2319.3855 | 5347.7031 | 9784.1432 | 0.094618 | 0.10914 | 0.030234 | 22.9326 | 12.8762 | 14.7311 | 17.0796 | 69.9133 | 129.3455 | 154.5517 | 121.8107 | 87.9408 | 99.29% | 98.98% | 97.55% | 99.26% | 98.69% | 98.68% | 126.8262 | 109.9545 | 396.9064 |  |  |  | 33 | 30 | 6 | 2574 | 1440 | 144 | 4158 | 129.1804 | 18 | 60 | 263 | 54 | 97% | 0.088962 | 0.097416 | 48.4746 | 50.5399 | 143.641 | 53.4282 | 97% | 3626.6732 | 98.64% | 98.99% | 84.97% |  |  | 98.6% | 1.0321
2020-03-15 | 191.3073 | 168.1459 | 168.1459 | 155.7204 | 142.7545 | 13.8606 | 13.8606 | 3471.713 | 1202.3248 | 120.2325 | 612.6108 | 48.7836 | 16.2612 | 54.204 | 237.5944 | 8977.2754 | 400.9473 |  |  | 24.3168 | 1.0266 | 37.0668 | 4084.3237 | 2149.1556 | 1935.1681 | 732.8433 | 23.1613 | 12.4255 | 12.9339 | 14.1703 | 12.8821 | 2.5764 | 3433.6712 | 8978.1271 | 10693.5653 | 2316.2591 | 5344.1888 | 9785.9061 | 0.094235 | 0.10873 | 0.03018 | 22.8763 | 12.9672 | 14.816 | 16.8883 | 69.0825 | 127.7013 | 154.366 | 121.6226 | 87.6353 | 99.3% | 98.99% | 97.57% | 99.27% | 98.71% | 98.7% | 127.3413 | 110.3633 | 397.6118 |  |  |  | 33 | 30 | 6 | 2574 | 1440 | 144 | 4158 | 128.9538 | 18 | 60 | 263 | 54 | 97.02% | 0.088625 | 0.097037 | 48.5208 | 50.6595 | 143.415 | 52.8035 | 97.02% | 3623.5818 | 98.65% | 99% | 85% |  |  | 98.62% | 1.0266
2020-03-14 | 193.3291 | 170.0949 | 170.0949 | 157.668 | 144.7533 | 13.9046 | 13.9046 | 3466.6228 | 1200.562 | 120.0562 | 611.0358 | 50.8604 | 16.9535 | 56.5116 | 247.7091 | 9301.2766 | 405.3688 |  |  | 24.0904 | 1.0355 | 38.6448 | 4077.6586 | 2146.0046 | 1931.654 | 731.092 | 23.2342 | 12.4269 | 12.9255 | 14.1495 | 12.8632 | 2.5726 | 3536.2584 | 9250.5211 | 11019.3919 | 2385.3036 | 5504.8978 | 10083.4239 | 0.093947 | 0.10853 | 0.03023 | 23.0066 | 13.0071 | 14.8614 | 17.222 | 70.4294 | 130.1493 | 155.9656 | 122.7349 | 88.1275 | 99.29% | 98.97% | 97.54% | 99.28% | 98.72% | 98.71% | 127.7317 | 110.5683 | 396.9574 |  |  |  | 33 | 30 | 6 | 2574 | 1440 | 144 | 4158 | 130.9508 | 18 | 60 | 263 | 54 | 96.98% | 0.088419 | 0.096791 | 48.5866 | 50.8751 | 144.7173 | 53.8369 | 96.98% | 3732.2841 | 98.64% | 99.01% | 85.02% |  |  | 98.59% | 1.0355
2020-03-13 | 192.7445 | 169.5576 | 169.5576 | 157.0782 | 144.3215 | 13.9609 | 13.9609 | 3462.6137 | 1199.1736 | 119.9174 | 610.7858 | 49.3359 | 16.4453 | 54.8177 | 240.284 | 9071.9756 | 403.9491 |  |  | 24.0103 | 1.0387 | 37.4864 | 4073.3995 | 2143.5228 | 1929.8767 | 730.7031 | 23.1869 | 12.4794 | 12.8881 | 14.1331 | 12.8483 | 2.5697 | 3453.3524 | 9030.7654 | 10756.6262 | 2329.4961 | 5375.1159 | 9843.4425 | 0.094334 | 0.10872 | 0.030085 | 22.9943 | 13.0781 | 14.829 | 17.139 | 70.1029 | 129.5757 | 155.6249 | 122.7555 | 88.7232 | 99.29% | 98.98% | 97.56% | 99.26% | 98.7% | 98.68% | 127.2072 | 110.3739 | 398.8708 |  |  |  | 33 | 30 | 6 | 2574 | 1440 | 144 | 4158 | 130.3323 | 18 | 60 | 263 | 54 | 97% | 0.088658 | 0.097092 | 48.5544 | 50.9014 | 144.6164 | 53.5846 | 97% | 3644.4795 | 98.65% | 98.99% | 85.01% |  |  | 98.6% | 1.0387
2020-03-12 | 191.9765 | 168.9505 | 168.9505 | 156.7766 | 143.9558 | 14.2327 | 14.2327 | 3469.573 | 1168.6983 | 116.8698 | 612.7299 | 57.4074 | 18.2024 | 64.4084 | 268.6015 | 9844.4265 | 403.1133 |  |  | 24.6898 | 1.012 | 42.201 | 4082.3029 | 2184.0049 | 1898.298 | 729.5997 | 23.026 | 12.1739 | 12.8637 | 14.4 | 12.5218 | 2.5044 | 3803.3957 | 9792.6362 | 11609.2154 | 2539.1332 | 5881.248 | 10649.4547 | 0.094855 | 0.106 | 0.030088 | 22.9648 | 12.9966 | 14.787 | 17.2754 | 71.4742 | 127.116 | 153.6261 | 119.5466 | 84.2292 | 99.28% | 98.9% | 97.48% | 99.32% | 98.78% | 98.81% | 126.5082 | 113.2111 | 398.8268 |  |  |  | 34.5 | 30 | 6 | 2691 | 1440 | 144 | 4275 | 129.6853 | 19.5 | 69 | 287.75 | 61.5 | 96.77% | 0.088058 | 0.096427 | 48.0636 | 50.7485 | 141.9186 | 56.3275 | 96.77% | 3938.088 | 98.54% | 99.07% | 84.99% |  |  | 98.53% | 1.012
2020-03-11 | 192.12 | 169.2337 | 169.2337 | 157.1777 | 144.4162 | 14.4079 | 14.4079 | 3470.4303 | 1158.419 | 115.8419 | 612.3475 | 59.9531 | 18.7353 | 67.4472 | 277.2829 | 10129.7262 | 403.6191 |  |  | 24.9248 | 1.0029 | 43.6254 | 4082.7778 | 2196.1694 | 1886.6084 | 728.1894 | 22.8863 | 12.0561 | 12.8313 | 14.4802 | 12.4116 | 2.4823 | 3929.3606 | 10072.9736 | 11926.0905 | 2614.0137 | 6064.8539 | 10947.4248 | 0.094734 | 0.10477 | 0.02998 | 22.8898 | 12.9677 | 14.7794 | 17.2122 | 71.2968 | 125.395 | 153.2926 | 118.8107 | 83.0383 | 99.28% | 98.89% | 97.47% | 99.34% | 98.82% | 98.85% | 126.6706 | 114.54 | 400.2672 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 129.8949 | 20 | 72 | 296 | 64 | 96.72% | 0.087584 | 0.095921 | 47.7736 | 50.6369 | 141.3177 | 56.7839 | 96.72% | 4044.0603 | 98.52% | 99.1% | 85% |  |  | 98.51% | 1.0029
2020-03-10 | 190.492 | 167.5894 | 167.5894 | 155.396 | 142.5205 | 13.965 | 13.965 | 3453.9075 | 1152.9038 | 115.2904 | 609.2006 | 55.7042 | 17.4076 | 62.6672 | 257.6319 | 9573.6761 | 394.8113 |  |  | 24.5951 | 1.0156 | 40.5337 | 4063.1081 | 2185.7134 | 1877.3947 | 724.491 | 22.9026 | 12.1934 | 12.7645 | 14.4113 | 12.3525 | 2.4705 | 3747.4014 | 9611.027 | 11381.1441 | 2492.6733 | 5785.1524 | 10446.2609 | 0.095854 | 0.1055 | 0.029853 | 23.0734 | 13.2131 | 14.8158 | 16.9034 | 69.9956 | 123.0627 | 152.6993 | 118.9152 | 84.0501 | 99.3% | 98.92% | 97.53% | 99.32% | 98.79% | 98.82% | 125.191 | 113.7419 | 401.9676 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 128.6936 | 20 | 72 | 296 | 64 | 96.8% | 0.088381 | 0.096871 | 47.8604 | 51.1023 | 141.2453 | 55.753 | 96.8% | 3857.1811 | 98.56% | 99.07% | 85.01% |  |  | 98.54% | 1.0156
2020-03-09 | 189.4048 | 166.2693 | 166.2693 | 153.8906 | 140.9333 | 13.9872 | 13.9872 | 3468.4066 | 1157.7435 | 115.7744 | 611.68 | 49.5585 | 15.487 | 55.7534 | 229.2082 | 8848.7616 | 395.6462 |  |  | 24.5715 | 1.0166 | 36.0618 | 4080.0866 | 2194.8887 | 1885.1978 | 727.4543 | 23.1355 | 12.3787 | 12.8614 | 14.4718 | 12.4044 | 2.4809 | 3498.8754 | 8978.6038 | 10634.626 | 2326.999 | 5402.7493 | 9759.9401 | 0.096601 | 0.10565 | 0.029404 | 23.1629 | 13.3311 | 14.8374 | 16.1915 | 67.0215 | 117.7833 | 152.2922 | 119.3577 | 85.771 | 99.33% | 98.97% | 97.65% | 99.3% | 98.76% | 98.79% | 124.2227 | 113.5849 | 408.1133 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 126.9226 | 20 | 72 | 296 | 64 | 96.95% | 0.088744 | 0.097378 | 48.3756 | 51.3314 | 141.5586 | 53.3905 | 96.95% | 3601.7843 | 98.62% | 99.05% | 85.01% |  |  | 98.6% | 1.0166
2020-03-08 | 189.0799 | 166.2407 | 166.2407 | 154.0212 | 141.2235 | 13.9152 | 13.9152 | 3449.7252 | 1151.5077 | 115.1508 | 609.8588 | 54.2185 | 16.9433 | 60.9958 | 250.7603 | 9393.3666 | 393.0414 |  |  | 24.6028 | 1.0153 | 39.4526 | 4059.584 | 2183.0667 | 1876.5173 | 725.0096 | 22.8392 | 12.2194 | 12.7171 | 14.3938 | 12.3376 | 2.4675 | 3681.684 | 9432.298 | 11165.9142 | 2449.4375 | 5681.1079 | 10250.4013 | 0.096414 | 0.10606 | 0.02993 | 23.0351 | 13.2441 | 14.7413 | 16.7178 | 69.2719 | 121.8852 | 151.5826 | 118.1152 | 83.709 | 99.31% | 98.93% | 97.55% | 99.32% | 98.78% | 98.81% | 124.463 | 113.1471 | 400.9402 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 127.359 | 20 | 72 | 296 | 64 | 96.83% | 0.088862 | 0.097414 | 47.7758 | 51.0205 | 140.3208 | 55.1657 | 96.83% | 3788.553 | 98.57% | 99.06% | 84.98% |  |  | 98.56% | 1.0153
2020-03-07 | 190.8521 | 168.036 | 168.036 | 155.9249 | 143.1364 | 13.9224 | 13.9224 | 3459.3961 | 1154.7358 | 115.4736 | 609.7159 | 58.6648 | 18.3328 | 65.9979 | 271.3248 | 10051.0833 | 397.7324 |  |  | 24.6477 | 1.0136 | 42.688 | 4069.112 | 2189.1867 | 1879.9253 | 725.1895 | 22.8161 | 12.111 | 12.8321 | 14.4342 | 12.3722 | 2.4744 | 3912.4588 | 10037.2666 | 11886.8301 | 2602.3459 | 6040.7055 | 10909.963 | 0.095874 | 0.10611 | 0.030432 | 22.9368 | 13.0995 | 14.874 | 17.0443 | 70.5669 | 124.0414 | 152.6016 | 118.1845 | 82.4151 | 99.3% | 98.91% | 97.51% | 99.35% | 98.83% | 98.86% | 125.1648 | 113.0917 | 394.3182 |  |  |  | 35 | 30 | 6 | 2730 | 1440 | 144 | 4314 | 129.3034 | 20 | 72 | 296 | 64 | 96.77% | 0.088678 | 0.097106 | 47.7592 | 50.9102 | 140.643 | 56.2108 | 96.77% | 4027.3655 | 98.54% | 99.1% | 85.02% |  |  | 98.53% | 1.0136
2020-03-06 | 191.0963 | 168.3602 | 168.3602 | 156.3093 | 143.3614 | 13.8812 | 13.8812 | 3454.3928 | 1160.6861 | 116.5755 | 609.6948 | 59.2644 | 18.5201 | 66.6724 | 274.0978 | 10234.4546 | 393.9517 |  |  | 24.7814 | 1.0084 | 43.3244 | 4064.0876 | 2177.1312 | 1886.9564 | 726.2703 | 22.736 | 12.0509 | 12.8214 | 14.3547 | 12.4359 | 2.498 | 3948.8224 | 10153.0657 | 12041.9538 | 2633.8247 | 6102.5701 | 11043.8478 | 0.094753 | 0.10603 | 0.030681 | 22.8448 | 12.9738 | 14.8439 | 16.8324 | 70.566 | 124.3316 | 152.7706 | 118.2741 | 82.1055 | 99.3% | 98.91% | 97.52% | 99.36% | 98.84% | 98.87% | 126.6455 | 113.1765 | 391.1257 |  |  |  | 34.4783 | 29.8696 | 6 | 2689.3043 | 1433.7391 | 144 | 4267.0435 | 129.5995 | 20 | 72 | 296 | 64 | 96.78% | 0.08811 | 0.096379 | 47.6084 | 50.6625 | 140.6289 | 55.6422 | 96.78% | 4083.1465 | 98.55% | 99.12% | 85% |  |  | 98.54% | 1.0084
2020-03-05 | 187.6991 | 165.4941 | 165.4941 | 153.6681 | 141.0966 | 13.5407 | 13.5407 | 3402.7831 | 1197.9449 | 123.9253 | 600.4787 | 59.5082 | 18.5963 | 66.9468 | 275.2256 | 10050.626 | 380.5448 |  |  | 24.7844 | 1.0083 | 44.9642 | 4003.2618 | 2080.9129 | 1922.3489 | 724.404 | 22.205 | 11.826 | 12.4863 | 13.7203 | 12.8351 | 2.6555 | 3734.3701 | 9799.1778 | 11764.7079 | 2538.2865 | 5820.9107 | 10722.1244 | 0.091947 | 0.11036 | 0.03281 | 22.455 | 12.4905 | 14.6377 | 16.7608 | 76.6608 | 136.681 | 150.4574 | 117.2705 | 81.6071 | 99.27% | 98.85% | 97.43% | 99.34% | 98.68% | 98.73% | 130.5099 | 108.7383 | 365.7366 |  |  |  | 31 | 29 | 6 | 2418 | 1392 | 144 | 3954 | 127.5687 | 20 | 72 | 296 | 64 | 96.7% | 0.088376 | 0.096274 | 46.5173 | 49.5832 | 138.3855 | 56.287 | 96.7% | 3991.9753 | 98.51% | 99.03% | 85% |  |  | 98.53% | 1.0083
2020-03-04 | 191.1921 | 168.2448 | 168.2448 | 155.9515 | 143.1351 | 13.8323 | 13.8323 | 3462.4715 | 1218.9581 | 126.0991 | 610.412 | 57.3157 | 17.9111 | 64.4801 | 265.0849 | 9908.4791 | 398.1875 |  |  | 24.6662 | 1.0129 | 43.3075 | 4072.8835 | 2117.4143 | 1955.4692 | 736.5111 | 22.9473 | 12.2933 | 12.8453 | 13.961 | 13.0603 | 2.7021 | 3684.4016 | 9675.5304 | 11619.5434 | 2503.9222 | 5744.8903 | 10588.2821 | 0.092148 | 0.11036 | 0.032546 | 22.6149 | 12.6582 | 14.6904 | 16.7275 | 76.4714 | 136.2637 | 153.4561 | 119.8638 | 84.095 | 99.28% | 98.88% | 97.5% | 99.33% | 98.67% | 98.71% | 130.2248 | 108.733 | 368.7144 |  |  |  | 31 | 29 | 6 | 2418 | 1392 | 144 | 3954 | 129.2935 | 20 | 72 | 296 | 64 | 96.78% | 0.08844 | 0.09639 | 48.0859 | 49.9636 | 141.5177 | 56.1553 | 96.78% | 3939.3232 | 98.55% | 99.02% | 85.01% |  |  | 98.53% | 1.0129
2020-03-03 | 192.7079 | 169.5984 | 169.5984 | 157.1462 | 144.2362 | 13.9169 | 13.9169 | 3471.1229 | 1202.2401 | 124.3697 | 612.4247 | 55.4729 | 17.3353 | 62.407 | 256.5623 | 9741.3509 | 403.2782 |  |  | 24.442 | 1.0216 | 41.5176 | 4083.5476 | 2144.5131 | 1939.0345 | 736.7944 | 23.1095 | 12.4522 | 12.9396 | 14.1396 | 12.8811 | 2.6651 | 3673.6757 | 9566.2453 | 11456.8324 | 2481.145 | 5707.8343 | 10454.7739 | 0.093247 | 0.10855 | 0.03174 | 22.8075 | 12.9381 | 14.7605 | 16.6905 | 74.107 | 132.8743 | 154.9171 | 121.2282 | 85.7832 | 99.3% | 98.91% | 97.55% | 99.33% | 98.7% | 98.73% | 128.6905 | 110.5439 | 378.077 |  |  |  | 31.8333 | 29 | 6 | 2483 | 1392 | 144 | 4019 | 130.3185 | 20 | 72 | 296 | 64 | 96.84% | 0.088304 | 0.096345 | 48.5012 | 50.5061 | 143.1821 | 55.7337 | 96.84% | 3884.418 | 98.57% | 99.03% | 85% |  |  | 98.54% | 1.0216
2020-03-02 | 190.5948 | 167.4281 | 167.4281 | 154.8851 | 142.0365 | 13.7752 | 13.7752 | 3464.663 | 1173.4333 | 121.3897 | 612.0454 | 51.3543 | 16.0482 | 57.7736 | 237.5136 | 9106.2588 | 396.4371 |  |  | 24.1866 | 1.0317 | 37.9394 | 4076.7084 | 2169.84 | 1906.8684 | 733.4351 | 23.1666 | 12.5431 | 12.9894 | 14.3066 | 12.5725 | 2.6012 | 3513.6518 | 9042.7608 | 10789.144 | 2353.0608 | 5432.231 | 9864.6109 | 0.096127 | 0.10764 | 0.031008 | 23.0878 | 13.2965 | 14.8791 | 16.6475 | 71.0528 | 128.5003 | 153.5512 | 120.5091 | 86.5501 | 99.32% | 98.94% | 97.59% | 99.29% | 98.69% | 98.7% | 124.8348 | 111.4855 | 387.0014 |  |  |  | 33 | 29 | 6 | 2574 | 1392 | 144 | 4110 | 128.1614 | 20 | 72 | 296 | 64 | 96.89% | 0.089391 | 0.097744 | 48.6991 | 51.2634 | 142.5284 | 55.2104 | 96.89% | 3659.1115 | 98.6% | 99.01% | 84.99% |  |  | 98.56% | 1.0317
2020-03-01 | 191.4505 | 168.2642 | 168.2642 | 155.8009 | 142.7171 | 13.8646 | 13.8646 | 3472.9473 | 1176.2391 | 121.6799 | 612.4846 | 54.2776 | 16.9617 | 61.0623 | 251.0337 | 9500.6172 | 398.5181 |  |  | 24.2067 | 1.0309 | 40.099 | 4085.4319 | 2175.0283 | 1910.4036 | 734.1645 | 23.1863 | 12.4633 | 12.9209 | 14.3408 | 12.6026 | 2.6074 | 3649.2244 | 9397.9857 | 11215.1746 | 2443.5898 | 5643.4328 | 10253.0977 | 0.096089 | 0.10804 | 0.031482 | 23.0366 | 13.18 | 14.7814 | 16.9707 | 72.4037 | 130.8801 | 153.8596 | 120.256 | 85.384 | 99.31% | 98.92% | 97.55% | 99.31% | 98.72% | 98.72% | 124.8837 | 111.0719 | 381.1716 |  |  |  | 33 | 29 | 6 | 2574 | 1392 | 144 | 4110 | 128.9249 | 20 | 72 | 296 | 64 | 96.84% | 0.089576 | 0.097873 | 48.5705 | 50.998 | 142.4664 | 56.2664 | 96.84% | 3800.95 | 98.57% | 99.02% | 85.01% |  |  | 98.53% | 1.0309
2020-02-29 | 189.8757 | 167.0335 | 167.0335 | 154.6746 | 141.837 | 13.9029 | 13.9029 | 3446.8329 | 1167.3945 | 120.7649 | 608.3192 | 57.3458 | 17.9205 | 64.514 | 265.2241 | 9772.9973 | 392.4344 |  |  | 24.6592 | 1.0132 | 42.3657 | 4055.1521 | 2158.6734 | 1896.4787 | 729.0842 | 22.8422 | 12.3589 | 12.8554 | 14.233 | 12.5078 | 2.5878 | 3731.7456 | 9603.641 | 11457.5254 | 2499.2647 | 5769.3084 | 10476.1033 | 0.094779 | 0.107 | 0.031475 | 22.948 | 13.2118 | 14.8592 | 17.0989 | 72.9847 | 132.002 | 152.145 | 118.4272 | 83.2985 | 99.28% | 98.88% | 97.47% | 99.32% | 98.73% | 98.74% | 126.6101 | 112.1445 | 381.2504 |  |  |  | 33 | 29 | 6 | 2574 | 1392 | 144 | 4110 | 127.9869 | 20 | 72 | 296 | 64 | 96.73% | 0.088563 | 0.096702 | 48.0566 | 51.019 | 140.4604 | 56.7101 | 96.73% | 3886.2636 | 98.52% | 99.04% | 85% |  |  | 98.52% | 1.0132
2020-02-28 | 190.5982 | 167.6357 | 167.6357 | 155.2659 | 142.0944 | 13.8515 | 13.8515 | 3473.7591 | 1178.0058 | 122.2139 | 612.7242 | 58.004 | 18.1381 | 65.1081 | 267.9144 | 9859.9648 | 396.5889 |  |  | 24.9655 | 1.0013 | 42.854 | 4086.4833 | 2173.5395 | 1912.9438 | 734.938 | 22.9625 | 12.3698 | 12.9094 | 14.331 | 12.6215 | 2.6189 | 3747.2502 | 9649.2236 | 11520.4179 | 2511.0338 | 5794.72 | 10529.6024 | 0.093913 | 0.10625 | 0.031398 | 22.7938 | 13.0565 | 14.7515 | 17.1414 | 73.1365 | 132.6877 | 152.801 | 118.9512 | 83.5202 | 99.28% | 98.88% | 97.46% | 99.32% | 98.74% | 98.74% | 127.7781 | 112.9447 | 382.1955 |  |  |  | 32.8333 | 28.9167 | 6 | 2561 | 1388 | 144 | 4093 | 128.3364 | 20 | 71.7917 | 295.4167 | 63.9583 | 96.71% | 0.087857 | 0.095896 | 48.2417 | 50.6018 | 141.0632 | 56.8355 | 96.71% | 3906.6923 | 98.52% | 99.04% | 85.01% |  |  | 98.51% | 1.0013
2020-02-27 | 187.0676 | 164.7749 | 164.7749 | 152.7232 | 140.1416 | 13.7957 | 13.7957 | 3408.3493 | 1193.1984 | 132.5776 | 601.0682 | 58.1443 | 18.4585 | 61.836 | 260.2648 | 9750.4975 | 380.5134 |  |  | 24.7173 | 1.0109 | 43.0499 | 4009.4175 | 2082.5732 | 1926.8443 | 733.6458 | 22.2927 | 12.0517 | 12.6133 | 13.7313 | 12.7843 | 2.8409 | 3607.8673 | 9375.1175 | 11385.5804 | 2453.5896 | 5600.6136 | 10315.3291 | 0.09257 | 0.11021 | 0.034869 | 22.483 | 12.6304 | 14.6235 | 17.269 | 73.491 | 144.099 | 149.9499 | 117.2595 | 82.3614 | 99.25% | 98.9% | 97.48% | 99.3% | 98.69% | 98.6% | 129.6318 | 108.8798 | 344.1405 |  |  |  | 29 | 27 | 6 | 2262 | 1296 | 144 | 3702 | 126.4073 | 20 | 67 | 282 | 63 | 96.66% | 0.088984 | 0.096502 | 46.9577 | 49.737 | 138.1804 | 57.1008 | 96.66% | 3861.1081 | 98.49% | 98.99% | 85.01% |  |  | 98.51% | 1.0109
2020-02-26 | 191.0525 | 168.0044 | 168.0044 | 155.5139 | 142.4001 | 13.8294 | 13.8294 | 3471.2488 | 1213.397 | 134.4071 | 612.3928 | 57.4488 | 18.1819 | 60.9629 | 255.1581 | 9738.2304 | 396.1521 |  |  | 24.7066 | 1.0113 | 42.312 | 4083.6416 | 2123.4447 | 1960.1968 | 746.7999 | 23.0482 | 12.4905 | 12.941 | 14.0007 | 13.0007 | 2.8802 | 3602.8503 | 9357.6926 | 11355.5032 | 2448.4705 | 5591.7201 | 10292.2476 | 0.092213 | 0.10931 | 0.034291 | 22.6271 | 12.7544 | 14.6 | 17.3875 | 73.8272 | 143.6007 | 153.5476 | 120.2759 | 84.9421 | 99.26% | 98.91% | 97.52% | 99.29% | 98.68% | 98.6% | 130.1339 | 109.7769 | 349.9502 |  |  |  | 29.1667 | 27.0833 | 6 | 2275 | 1300 | 144 | 3719 | 128.5641 | 19.8333 | 66.5 | 278.3333 | 62.6667 | 96.7% | 0.088417 | 0.095947 | 48.4797 | 49.9815 | 141.8152 | 57.6344 | 96.7% | 3850.925 | 98.51% | 98.98% | 85% |  |  | 98.49% | 1.0113
2020-02-25 | 189.0182 | 165.9321 | 165.9321 | 153.3453 | 140.3972 | 13.9402 | 13.9402 | 3464.8248 | 1192.1978 | 127.7355 | 612.1392 | 55.2116 | 16.8442 | 57.0832 | 222.718 | 9247.0527 | 392.0965 |  |  | 24.4061 | 1.023 | 38.2797 | 4076.9639 | 2144.8915 | 1932.0724 | 739.8747 | 23.0861 | 12.5867 | 12.9666 | 14.1421 | 12.7735 | 2.7372 | 3486.6549 | 9012.8986 | 10847.1512 | 2352.4041 | 5400.528 | 9873.4583 | 0.095274 | 0.10983 | 0.03307 | 22.8615 | 13.1064 | 14.7454 | 17.1319 | 71.1418 | 125.6159 | 151.8571 | 118.9813 | 84.6773 | 99.28% | 98.94% | 97.74% | 99.27% | 98.68% | 98.73% | 125.9525 | 109.2582 | 362.8686 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 126.3754 | 18 | 61 | 238 | 59 | 96.68% | 0.08998 | 0.09799 | 48.6394 | 50.7133 | 140.68 | 58.5508 | 96.68% | 3678.4948 | 98.5% | 99% | 84.99% |  |  | 98.47% | 1.023
2020-02-24 | 188.308 | 165.087 | 165.087 | 152.2678 | 138.9133 | 14.0819 | 14.0819 | 3471.7637 | 1194.5853 | 127.9913 | 613.4603 | 52.2095 | 15.9283 | 53.9793 | 210.6077 | 8649.756 | 391.4245 |  |  | 24.2887 | 1.0277 | 36.1982 | 4085.224 | 2149.187 | 1936.0369 | 741.4516 | 23.2209 | 12.8192 | 13.1015 | 14.1705 | 12.7991 | 2.7427 | 3291.3109 | 8507.1186 | 10238.0881 | 2220.6514 | 5097.7493 | 9319.2318 | 0.096065 | 0.11018 | 0.032787 | 22.925 | 13.3071 | 14.8511 | 17.2738 | 71.7351 | 126.6727 | 151.592 | 119.3766 | 85.9655 | 99.28% | 98.94% | 97.74% | 99.22% | 98.59% | 98.64% | 124.9159 | 108.9092 | 365.9959 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 124.9695 | 18 | 61 | 238 | 59 | 96.67% | 0.090458 | 0.09859 | 49.1416 | 51.0832 | 140.9487 | 59.0382 | 96.67% | 3472.3194 | 98.5% | 98.93% | 84.98% |  |  | 98.45% | 1.0277
2020-02-23 | 188.9393 | 165.6831 | 165.6831 | 152.8873 | 139.8109 | 14.0976 | 14.0976 | 3472.7483 | 1194.9241 | 128.0276 | 613.1733 | 53.3715 | 16.2828 | 55.1807 | 215.2954 | 8912.2204 | 392.3484 |  |  | 24.2029 | 1.0311 | 37.0039 | 4085.9216 | 2149.7966 | 1936.125 | 741.2009 | 23.2562 | 12.7958 | 13.1579 | 14.1745 | 12.8028 | 2.7434 | 3376.3115 | 8730.4599 | 10508.3848 | 2277.8192 | 5230.3225 | 9564.5605 | 0.096211 | 0.11064 | 0.033082 | 22.9554 | 13.284 | 14.924 | 17.2769 | 71.7299 | 126.624 | 151.906 | 119.3119 | 85.5052 | 99.29% | 98.94% | 97.75% | 99.24% | 98.63% | 98.68% | 124.7265 | 108.4604 | 362.7328 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 125.6605 | 18 | 61 | 238 | 59 | 96.68% | 0.090727 | 0.098848 | 49.21 | 51.1634 | 141.0034 | 59.038 | 96.68% | 3562.3699 | 98.5% | 98.95% | 84.99% |  |  | 98.45% | 1.0311
2020-02-22 | 190.1477 | 167.0727 | 167.0727 | 154.3158 | 141.2609 | 14.0553 | 14.0553 | 3473.6781 | 1195.2441 | 128.0619 | 613.0149 | 56.4957 | 17.236 | 58.4108 | 227.898 | 9452.1616 | 396.0167 |  |  | 24.3557 | 1.025 | 39.17 | 4086.693 | 2150.3721 | 1936.3208 | 741.0768 | 23.075 | 12.7569 | 13.0791 | 14.1783 | 12.8062 | 2.7442 | 3561.6758 | 9211.9091 | 11088.7137 | 2402.7824 | 5518.0142 | 10092.3749 | 0.09522 | 0.10999 | 0.033324 | 22.771 | 13.2431 | 14.8392 | 17.2401 | 71.5671 | 126.3152 | 152.6271 | 119.3409 | 84.4106 | 99.28% | 98.94% | 97.74% | 99.28% | 98.7% | 98.75% | 126.0241 | 109.0975 | 360.1051 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 127.0862 | 18 | 61 | 238 | 59 | 96.67% | 0.090044 | 0.098021 | 48.911 | 50.8533 | 141.1444 | 58.9062 | 96.67% | 3758.1774 | 98.5% | 99.01% | 85% |  |  | 98.46% | 1.025
2020-02-21 | 189.9271 | 166.8459 | 166.8459 | 154.1976 | 140.8873 | 14.2148 | 14.2148 | 3472.7881 | 1194.9379 | 128.0291 | 612.2143 | 57.3889 | 17.5085 | 59.3343 | 231.5011 | 9601.9374 | 394.6068 |  |  | 24.4528 | 1.0212 | 39.7893 | 4085.0025 | 2149.8212 | 1935.1812 | 740.2434 | 23.0812 | 12.6483 | 13.0561 | 14.1746 | 12.8029 | 2.7435 | 3613.2449 | 9350.1451 | 11257.0776 | 2437.3447 | 5599.1366 | 10244.6896 | 0.095187 | 0.11023 | 0.033649 | 22.7932 | 13.1449 | 14.8399 | 17.1955 | 71.36 | 125.9013 | 152.0726 | 118.608 | 83.2618 | 99.28% | 98.94% | 97.74% | 99.29% | 98.73% | 98.77% | 126.0682 | 108.8609 | 356.6239 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 126.8002 | 18 | 61 | 238 | 59 | 96.67% | 0.090155 | 0.098095 | 48.7856 | 50.7781 | 140.4634 | 58.7408 | 96.67% | 3813.1015 | 98.49% | 99.03% | 85.01% |  |  | 98.46% | 1.0212
2020-02-20 | 188.8812 | 165.8045 | 165.8045 | 153.1873 | 140.0268 | 14.1124 | 14.1124 | 3467.9266 | 1193.2651 | 127.8498 | 612.7639 | 56.9266 | 17.3674 | 58.8563 | 229.636 | 9450.381 | 392.4319 |  |  | 24.4901 | 1.0197 | 39.4687 | 4080.6906 | 2146.8117 | 1933.8788 | 740.6138 | 23.0767 | 12.6172 | 13.0821 | 14.1548 | 12.785 | 2.7396 | 3568.4603 | 9223.0783 | 11099.5107 | 2407.6787 | 5526.9127 | 10103.4439 | 0.095415 | 0.11045 | 0.033609 | 22.8206 | 13.1194 | 14.8543 | 17.2183 | 71.5073 | 126.2748 | 151.2789 | 118.0433 | 83.1256 | 99.28% | 98.94% | 97.73% | 99.28% | 98.71% | 98.75% | 125.7658 | 108.6498 | 357.0505 |  |  |  | 31 | 28 | 6 | 2418 | 1344 | 144 | 3906 | 125.7666 | 18 | 61 | 238 | 59 | 96.65% | 0.090336 | 0.098309 | 48.776 | 50.7944 | 139.8144 | 58.8501 | 96.65% | 3764.6784 | 98.49% | 99.01% | 84.98% |  |  | 98.46% | 1.0197
2020-02-19 | 189.2852 | 166.1798 | 166.1798 | 153.4948 | 140.5887 | 14.1175 | 14.1175 | 3465.395 | 1191.6003 | 131.8142 | 609.6058 | 57.6155 | 17.7658 | 59.5894 | 231.6955 | 9601.2895 | 392.0059 |  |  | 24.3647 | 1.0247 | 40.2844 | 4075.0008 | 2141.9806 | 1933.0202 | 741.42 | 23.1054 | 12.685 | 13.1009 | 14.1229 | 12.7671 | 2.8246 | 3616.2916 | 9332.5758 | 11300.4462 | 2441.3096 | 5597.4198 | 10253.835 | 0.095523 | 0.11084 | 0.034949 | 22.8864 | 13.1903 | 14.9145 | 17.4153 | 71.7311 | 130.0563 | 151.4973 | 118.0307 | 82.8136 | 99.27% | 98.94% | 97.74% | 99.29% | 98.72% | 98.73% | 125.6248 | 108.2672 | 343.354 |  |  |  | 31.25 | 28.25 | 6.25 | 2437.5 | 1356 | 150 | 3943.5 | 126.3246 | 18 | 60.375 | 234.75 | 58.375 | 96.66% | 0.090731 | 0.098484 | 48.8913 | 50.9912 | 139.826 | 58.8827 | 96.66% | 3823.7273 | 98.49% | 99.02% | 85.04% |  |  | 98.46% | 1.0247
2020-02-18 | 189.5019 | 166.3057 | 166.3057 | 153.349 | 140.3668 | 14.1636 | 14.1636 | 3472.211 | 1188.7741 | 158.5032 | 611.8958 | 54.4776 | 18.1592 | 56.4953 | 213.875 | 9327.7537 | 395.2767 |  |  | 24.2018 | 1.0311 | 40.2185 | 4084.1068 | 2124.9337 | 1959.1731 | 770.399 | 23.1962 | 12.9567 | 13.2585 | 14.0106 | 12.7369 | 3.3965 | 3486.3951 | 8778.9461 | 10997.6102 | 2368.7248 | 5340.5407 | 9805.1 | 0.095051 | 0.11014 | 0.04133 | 22.7756 | 13.0668 | 14.5847 | 18.3148 | 71.5557 | 151.917 | 151.9873 | 119.2435 | 84.7381 | 99.23% | 98.94% | 97.82% | 99.23% | 98.66% | 98.45% | 126.2484 | 108.9546 | 290.3495 |  |  |  | 33 | 30 | 8 | 2574 | 1440 | 192 | 4206 | 126.0702 | 18 | 56 | 212 | 54 | 96.76% | 0.091283 | 0.097764 | 49.4114 | 50.427 | 140.4531 | 57.614 | 96.76% | 3725.6432 | 98.54% | 98.92% | 85.02% |  |  | 98.49% | 1.0311
2020-02-17 | 187.9039 | 164.6169 | 164.6169 | 151.6097 | 138.1055 | 14.0822 | 14.0822 | 3470.2314 | 1188.0963 | 158.4128 | 611.8312 | 52.9981 | 17.666 | 54.961 | 208.0665 | 8812.8781 | 392.0373 |  |  | 24.0197 | 1.0384 | 39.1262 | 4082.0626 | 2123.7222 | 1958.3404 | 770.244 | 23.287 | 13.0072 | 13.2744 | 14.0026 | 12.7296 | 3.3946 | 3316.8385 | 8348.2629 | 10455.8894 | 2253.7791 | 5079.8475 | 9323.1341 | 0.096292 | 0.11116 | 0.041371 | 22.8811 | 13.1248 | 14.6056 | 18.8472 | 73.6578 | 156.436 | 150.9976 | 118.9066 | 85.2001 | 99.22% | 98.92% | 97.77% | 99.16% | 98.55% | 98.32% | 124.6208 | 107.9491 | 290.0576 |  |  |  | 33 | 30 | 8 | 2574 | 1440 | 192 | 4206 | 124.1609 | 18 | 56 | 212 | 54 | 96.69% | 0.092264 | 0.098877 | 49.5686 | 50.6115 | 139.9917 | 59.3021 | 96.69% | 3544.0441 | 98.5% | 98.83% | 85.01% |  |  | 98.45% | 1.0384
2020-02-16 | 183.7945 | 161.5459 | 161.5459 | 149.0882 | 136.1949 | 14.0003 | 14.0003 | 3393.715 | 1161.8996 | 154.9199 | 596.9409 | 54.7993 | 18.2664 | 56.8289 | 215.1382 | 9028.9403 | 374.2522 |  |  | 24.0329 | 1.0378 | 40.456 | 3990.6559 | 2076.8955 | 1913.7604 | 751.8608 | 22.2486 | 12.4577 | 12.7831 | 13.6938 | 12.4489 | 3.3197 | 3392.3835 | 8547.0335 | 10709.3527 | 2304.7071 | 5197.7733 | 9547.0515 | 0.096525 | 0.11175 | 0.042026 | 22.6203 | 13.0183 | 14.5888 | 18.6274 | 72.7552 | 154.3978 | 147.2377 | 115.6121 | 81.9817 | 99.21% | 98.91% | 97.75% | 99.19% | 98.6% | 98.38% | 124.3205 | 107.3791 | 285.5385 |  |  |  | 33 | 30 | 8 | 2574 | 1440 | 192 | 4206 | 122.1353 | 18 | 56 | 212 | 54 | 96.65% | 0.092678 | 0.099251 | 47.4894 | 50.2273 | 135.9874 | 58.5836 | 96.65% | 3625.8068 | 98.49% | 98.87% | 85.04% |  |  | 98.47% | 1.0378
2020-02-15 | 188.2473 | 165.3432 | 165.3432 | 152.4899 | 138.9728 | 14.0364 | 14.0364 | 3447.9943 | 1149.8743 | 201.9609 | 608.0404 | 56.8917 | 17.6697 | 42.7084 | 197.6948 | 9482.6781 | 390.776 |  |  | 23.9945 | 1.0394 | 36.5646 | 4056.0347 | 2096.159 | 1959.8757 | 810.0014 | 22.9041 | 12.8533 | 13.2 | 13.8208 | 12.3201 | 4.3277 | 3514.9764 | 8444.1925 | 11183.2709 | 2397.5014 | 5277.4958 | 9685.8154 | 0.095222 | 0.10787 | 0.053388 | 22.6424 | 12.6806 | 13.9747 | 17.5081 | 53.3731 | 182.5808 | 150.8597 | 118.7062 | 84.2543 | 99.26% | 99.19% | 97.96% | 99.27% | 98.99% | 98.11% | 126.0214 | 111.241 | 224.7692 |  |  |  | 33 | 29.4167 | 10.3333 | 2574 | 1412 | 248 | 4234 | 125.2116 | 18.5833 | 44.9167 | 207.9167 | 59.8333 | 96.67% | 0.092577 | 0.096991 | 48.9574 | 49.2977 | 139.0999 | 59.2843 | 96.67% | 3784.8547 | 98.5% | 99% | 85.01% |  |  | 98.45% | 1.0394
2020-02-14 | 188.9525 | 165.7097 | 165.7097 | 152.6705 | 139.2184 | 14.0678 | 14.0678 | 3472.9584 | 1136.4265 | 235.1227 | 612.7361 | 56.8549 | 16.8788 | 32.8692 | 182.1134 | 9453.6731 | 395.346 |  |  | 23.9748 | 1.0402 | 33.2978 | 4085.6945 | 2101.4093 | 1984.2852 | 847.8588 | 23.2428 | 13.0392 | 13.3222 | 13.8554 | 12.176 | 5.0383 | 3485.8592 | 8114.07 | 11157.7675 | 2384.0939 | 5163.368 | 9474.8753 | 0.095175 | 0.10601 | 0.061358 | 22.671 | 12.442 | 13.4923 | 16.8734 | 41.5254 | 200.3185 | 151.4273 | 119.4698 | 85.4129 | 99.29% | 99.36% | 98.08% | 99.29% | 99.2% | 97.89% | 126.0838 | 113.1956 | 195.5741 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 125.2171 | 19 | 37 | 205 | 64 | 96.66% | 0.093232 | 0.096431 | 49.6042 | 48.6053 | 139.6947 | 59.8985 | 96.66% | 3773.5848 | 98.49% | 99.04% | 85% |  |  | 98.43% | 1.0402
2020-02-13 | 186.6486 | 163.8323 | 163.8323 | 150.9305 | 137.6356 | 14.1133 | 14.1133 | 3434.8073 | 1123.9426 | 232.5398 | 605.441 | 57.7083 | 17.1322 | 33.3626 | 184.847 | 9459.6421 | 385.258 |  |  | 24.0354 | 1.0377 | 33.7976 | 4040.2483 | 2078.3248 | 1961.9235 | 837.9809 | 22.8163 | 12.9017 | 13.1977 | 13.7032 | 12.0422 | 4.983 | 3492.3415 | 8131.6999 | 11183.9541 | 2388.4213 | 5173.6657 | 9496.2433 | 0.095266 | 0.1063 | 0.061846 | 22.6331 | 12.5241 | 13.6055 | 16.8684 | 41.5056 | 200.171 | 149.2707 | 117.5666 | 83.6128 | 99.28% | 99.36% | 98.05% | 99.29% | 99.2% | 97.89% | 125.9627 | 112.893 | 194.0317 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 123.6882 | 19 | 37 | 205 | 64 | 96.61% | 0.093448 | 0.096613 | 48.9158 | 48.7627 | 137.4704 | 59.8715 | 96.61% | 3781.0195 | 98.47% | 99.04% | 85.01% |  |  | 98.43% | 1.0377
2020-02-12 | 188.9717 | 165.7769 | 165.7769 | 152.6854 | 139.3703 | 14.3027 | 14.3027 | 3473.9975 | 1136.7664 | 235.1931 | 612.2654 | 59.1464 | 17.5591 | 34.194 | 189.4534 | 9732.9288 | 394.358 |  |  | 23.9877 | 1.0397 | 34.6398 | 4086.2629 | 2102.038 | 1984.2249 | 847.4585 | 23.1949 | 13.0915 | 13.3752 | 13.8596 | 12.1796 | 5.0399 | 3577.4678 | 8330.3551 | 11457.5667 | 2446.6138 | 5299.896 | 9728.3913 | 0.095472 | 0.10677 | 0.062355 | 22.6213 | 12.495 | 13.558 | 17.1015 | 42.0779 | 202.9216 | 150.9264 | 118.6 | 84.0305 | 99.28% | 99.35% | 98.05% | 99.3% | 99.21% | 97.91% | 125.6916 | 112.3937 | 192.4469 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 124.8942 | 19 | 37 | 205 | 64 | 96.61% | 0.093788 | 0.096926 | 49.6615 | 48.6743 | 138.8606 | 60.6973 | 96.61% | 3873.2524 | 98.47% | 99.05% | 85.02% |  |  | 98.41% | 1.0397
2020-02-11 | 187.8237 | 164.4948 | 164.4948 | 151.1961 | 137.555 | 14.2045 | 14.2045 | 3469.8996 | 1135.4256 | 234.9156 | 613.5008 | 55.6791 | 16.5297 | 32.1895 | 178.3473 | 9234.1865 | 390.8801 |  |  | 23.9277 | 1.0421 | 32.6092 | 4083.4004 | 2099.5585 | 1983.842 | 848.4164 | 23.3289 | 13.2987 | 13.5347 | 13.8432 | 12.1653 | 5.0339 | 3413.3031 | 7938.2071 | 10909.5356 | 2334.9085 | 5053.9849 | 9266.9445 | 0.095938 | 0.10695 | 0.061912 | 22.7703 | 12.6888 | 13.6889 | 16.8883 | 41.5856 | 200.7653 | 150.3628 | 118.532 | 84.7281 | 99.29% | 99.36% | 98.08% | 99.28% | 99.18% | 97.83% | 125.0806 | 112.202 | 193.8248 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 123.3322 | 19 | 37 | 205 | 64 | 96.66% | 0.094018 | 0.097238 | 50.1622 | 49.148 | 138.7706 | 59.9804 | 96.66% | 3693.9543 | 98.49% | 99.01% | 84.98% |  |  | 98.43% | 1.0421
2020-02-10 | 185.8178 | 162.395 | 162.395 | 148.8019 | 135.172 | 14.1471 | 14.1471 | 3472.7816 | 1136.3686 | 235.1107 | 612.2885 | 51.3208 | 15.2359 | 29.6698 | 164.387 | 8584.0323 | 387.6672 |  |  | 23.6708 | 1.0524 | 30.0566 | 4085.0701 | 2101.3023 | 1983.7678 | 847.3992 | 23.4228 | 13.593 | 13.6791 | 13.8547 | 12.1754 | 5.0381 | 3176.2667 | 7395.8761 | 10172.673 | 2172.1655 | 4705.4598 | 8637.2402 | 0.097747 | 0.10853 | 0.062033 | 22.853 | 12.9772 | 13.8667 | 16.9134 | 41.6143 | 200.6863 | 149.1747 | 118.0724 | 85.4756 | 99.3% | 99.37% | 98.1% | 99.22% | 99.12% | 97.68% | 122.7659 | 110.5725 | 193.4451 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 120.9474 | 19 | 37 | 205 | 64 | 96.69% | 0.095482 | 0.098856 | 50.695 | 49.6968 | 138.231 | 60.029 | 96.69% | 3438.8057 | 98.51% | 98.94% | 85.01% |  |  | 98.43% | 1.0524
2020-02-09 | 186.2195 | 162.8358 | 162.8358 | 149.2731 | 135.5154 | 14.1857 | 14.1857 | 3470.6761 | 1135.6796 | 234.9682 | 612.9377 | 54.7498 | 16.2539 | 31.6522 | 175.3705 | 9013.5217 | 388.8642 |  |  | 23.5926 | 1.0556 | 32.0649 | 4083.6138 | 2100.0283 | 1983.5855 | 847.9059 | 23.3837 | 13.5627 | 13.7324 | 13.8463 | 12.168 | 5.035 | 3337.4075 | 7765.1146 | 10674.625 | 2282.7987 | 4942.5443 | 9066.0741 | 0.098092 | 0.10949 | 0.063461 | 22.8241 | 12.946 | 13.9042 | 17.2105 | 42.3675 | 204.4617 | 149.0093 | 117.3143 | 83.7551 | 99.29% | 99.36% | 98.07% | 99.25% | 99.14% | 97.74% | 122.3338 | 109.5974 | 189.0937 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 121.2809 | 19 | 37 | 205 | 64 | 96.64% | 0.096199 | 0.099478 | 50.6788 | 49.6742 | 137.548 | 61.1106 | 96.64% | 3612.3589 | 98.48% | 98.97% | 84.99% |  |  | 98.4% | 1.0556
2020-02-08 | 185.8321 | 162.8024 | 162.8024 | 149.5928 | 135.5799 | 14.1467 | 14.1467 | 3443.7379 | 1126.8649 | 233.1445 | 609.2095 | 58.6485 | 17.4113 | 33.9062 | 187.8586 | 9552.7736 | 384.4909 |  |  | 23.906 | 1.0429 | 34.3482 | 4052.9474 | 2083.7286 | 1969.2188 | 842.3539 | 23.0297 | 13.2096 | 13.6967 | 13.7389 | 12.0736 | 4.996 | 3522.0992 | 8188.4538 | 11250.2815 | 2409.5909 | 5214.3152 | 9557.8035 | 0.096679 | 0.10841 | 0.063862 | 22.7311 | 12.7432 | 14.0012 | 17.122 | 42.1718 | 203.6614 | 148.2096 | 116.1488 | 81.5899 | 99.28% | 99.35% | 98.03% | 99.29% | 99.19% | 97.87% | 124.122 | 110.6887 | 187.9064 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 121.5462 | 19 | 37 | 205 | 64 | 96.59% | 0.095183 | 0.098297 | 49.936 | 49.4755 | 136.1816 | 60.8232 | 96.59% | 3811.2979 | 98.46% | 99.03% | 84.97% |  |  | 98.41% | 1.0429
2020-02-07 | 187.2631 | 163.8948 | 163.8948 | 150.3396 | 136.6399 | 14.2863 | 14.2863 | 3475.8914 | 1137.3862 | 235.3213 | 612.6392 | 59.8903 | 17.7799 | 34.6241 | 191.8361 | 9862.7832 | 392.868 |  |  | 23.9284 | 1.042 | 35.0755 | 4088.5307 | 2103.184 | 1985.3467 | 847.9605 | 23.3683 | 13.5552 | 13.9237 | 13.8671 | 12.1863 | 5.0426 | 3647.457 | 8493.4213 | 11682.149 | 2494.444 | 5403.6078 | 9918.9451 | 0.097039 | 0.10948 | 0.065219 | 22.7714 | 12.9264 | 14.1014 | 17.0327 | 41.9078 | 202.0976 | 148.9093 | 115.986 | 80.5679 | 99.29% | 99.36% | 98.07% | 99.32% | 99.22% | 97.96% | 123.6612 | 109.6057 | 183.9951 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 122.2315 | 19 | 37 | 205 | 64 | 96.64% | 0.09593 | 0.098957 | 50.8472 | 49.7992 | 136.4153 | 60.4522 | 96.64% | 3949.0308 | 98.48% | 99.07% | 85.02% |  |  | 98.42% | 1.042
2020-02-06 | 186.5913 | 163.1113 | 163.1113 | 149.3664 | 135.4662 | 14.313 | 14.313 | 3472.5964 | 1136.308 | 235.0982 | 612.8816 | 60.2037 | 17.873 | 34.8053 | 192.8401 | 9728.0029 | 391.243 |  |  | 23.685 | 1.0519 | 35.259 | 4085.478 | 2101.1902 | 1984.2878 | 847.9798 | 23.48 | 13.7449 | 14.147 | 13.854 | 12.1747 | 5.0378 | 3630.3401 | 8448.4207 | 11615.2187 | 2483.1024 | 5376.8412 | 9864.3672 | 0.098323 | 0.11115 | 0.06645 | 22.9035 | 13.1145 | 14.3237 | 17.3459 | 42.696 | 206.0121 | 148.2121 | 115.2156 | 79.7457 | 99.28% | 99.35% | 98.05% | 99.3% | 99.21% | 97.91% | 122.047 | 107.9619 | 180.5856 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 121.0409 | 19 | 37 | 205 | 64 | 96.6% | 0.097328 | 0.10036 | 51.3719 | 50.3418 | 135.7009 | 61.5852 | 96.6% | 3929.7147 | 98.47% | 99.05% | 85% |  |  | 98.39% | 1.0519
2020-02-05 | 171.7387 | 148.6858 | 148.6858 | 134.9095 | 129.1925 | 12.9992 | 12.9992 | 3368.6314 | 1102.2884 | 228.0597 | 629.3106 | 63.5767 | 18.8743 | 36.7553 | 203.644 | 9766.7478 | 371.9526 |  |  | 23.3965 | 1.0637 | 37.2344 | 3997.9419 | 2038.2833 | 1959.6586 | 857.3702 | 23.0528 | 13.7763 | 14.8757 | 13.4392 | 11.8102 | 4.887 | 3614.8364 | 8215.0396 | 11118.3377 | 2485.5011 | 5299.344 | 9520.6971 | 0.10598 | 0.12258 | 0.071732 | 23.1248 | 13.2513 | 14.6709 | 17.9513 | 44.8756 | 221.1115 | 134.8799 | 102.4855 | 72.4665 | 99.24% | 99.31% | 97.86% | 99.28% | 99.15% | 97.68% | 113.2262 | 97.899 | 167.2899 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 110.4791 | 19 | 37 | 205 | 64 | 96.43% | 0.10581 | 0.10909 | 51.7049 | 51.047 | 122.3583 | 64.5714 | 96.43% | 3882.5406 | 98.36% | 98.98% | 84.26% |  |  | 98.31% | 1.0637
2020-02-04 | 185.426 | 162.4863 | 162.4863 | 148.9069 | 134.8904 | 13.2497 | 13.2497 | 3427.9062 | 1121.6844 | 232.0726 | 605.6103 | 54.0737 | 16.0531 | 54.0737 | 173.205 | 9253.6172 | 366.0565 |  |  | 22.8026 | 1.0885 | 39.1336 | 4033.5164 | 2074.1491 | 1959.3673 | 837.6829 | 22.9397 | 13.5795 | 13.9578 | 13.6757 | 12.018 | 4.973 | 3482.6296 | 8073.5763 | 11101.0348 | 2381.8436 | 5149.5383 | 9427.1685 | 0.099984 | 0.11183 | 0.065707 | 22.8084 | 13.2022 | 14.391 | 16.5907 | 70.7471 | 197.7723 | 148.8776 | 116.9696 | 82.3792 | 99.33% | 98.95% | 98.16% | 99.3% | 98.63% | 97.9% | 120.0192 | 107.3027 | 182.6298 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 121.8229 | 19 | 64 | 205 | 64 | 96.82% | 0.098291 | 0.10154 | 50.477 | 50.4016 | 136.7991 | 58.9819 | 96.82% | 3764.4681 | 98.56% | 98.86% | 84.99% |  |  | 98.46% | 1.0885
2020-02-03 | 182.7648 | 159.2587 | 159.2587 | 145.2655 | 130.9545 | 13.9878 | 13.9878 | 3469.7253 | 1135.3685 | 234.9038 | 613.6209 | 52.0792 | 15.461 | 52.0792 | 166.8162 | 8703.3396 | 381.5528 |  |  | 23.731 | 1.05 | 37.6902 | 4083.3461 | 2099.4529 | 1983.8932 | 848.5247 | 23.506 | 13.9932 | 14.3062 | 13.8425 | 12.1647 | 5.0337 | 3289.4903 | 7621.3083 | 10475.0063 | 2250.0727 | 4862.7124 | 8897.3986 | 0.099655 | 0.11183 | 0.065682 | 22.9432 | 13.3504 | 14.4658 | 16.516 | 70.457 | 197.0648 | 145.8509 | 114.2211 | 80.4693 | 99.31% | 98.93% | 98.13% | 99.27% | 98.55% | 97.79% | 120.4158 | 107.3091 | 182.6994 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 116.9741 | 19 | 64 | 205 | 64 | 96.76% | 0.098114 | 0.10134 | 51.8055 | 50.7595 | 134.3307 | 58.7363 | 96.76% | 3555.015 | 98.54% | 98.8% | 84.97% |  |  | 98.46% | 1.05
2020-02-02 | 181.8242 | 158.5774 | 158.5774 | 144.827 | 130.4798 | 13.9978 | 13.9978 | 3459.8623 | 1132.1411 | 234.2361 | 610.6985 | 56.2175 | 16.6896 | 56.2175 | 180.0718 | 9203.6261 | 378.3392 |  |  | 24.2064 | 1.0309 | 40.6851 | 4070.5608 | 2093.4851 | 1977.0757 | 844.9346 | 23.2467 | 13.7505 | 14.2027 | 13.8032 | 12.1301 | 5.0193 | 3455.9236 | 8011.2433 | 11014.9237 | 2363.695 | 5109.9339 | 9354.2224 | 0.098501 | 0.11122 | 0.066525 | 22.8005 | 13.1915 | 14.4577 | 16.6158 | 70.8594 | 198.0955 | 144.468 | 112.4358 | 77.7848 | 99.29% | 98.9% | 98.07% | 99.3% | 98.61% | 97.88% | 121.8268 | 107.8926 | 180.3844 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 116.4511 | 19 | 64 | 205 | 64 | 96.67% | 0.097455 | 0.1005 | 51.1999 | 50.4497 | 132.4348 | 59.0744 | 96.67% | 3735.5889 | 98.5% | 98.85% | 85% |  |  | 98.45% | 1.0309
2020-02-01 | 183.3304 | 160.1068 | 160.1068 | 146.339 | 131.7764 | 14.2154 | 14.2154 | 3464.9513 | 1133.8064 | 234.5806 | 611.5815 | 59.1474 | 17.5594 | 59.1474 | 189.4565 | 9728.0321 | 382.8107 |  |  | 24.4441 | 1.0216 | 42.8055 | 4076.5328 | 2096.5644 | 1979.9685 | 846.1621 | 23.2236 | 13.7678 | 14.3604 | 13.8235 | 12.1479 | 5.0267 | 3627.5749 | 8409.0531 | 11561.7942 | 2481.1077 | 5363.7108 | 9818.683 | 0.097265 | 0.11032 | 0.066953 | 22.7279 | 13.1792 | 14.5864 | 16.5272 | 70.4823 | 197.0433 | 145.1855 | 112.4847 | 76.6962 | 99.29% | 98.9% | 98.07% | 99.33% | 98.69% | 97.99% | 123.3746 | 108.7707 | 179.2292 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 117.6335 | 19 | 64 | 205 | 64 | 96.66% | 0.096594 | 0.099486 | 51.3518 | 50.4935 | 132.563 | 58.7599 | 96.66% | 3921.1183 | 98.49% | 98.91% | 85% |  |  | 98.46% | 1.0216
2020-01-31 | 183.5837 | 160.4197 | 160.4197 | 146.5715 | 131.834 | 14.2345 | 14.2345 | 3460.6804 | 1132.4088 | 234.2915 | 611.1137 | 60.4579 | 17.9484 | 60.4579 | 193.6541 | 9909.3642 | 382.6009 |  |  | 24.3099 | 1.0268 | 43.7539 | 4071.7941 | 2093.9801 | 1977.814 | 845.4052 | 23.164 | 13.8482 | 14.66 | 13.8065 | 12.133 | 5.0205 | 3688.1745 | 8547.4521 | 11750.1684 | 2522.6977 | 5452.7424 | 9979.5126 | 0.097608 | 0.11094 | 0.067798 | 22.7083 | 13.2767 | 14.9096 | 16.6802 | 71.1463 | 198.9426 | 145.2434 | 112.2996 | 76.0389 | 99.29% | 98.89% | 98.06% | 99.34% | 98.7% | 98.01% | 122.9402 | 108.1662 | 176.9971 |  |  |  | 33 | 29 | 12 | 2574 | 1392 | 288 | 4254 | 117.5684 | 19 | 64 | 205 | 64 | 96.64% | 0.097105 | 0.099953 | 51.6723 | 50.8946 | 132.3218 | 59.312 | 96.64% | 3986.3049 | 98.48% | 98.92% | 84.99% |  |  | 98.45% | 1.0268
2020-01-30 | 182.5302 | 159.3087 | 159.3087 | 145.3794 | 130.4067 | 14.201 | 14.201 | 3455.7863 | 1163.5426 | 322.486 | 610.579 | 58.7594 | 18.7898 | 58.7594 | 155.593 | 9821.4699 | 378.057 |  |  | 24.1027 | 1.0351 | 45.0135 | 4066.3653 | 1969.7577 | 2096.6076 | 933.0651 | 23.2215 | 13.9293 | 14.7322 | 12.9874 | 12.4665 | 6.9104 | 3447.5379 | 7673.3825 | 11644.0104 | 2437.7146 | 5008.7012 | 9384.3051 | 0.09295 | 0.1138 | 0.092235 | 22.1394 | 12.0129 | 13.7325 | 17.1351 | 77.967 | 235.8398 | 144.6238 | 113.3933 | 77.5485 | 99.23% | 98.83% | 98.34% | 99.3% | 98.44% | 97.49% | 129.1019 | 105.4526 | 130.1022 |  |  |  | 31.1667 | 29.9167 | 16.5833 | 2431 | 1436 | 398 | 4265 | 116.2362 | 19 | 59.4167 | 157.3333 | 59.4167 | 96.71% | 0.099506 | 0.099902 | 51.883 | 47.8849 | 131.4412 | 58.535 | 96.71% | 3951.5903 | 98.51% | 98.73% | 84.98% |  |  | 98.47% | 1.0351
2020-01-29 | 181.5019 | 157.9892 | 157.9892 | 143.7778 | 128.3238 | 14.1546 | 14.1546 | 3473.2552 | 1172.4068 | 332.1819 | 612.8088 | 57.359 | 18.4715 | 57.359 | 148.7445 | 9589.5485 | 376.4621 |  |  | 24.193 | 1.0315 | 44.0574 | 4086.064 | 1968.6665 | 2117.3976 | 944.9907 | 23.5127 | 14.2114 | 15.2455 | 12.9802 | 12.5615 | 7.1182 | 3354.8606 | 7445.9201 | 11401.4603 | 2378.8095 | 4868.0481 | 9144.4861 | 0.093113 | 0.11499 | 0.095455 | 22.1979 | 12.0603 | 14.0178 | 17.1924 | 78.6303 | 237.5008 | 143.7892 | 112.6754 | 76.9175 | 99.22% | 98.82% | 98.37% | 99.28% | 98.38% | 97.4% | 128.8757 | 104.3552 | 125.7136 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 114.2946 | 19 | 59 | 153 | 59 | 96.72% | 0.10049 | 0.10072 | 52.9696 | 48.276 | 130.7035 | 58.4944 | 96.72% | 3866.1278 | 98.52% | 98.69% | 85% |  |  | 98.47% | 1.0315
2020-01-28 | 179.4655 | 155.9351 | 155.9351 | 141.5429 | 126.1417 | 14.0553 | 14.0553 | 3466.2425 | 1170.0397 | 331.5112 | 612.1103 | 54.5309 | 17.5608 | 54.5309 | 141.4106 | 9290.1113 | 372.6691 |  |  | 24.1585 | 1.0328 | 41.8851 | 4078.3528 | 1964.6916 | 2113.6612 | 943.6215 | 23.5304 | 14.3922 | 15.2975 | 12.954 | 12.5361 | 7.1038 | 3263.3871 | 7242.1953 | 11087.8911 | 2313.9569 | 4735.1161 | 8893.6844 | 0.094113 | 0.11635 | 0.096508 | 22.2763 | 12.2444 | 14.0936 | 16.7912 | 76.7987 | 231.997 | 142.163 | 111.2807 | 76.0256 | 99.24% | 98.85% | 98.41% | 99.27% | 98.38% | 97.39% | 127.5065 | 103.1351 | 124.3421 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 112.0563 | 19 | 59 | 153 | 59 | 96.79% | 0.10161 | 0.10185 | 53.2201 | 48.6143 | 129.3476 | 57.1325 | 96.79% | 3760.5106 | 98.55% | 98.69% | 84.99% |  |  | 98.5% | 1.0328
2020-01-27 | 178.0829 | 154.3019 | 154.3019 | 139.5194 | 123.7974 | 13.9959 | 13.9959 | 3473.6318 | 1172.5339 | 332.2179 | 612.1261 | 51.8596 | 16.7005 | 51.8596 | 134.4833 | 8719.5085 | 370.1692 |  |  | 24.0002 | 1.0392 | 39.8333 | 4085.7578 | 1968.8799 | 2116.878 | 944.344 | 23.7809 | 14.7825 | 15.7056 | 12.9816 | 12.5629 | 7.119 | 3090.4266 | 6863.2285 | 10515.1067 | 2190.9898 | 4485.5364 | 8431.0631 | 0.095453 | 0.11788 | 0.097109 | 22.4557 | 12.5522 | 14.4593 | 17.0042 | 77.7375 | 234.6618 | 141.325 | 110.7464 | 76.1796 | 99.24% | 98.84% | 98.4% | 99.22% | 98.27% | 97.22% | 125.7161 | 101.7986 | 123.5729 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 109.8593 | 19 | 59 | 153 | 59 | 96.78% | 0.10289 | 0.10318 | 54.269 | 49.4671 | 128.9607 | 57.8306 | 96.78% | 3562.3205 | 98.54% | 98.6% | 85.02% |  |  | 98.49% | 1.0392
2020-01-26 | 178.3269 | 154.6726 | 154.6726 | 139.9462 | 124.223 | 14.0365 | 14.0365 | 3473.2633 | 1172.4095 | 332.1827 | 613.1623 | 54.7579 | 17.6339 | 54.7579 | 141.9993 | 9173.1726 | 370.2332 |  |  | 23.8598 | 1.0448 | 42.0595 | 4086.4256 | 1968.671 | 2117.7546 | 945.3451 | 23.6543 | 14.7264 | 15.8883 | 12.9802 | 12.5615 | 7.1182 | 3230.0197 | 7167.9545 | 10974.2887 | 2290.3354 | 4686.6463 | 8802.5368 | 0.096114 | 0.11919 | 0.099499 | 22.3277 | 12.493 | 14.5988 | 17.2672 | 78.9778 | 238.5827 | 141.0997 | 110.1134 | 74.7454 | 99.23% | 98.83% | 98.39% | 99.25% | 98.31% | 97.29% | 124.8513 | 100.6811 | 120.6047 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 110.1324 | 19 | 59 | 153 | 59 | 96.75% | 0.10404 | 0.10423 | 54.269 | 49.4196 | 128.1956 | 58.7532 | 96.75% | 3722.0433 | 98.53% | 98.64% | 85% |  |  | 98.46% | 1.0448
2020-01-25 | 178.4981 | 155.0217 | 155.0217 | 140.4427 | 124.7791 | 14.0617 | 14.0617 | 3458.393 | 1167.39 | 330.7605 | 609.4792 | 57.1518 | 18.4048 | 57.1518 | 148.2072 | 9684.672 | 367.3102 |  |  | 24.1376 | 1.0337 | 43.8983 | 4067.8722 | 1960.2424 | 2107.6297 | 940.2397 | 23.4764 | 14.579 | 15.7719 | 12.9247 | 12.5078 | 7.0877 | 3386.5438 | 7520.2759 | 11521.051 | 2400.9745 | 4915.1676 | 9237.9404 | 0.094895 | 0.1182 | 0.10022 | 22.3144 | 12.4608 | 14.6153 | 16.9357 | 77.4284 | 233.7452 | 140.7853 | 109.3804 | 73.1005 | 99.23% | 98.84% | 98.4% | 99.29% | 98.42% | 97.47% | 126.4553 | 101.5218 | 119.7327 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 110.7715 | 19 | 59 | 153 | 59 | 96.76% | 0.10321 | 0.10327 | 53.8273 | 49.3905 | 127.3544 | 57.6004 | 96.76% | 3903.5343 | 98.54% | 98.72% | 85.02% |  |  | 98.49% | 1.0337
2020-01-24 | 178.6332 | 155.1046 | 155.1046 | 140.4397 | 124.5008 | 14.1493 | 14.1493 | 3463.025 | 1168.9536 | 331.2035 | 611.9543 | 53.5895 | 17.2576 | 53.5895 | 138.9694 | 9829.5878 | 370.4634 |  |  | 24.1456 | 1.0333 | 41.1621 | 4074.9794 | 1962.8679 | 2112.1114 | 943.1578 | 23.5286 | 14.6649 | 15.9045 | 12.942 | 12.5245 | 7.0972 | 3438.8547 | 7634.566 | 11691.3525 | 2438.0476 | 4990.5591 | 9376.5501 | 0.095107 | 0.1188 | 0.10167 | 22.3012 | 12.4888 | 14.6616 | 15.6547 | 71.5789 | 216.1577 | 140.6157 | 108.938 | 72.133 | 99.29% | 98.93% | 98.52% | 99.36% | 98.57% | 97.69% | 126.1732 | 101.0074 | 118.0267 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 110.2953 | 19 | 59 | 153 | 59 | 97.01% | 0.10374 | 0.10373 | 54.098 | 49.4515 | 126.9889 | 53.251 | 97.01% | 3963.2528 | 98.65% | 98.84% | 84.98% |  |  | 98.61% | 1.0333
2020-01-23 | 176.786 | 153.4802 | 153.4802 | 138.8702 | 122.9514 | 14.2081 | 14.2081 | 3444.4359 | 1162.6788 | 329.4257 | 606.828 | 55.1742 | 17.768 | 55.1742 | 143.0789 | 9731.6263 | 363.4539 |  |  | 24.1407 | 1.0335 | 42.3793 | 4051.2639 | 1952.3315 | 2098.9324 | 936.2536 | 23.3058 | 14.61 | 15.9766 | 12.8725 | 12.4573 | 7.0591 | 3423.4557 | 7606.3281 | 11657.8649 | 2426.7812 | 4969.8998 | 9345.5029 | 0.095797 | 0.11989 | 0.10321 | 22.2891 | 12.5657 | 14.9007 | 16.1086 | 73.6187 | 222.1326 | 138.88 | 107.3935 | 70.6906 | 99.27% | 98.89% | 98.47% | 99.34% | 98.52% | 97.62% | 125.2645 | 100.0937 | 116.2687 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 108.7759 | 19 | 59 | 153 | 59 | 96.9% | 0.10469 | 0.10464 | 53.8925 | 49.7555 | 125.2263 | 54.7674 | 96.9% | 3946.924 | 98.6% | 98.8% | 85.02% |  |  | 98.57% | 1.0335
2020-01-22 | 177.3749 | 153.7023 | 153.7023 | 138.8678 | 122.7921 | 14.1076 | 14.1076 | 3471.7173 | 1171.8877 | 332.0348 | 613.0549 | 59.199 | 19.0641 | 59.199 | 153.5162 | 9790.9674 | 367.5566 |  |  | 24.0025 | 1.0391 | 45.4707 | 4084.7722 | 1967.7948 | 2116.9774 | 945.0897 | 23.6726 | 14.8345 | 16.2832 | 12.9745 | 12.5559 | 7.115 | 3445.3945 | 7644.1923 | 11701.1954 | 2443.1957 | 4998.6607 | 9386.5473 | 0.096772 | 0.12138 | 0.10478 | 22.3581 | 12.5911 | 14.9669 | 17.3959 | 79.579 | 240.4507 | 139.3103 | 107.4801 | 70.5572 | 99.22% | 98.82% | 98.36% | 99.29% | 98.41% | 97.44% | 124.0034 | 98.8596 | 114.5261 |  |  |  | 31 | 30 | 17 | 2418 | 1440 | 408 | 4266 | 108.6158 | 19 | 59 | 153 | 59 | 96.7% | 0.10593 | 0.10585 | 54.7903 | 49.9162 | 125.5394 | 59.2001 | 96.7% | 3969.8617 | 98.51% | 98.71% | 84.99% |  |  | 98.45% | 1.0391
2020-01-21 | 175.6524 | 152.0267 | 152.0267 | 137.0384 | 120.6292 | 14.0189 | 14.0189 | 3469.8446 | 1173.2987 | 332.4346 | 613.1368 | 57.1742 | 18.5368 | 57.6342 | 148.5241 | 9429.0266 | 362.7331 |  |  | 23.9495 | 1.0412 | 44.2109 | 4082.9814 | 1964.1113 | 2118.8701 | 945.5714 | 23.6257 | 14.9883 | 16.4519 | 12.9502 | 12.5711 | 7.1236 | 3310.0436 | 7345.7488 | 11247.9882 | 2349.0103 | 4802.8173 | 9021.4316 | 0.097588 | 0.12257 | 0.10528 | 22.3133 | 12.7069 | 15.1137 | 17.5959 | 80.897 | 242.8342 | 138.1683 | 106.7878 | 70.4504 | 99.21% | 98.8% | 98.35% | 99.25% | 98.32% | 97.31% | 122.9658 | 97.9042 | 113.9818 |  |  |  | 30.9048 | 30 | 17 | 2410.5714 | 1440 | 408 | 4258.5714 | 106.4799 | 19.1905 | 59.6667 | 153.7619 | 59.1905 | 96.69% | 0.10681 | 0.10677 | 55.0658 | 50.1339 | 124.7536 | 59.5388 | 96.69% | 3818.0076 | 98.5% | 98.64% | 84.98% |  |  | 98.44% | 1.0412
2020-01-20 | 174.966 | 151.1795 | 151.1795 | 135.9832 | 119.5219 | 13.9617 | 13.9617 | 3474.3065 | 1194.604 | 338.4711 | 613.1718 | 54.9706 | 18.9243 | 59.4764 | 145.0863 | 9154.1498 | 360.6056 |  |  | 23.9515 | 1.0411 | 45.1586 | 4087.4783 | 1941.2314 | 2146.2468 | 951.6429 | 23.7865 | 15.1963 | 16.5657 | 12.7993 | 12.7993 | 7.253 | 3199.1991 | 7140.515 | 11001.9951 | 2285.342 | 4653.5307 | 8794.7623 | 0.096716 | 0.12495 | 0.10704 | 22.2931 | 12.6751 | 15.1293 | 18.2478 | 87.7187 | 247.7266 | 137.779 | 106.6494 | 70.5425 | 99.17% | 98.72% | 98.35% | 99.2% | 98.12% | 97.18% | 124.074 | 96.0409 | 112.104 |  |  |  | 30 | 30 | 17 | 2340 | 1440 | 408 | 4188 | 105.4947 | 21 | 66 | 161 | 61 | 96.75% | 0.1074 | 0.10743 | 55.5485 | 50.0976 | 124.5021 | 58.6062 | 96.75% | 3733.7745 | 98.53% | 98.53% | 85% |  |  | 98.47% | 1.0411
2020-01-19 | 174.6265 | 150.8079 | 150.8079 | 135.581 | 118.8461 | 13.9905 | 13.9905 | 3472.4362 | 1193.9609 | 338.2889 | 612.497 | 48.0079 | 16.5273 | 51.943 | 126.7095 | 9088.4059 | 361.4638 |  |  | 23.953 | 1.041 | 39.4387 | 4084.9332 | 1940.1864 | 2144.7468 | 950.7859 | 23.8187 | 15.2268 | 16.6966 | 12.7924 | 12.7924 | 7.249 | 3188.1213 | 7126.415 | 10992.4304 | 2276.5048 | 4640.4192 | 8781.9052 | 0.096906 | 0.12533 | 0.10789 | 22.345 | 12.7151 | 15.2713 | 15.9888 | 76.7786 | 216.5362 | 137.4268 | 106.2616 | 69.9471 | 99.27% | 98.88% | 98.56% | 99.3% | 98.35% | 97.53% | 123.8311 | 95.749 | 111.2244 |  |  |  | 30 | 30 | 17 | 2340 | 1440 | 408 | 4188 | 104.9432 | 21 | 66 | 161 | 61 | 97.15% | 0.10776 | 0.10775 | 55.7421 | 50.3314 | 124.1765 | 51.2994 | 97.15% | 3723.076 | 98.71% | 98.71% | 85.01% |  |  | 98.66% | 1.041
2020-01-18 | 174.8308 | 151.1952 | 151.1952 | 136.1611 | 119.4479 | 13.9568 | 13.9568 | 3462.2626 | 1190.4628 | 337.2978 | 610.1619 | 57.5198 | 19.8019 | 62.2346 | 151.8146 | 9530.8943 | 360.4948 |  |  | 23.8516 | 1.0451 | 47.2528 | 4072.4245 | 1934.502 | 2137.9224 | 947.4597 | 23.6356 | 15.0341 | 16.5793 | 12.755 | 12.755 | 7.2278 | 3325.1329 | 7424.8947 | 11445.4571 | 2375.0946 | 4837.6456 | 9146.9882 | 0.097105 | 0.12595 | 0.10968 | 22.2768 | 12.6162 | 15.2467 | 18.3794 | 88.327 | 249.3282 | 137.2798 | 105.8443 | 68.8718 | 99.17% | 98.71% | 98.34% | 99.23% | 98.17% | 97.27% | 123.5774 | 95.2796 | 109.4073 |  |  |  | 30 | 30 | 17 | 2340 | 1440 | 408 | 4188 | 105.5475 | 21 | 66 | 161 | 61 | 96.72% | 0.10835 | 0.10825 | 55.249 | 50.1398 | 123.5501 | 59.012 | 96.72% | 3881.543 | 98.52% | 98.58% | 85.02% |  |  | 98.46% | 1.0451
2020-01-17 | 174.2422 | 150.4325 | 150.4325 | 135.3185 | 118.4204 | 13.9979 | 13.9979 | 3472.1356 | 1193.8575 | 338.2596 | 613.3621 | 62.874 | 21.6451 | 68.0276 | 165.9461 | 9670.6039 | 359.6265 |  |  | 23.8571 | 1.0449 | 51.6512 | 4085.4977 | 1940.0185 | 2145.4793 | 951.6217 | 23.8097 | 15.114 | 16.7365 | 12.7913 | 12.7913 | 7.2484 | 3368.1621 | 7508.3474 | 11557.5673 | 2406.8187 | 4896.6759 | 9243.6623 | 0.097979 | 0.12762 | 0.11223 | 22.3296 | 12.6113 | 15.2828 | 19.8777 | 95.6364 | 270.3975 | 136.4135 | 104.7343 | 67.483 | 99.1% | 98.61% | 98.2% | 99.17% | 98.05% | 97.07% | 122.4746 | 94.0324 | 106.9191 |  |  |  | 30 | 30 | 17 | 2340 | 1440 | 408 | 4188 | 104.3832 | 21 | 66 | 161 | 61 | 96.47% | 0.10974 | 0.10956 | 55.6601 | 50.2237 | 122.5125 | 63.8942 | 96.47% | 3928.9836 | 98.4% | 98.48% | 84.99% |  |  | 98.33% | 1.0449
2020-01-16 | 170.7218 | 146.9361 | 146.9361 | 131.7539 | 115.2753 | 13.8246 | 13.8246 | 3467.1482 | 1200.1897 | 147.6233 | 612.4932 | 66.3581 | 24.4442 | 79.0452 | 337.3704 | 9556.28 | 352.4447 |  |  | 23.8717 | 1.0443 | 56.6686 | 4079.6413 | 2119.3351 | 1960.3062 | 760.1165 | 23.7857 | 15.1823 | 16.7104 | 13.9736 | 12.8592 | 3.1634 | 3629.7533 | 9236.1617 | 11380.9519 | 2470.678 | 5584.8689 | 10234.0212 | 0.10991 | 0.13704 | 0.05487 | 23.3737 | 15.3885 | 18.5768 | 23.8759 | 97.8938 | 216.5712 | 132.7732 | 97.9913 | 60.2068 | 99.01% | 98.58% | 96.7% | 99.03% | 98.25% | 97.88% | 109.1817 | 87.5635 | 218.6986 |  |  |  | 32.6 | 30 | 7.38 | 2542.8 | 1440 | 177.12 | 4159.92 | 101.3849 | 18.4 | 59.5 | 253.95 | 49.95 | 96.22% | 0.10979 | 0.11696 | 55.6783 | 57.3389 | 119.4586 | 68.1633 | 96.22% | 3879.2335 | 98.29% | 98.6% | 84.99% |  |  | 98.22% | 1.0443
2020-01-15 | 170.2487 | 146.327 | 146.327 | 131.0253 | 114.5365 | 13.8611 | 13.8611 | 3473.4847 | 1206.7694 | 44.2482 | 615.2678 | 76.5806 | 29.588 | 97.4663 | 529.1026 | 9925.716 | 352.5466 |  |  | 23.8749 | 1.0442 | 59.5337 | 4088.7525 | 2222.467 | 1866.2855 | 659.516 | 23.9216 | 15.3018 | 16.858 | 14.6536 | 12.9297 | 0.94818 | 3805.4179 | 10590.1549 | 11313.7156 | 2519.3036 | 6079.3768 | 10943.9663 | 0.11594 | 0.14226 | 0.017417 | 24.0118 | 17.3363 | 20.939 | 29.7177 | 111.4828 | 95.1901 | 131.9782 | 94.9055 | 56.8455 | 98.83% | 98.4% | 95.17% | 98.82% | 98.17% | 99.13% | 103.5047 | 84.3543 | 688.9854 |  |  |  | 34 | 30 | 2.2 | 2652 | 1440 | 52.8 | 4144.8 | 100.5897 | 17 | 56 | 304 | 44 | 95.63% | 0.1086 | 0.12383 | 56.0814 | 62.2871 | 118.9177 | 79.1191 | 95.63% | 3863.4764 | 98.02% | 98.66% | 84.95% |  |  | 97.93% | 1.0442
2020-01-14
2020-01-13 | 190.8183 | 168.1409 | 168.1409 | 156.461 | 144.0577 | 13.861 | 13.861 | 3476.6028 | 1207.8527 | 44.2879 | 613.3272 | 42.2024 | 16.3055 | 53.7121 | 291.5801 | 8947.1025 | 399.4844 |  |  | 23.8219 | 1.0463 | 32.8081 | 4089.9299 | 2224.4621 | 1865.4678 | 657.6151 | 22.6774 | 11.6799 | 12.4593 | 14.6668 | 12.9413 | 0.94903 | 3648.7442 | 10251.8 | 10971.0207 | 2409.2822 | 5852.3249 | 10603.2839 | 0.099875 | 0.11336 | 0.011704 | 22.7609 | 13.2542 | 15.5457 | 17.1753 | 64.0081 | 54.3028 | 153.6538 | 119.4469 | 84.8399 | 99.32% | 99.08% | 97.25% | 99.29% | 98.91% | 99.49% | 120.1498 | 105.8553 | 1025.2654 |  |  |  | 34 | 30 | 2.2 | 2652 | 1440 | 52.8 | 4144.8 | 130.192 | 17 | 56 | 304 | 44 | 97.48% | 0.090084 | 0.10344 | 46.8166 | 51.5608 | 142.8458 | 45.5406 | 97.48% | 3709.8576 | 98.86% | 99.2% | 85% |  |  | 98.81% | 1.0463
2020-01-12 | 194.3111 | 171.673 | 171.673 | 159.9968 | 147.7223 | 13.8413 | 13.8413 | 3470.6036 | 1215.9779 | 81.0652 | 612.318 | 44.6805 | 17.4837 | 54.3937 | 293.3374 | 9219.2429 | 407.0086 |  |  | 23.8355 | 1.0458 | 36.859 | 4082.9217 | 2173.5605 | 1909.3611 | 693.3832 | 22.6381 | 11.6762 | 12.2514 | 14.3312 | 13.0283 | 1.7371 | 3606.1068 | 9834.704 | 11097.8919 | 2415.118 | 5712.6224 | 10440.8702 | 0.095361 | 0.11014 | 0.020347 | 22.512 | 12.6464 | 14.68 | 17.942 | 66.817 | 101.4976 | 157.1626 | 123.7025 | 89.2806 | 99.28% | 99.05% | 97.19% | 99.26% | 98.83% | 99.03% | 125.8376 | 108.9513 | 589.756 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 133.9378 | 18 | 56 | 302 | 46 | 97.37% | 0.088088 | 0.098787 | 46.5657 | 49.8383 | 146.1191 | 47.4911 | 97.37% | 3757.9108 | 98.81% | 99.08% | 85% |  |  | 98.76% | 1.0458
2020-01-11 | 195.0838 | 172.6694 | 172.6694 | 161.0654 | 148.8373 | 13.8247 | 13.8247 | 3471.3629 | 1216.244 | 81.0829 | 612.0552 | 50.4145 | 19.7274 | 61.3742 | 330.9821 | 9668.5595 | 408.4405 |  |  | 23.8151 | 1.0466 | 41.5892 | 4083.4182 | 2174.0361 | 1909.3821 | 693.1382 | 22.4144 | 11.604 | 12.2786 | 14.3343 | 13.0312 | 1.7375 | 3740.0312 | 10194.9412 | 11501.6838 | 2505.3368 | 5923.564 | 10822.0593 | 0.095178 | 0.11023 | 0.020508 | 22.2866 | 12.5699 | 14.7212 | 19.5352 | 72.7803 | 110.6006 | 157.6239 | 123.7317 | 88.6713 | 99.21% | 98.96% | 96.94% | 99.22% | 98.77% | 98.98% | 126.0799 | 108.8674 | 585.1415 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 135.0031 | 18 | 56 | 302 | 46 | 97.13% | 0.088046 | 0.098706 | 46.2971 | 49.5776 | 146.1189 | 51.7223 | 97.13% | 3897.223 | 98.71% | 99.04% | 85.01% |  |  | 98.65% | 1.0466
2020-01-10 | 195.3908 | 173.0294 | 173.0294 | 161.5259 | 149.0999 | 13.8672 | 13.8672 | 3469.1749 | 1215.4773 | 81.0318 | 613.5557 | 52.6093 | 20.5862 | 64.0461 | 345.3912 | 9926.2826 | 409.53 |  |  | 23.9871 | 1.0397 | 43.3997 | 4082.7306 | 2172.6657 | 1910.0649 | 694.5876 | 22.3614 | 11.5036 | 12.298 | 14.3253 | 13.023 | 1.7364 | 3816.9509 | 10384.2593 | 11710.0846 | 2557.8036 | 6040.4459 | 11020.633 | 0.094469 | 0.10961 | 0.020499 | 22.2339 | 12.4458 | 14.6946 | 19.823 | 73.9401 | 112.5155 | 157.6568 | 123.5284 | 88.0695 | 99.2% | 98.94% | 96.87% | 99.22% | 98.78% | 98.98% | 127.0258 | 109.481 | 585.4075 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 135.2892 | 18 | 56 | 302 | 46 | 97.07% | 0.087478 | 0.098045 | 46.163 | 49.3742 | 145.9385 | 52.526 | 97.07% | 3975.6714 | 98.68% | 99.04% | 84.97% |  |  | 98.63% | 1.0397
2020-01-09 | 194.5086 | 172.2013 | 172.2013 | 160.6802 | 148.4145 | 13.9103 | 13.9103 | 3465.5513 | 1214.2077 | 80.9472 | 611.9683 | 52.854 | 20.682 | 64.3439 | 346.9977 | 9887.8864 | 407.1447 |  |  | 24.1239 | 1.0342 | 43.6016 | 4077.5196 | 2170.3963 | 1907.1232 | 692.9155 | 22.3073 | 11.5211 | 12.3213 | 14.3103 | 13.0094 | 1.7346 | 3794.1152 | 10329.8576 | 11650.3253 | 2542.2212 | 6006.1851 | 10963.6298 | 0.094365 | 0.10955 | 0.020489 | 22.2255 | 12.4979 | 14.7775 | 19.9111 | 74.2373 | 112.9111 | 156.837 | 122.8213 | 87.5539 | 99.19% | 98.93% | 96.84% | 99.22% | 98.76% | 98.97% | 127.1659 | 109.544 | 585.6687 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 134.4641 | 18 | 56 | 302 | 46 | 97.04% | 0.087402 | 0.097958 | 46.1496 | 49.5009 | 145.1541 | 52.7444 | 97.04% | 3952.5772 | 98.66% | 99.03% | 84.99% |  |  | 98.62% | 1.0342
2020-01-08 | 194.25 | 171.8147 | 171.8147 | 160.3756 | 148.0658 | 14.0426 | 14.0426 | 3468.1473 | 1215.1173 | 81.0078 | 612.3667 | 52.722 | 20.6303 | 64.1833 | 346.1311 | 9850.3426 | 407.0123 |  |  | 24.0791 | 1.036 | 43.4927 | 4080.514 | 2172.0222 | 1908.4919 | 693.3746 | 22.4352 | 11.4391 | 12.2543 | 14.321 | 13.0191 | 1.7359 | 3783.638 | 10301.8666 | 11618.8755 | 2535.1798 | 5989.7293 | 10933.9765 | 0.094853 | 0.11017 | 0.020614 | 22.3285 | 12.3959 | 14.6827 | 19.9659 | 74.4394 | 113.2145 | 156.417 | 122.4249 | 87.2389 | 99.19% | 98.93% | 96.83% | 99.21% | 98.76% | 98.96% | 126.5119 | 108.9205 | 582.1187 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 134.0415 | 18 | 56 | 302 | 46 | 97.04% | 0.087877 | 0.098486 | 46.1286 | 49.4072 | 144.8341 | 52.8885 | 97.04% | 3941.7092 | 98.66% | 99.03% | 84.99% |  |  | 98.62% | 1.036
2020-01-07 | 193.464 | 171.0705 | 171.0705 | 159.5256 | 147.2201 | 13.9688 | 13.9688 | 3471.0281 | 1216.1266 | 81.0751 | 612.4115 | 51.5362 | 19.8027 | 64.861 | 330.6188 | 9593.5597 | 404.9512 |  |  | 24.2311 | 1.03 | 42.8495 | 4083.4396 | 2173.8264 | 1909.6133 | 693.4866 | 22.3936 | 11.5448 | 12.1788 | 14.3329 | 13.0299 | 1.7373 | 3690.7378 | 10049.2244 | 11335.8381 | 2472.6186 | 5842.7357 | 10666.7099 | 0.094609 | 0.10961 | 0.020398 | 22.2645 | 12.5016 | 14.5896 | 19.5513 | 76.7315 | 110.2947 | 156.0344 | 122.4399 | 87.7236 | 99.2% | 98.89% | 96.9% | 99.21% | 98.69% | 98.97% | 126.8381 | 109.4825 | 588.3012 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 133.2818 | 20.125 | 65.9167 | 336 | 52.375 | 97.03% | 0.087534 | 0.09813 | 46.1172 | 49.3557 | 144.7102 | 52.7367 | 97.03% | 3844.7844 | 98.66% | 99% | 85% |  |  | 98.62% | 1.03
2020-01-06 | 191.9944 | 169.4657 | 169.4657 | 157.7899 | 145.4683 | 13.887 | 13.887 | 3470.3914 | 1215.9036 | 81.0602 | 612.6488 | 48.1007 | 18.3657 | 61.219 | 306.0952 | 8999.2605 | 401.4136 |  |  | 24.1875 | 1.0317 | 40.1007 | 4083.0402 | 2173.4276 | 1909.6126 | 693.709 | 22.5287 | 11.6757 | 12.3346 | 14.3303 | 13.0275 | 1.737 | 3482.7704 | 9479.9197 | 10693.7186 | 2333.2799 | 5512.7663 | 10062.4577 | 0.095218 | 0.10973 | 0.020144 | 22.4011 | 12.6417 | 14.7685 | 19.2442 | 76.8729 | 108.4076 | 155.2684 | 122.483 | 88.9603 | 99.21% | 98.89% | 96.96% | 99.18% | 98.61% | 98.92% | 126.0267 | 109.3574 | 595.7026 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 131.5325 | 21 | 70 | 350 | 55 | 97.06% | 0.087851 | 0.09855 | 46.5391 | 49.8113 | 144.5312 | 52.2433 | 97.06% | 3627.7961 | 98.67% | 98.95% | 85% |  |  | 98.63% | 1.0317
2020-01-05 | 191.9604 | 169.509 | 169.509 | 157.8333 | 145.4372 | 13.8661 | 13.8661 | 3474.2416 | 1217.2525 | 81.1502 | 613.6889 | 48.588 | 18.5518 | 61.8393 | 309.1964 | 9102.2283 | 401.1421 |  |  | 24.1001 | 1.0352 | 40.507 | 4087.9305 | 2175.8389 | 1912.0916 | 694.839 | 22.4514 | 11.6757 | 12.3195 | 14.3462 | 13.042 | 1.7389 | 3516.416 | 9568.3101 | 10792.6743 | 2355.9559 | 5565.2472 | 10155.9329 | 0.095698 | 0.1104 | 0.020332 | 22.2831 | 12.6154 | 14.7138 | 19.3384 | 77.2644 | 108.9846 | 155.1816 | 122.2881 | 88.5355 | 99.21% | 98.89% | 96.96% | 99.18% | 98.61% | 98.93% | 125.3939 | 108.6958 | 590.2115 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 131.559 | 21 | 70 | 350 | 55 | 97.06% | 0.088344 | 0.099089 | 46.4466 | 49.6123 | 144.3309 | 52.506 | 97.06% | 3662.5684 | 98.67% | 98.96% | 84.99% |  |  | 98.63% | 1.0352
2020-01-04 | 189.1067 | 167.4001 | 167.4001 | 156.1605 | 144.1043 | 13.8307 | 13.8307 | 3418.5065 | 1197.7249 | 79.8483 | 602.9294 | 51.0711 | 19.4999 | 64.9996 | 324.9978 | 9321.5007 | 389.7673 |  |  | 24.0823 | 1.0359 | 42.5771 | 4021.4359 | 2140.9333 | 1880.5026 | 682.7777 | 21.7066 | 11.2396 | 11.9256 | 14.116 | 12.8328 | 1.711 | 3600.0709 | 9801.2736 | 11056.2544 | 2411.8726 | 5698.9401 | 10403.5754 | 0.095909 | 0.11098 | 0.020631 | 22.0832 | 12.4558 | 14.6242 | 19.5503 | 78.089 | 110.1089 | 152.4609 | 119.7799 | 85.9088 | 99.19% | 98.86% | 96.88% | 99.19% | 98.63% | 98.94% | 125.1182 | 108.1282 | 581.6393 |  |  |  | 33 | 30 | 4 | 2574 | 1440 | 96 | 4110 | 130.1907 | 21 | 70 | 350 | 55 | 96.98% | 0.088687 | 0.099431 | 44.8718 | 49.1631 | 141.3713 | 53.0712 | 96.98% | 3750.2134 | 98.64% | 98.97% | 85.01% |  |  | 98.61% | 1.0359
2020-01-03 | 192.6595 | 170.3889 | 170.3889 | 158.8653 | 146.4451 | 13.8824 | 13.8824 | 3465.3483 | 1211.8855 | 81.8949 | 610.6993 | 51.0603 | 19.4738 | 64.8089 | 324.5896 | 9489.8479 | 403.2565 |  |  | 24.2081 | 1.0309 | 42.5388 | 4076.0476 | 2171.568 | 1904.4797 | 692.5942 | 22.2706 | 11.5236 | 12.3028 | 14.318 | 12.9845 | 1.7549 | 3632.0907 | 9874.0392 | 11154.6221 | 2432.1318 | 5746.1245 | 10488.3168 | 0.094872 | 0.10941 | 0.020568 | 22.2118 | 12.5221 | 14.7824 | 19.5437 | 77.7559 | 111.3373 | 155.5785 | 122.3381 | 87.9542 | 99.2% | 98.87% | 96.91% | 99.2% | 98.65% | 98.94% | 126.4868 | 109.6771 | 583.4252 |  |  |  | 32.9621 | 29.8921 | 4.04 | 2571.0425 | 1434.82 | 96.96 | 4102.8225 | 132.5825 | 20.8333 | 69.3333 | 347.25 | 54.625 | 97.01% | 0.087636 | 0.098201 | 46.0971 | 49.5163 | 144.3787 | 53.0847 | 97.01% | 3781.4738 | 98.65% | 98.98% | 85.02% |  |  | 98.61% | 1.0309
2020-01-02 | 191.4824 | 169.1126 | 169.1126 | 157.4404 | 145.116 | 13.814 | 13.814 | 3463.8422 | 1157.341 | 104.7138 | 612.3592 | 50.7315 | 18.7486 | 59.5544 | 313.2118 | 9060.1204 | 400.788 |  |  | 23.9363 | 1.0417 | 41.2844 | 4076.2015 | 2201.7874 | 1874.4141 | 717.0731 | 22.3698 | 11.6722 | 12.2848 | 14.5173 | 12.4001 | 2.2439 | 3519.2432 | 9103.1089 | 10606.1868 | 2335.6894 | 5452.5139 | 9816.3939 | 0.097631 | 0.10545 | 0.025987 | 22.4792 | 12.7246 | 14.3275 | 20.0746 | 72.6673 | 148.3179 | 154.8988 | 122.4977 | 89.9483 | 99.2% | 98.91% | 96.81% | 99.14% | 98.67% | 98.49% | 122.9118 | 113.7978 | 461.7707 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 131.2041 | 17 | 54 | 284 | 46 | 96.88% | 0.08867 | 0.098078 | 46.3268 | 49.5313 | 144.2914 | 55.9103 | 96.88% | 3603.2303 | 98.59% | 98.88% | 84.98% |  |  | 98.54% | 1.0417
2020-01-01 | 191.8067 | 169.3963 | 169.3963 | 157.8461 | 145.3043 | 13.8065 | 13.8065 | 3468.2877 | 1158.8263 | 104.8482 | 611.7405 | 51.5025 | 19.0335 | 60.4594 | 317.9718 | 9258.0734 | 401.4005 |  |  | 23.9902 | 1.0396 | 41.9118 | 4080.0283 | 2204.6132 | 1875.4151 | 716.5887 | 22.4104 | 11.5503 | 12.2324 | 14.5359 | 12.416 | 2.2467 | 3580.9555 | 9274.1005 | 10809.1206 | 2376.0926 | 5550.9979 | 10002.456 | 0.097484 | 0.10548 | 0.026141 | 22.4926 | 12.5879 | 14.2843 | 20.0172 | 72.4052 | 147.6535 | 155.0097 | 122.362 | 89.3462 | 99.2% | 98.91% | 96.82% | 99.16% | 98.7% | 98.52% | 123.0976 | 113.7622 | 459.0448 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 131.5692 | 17 | 54 | 284 | 46 | 96.89% | 0.088629 | 0.098 | 46.1931 | 49.3647 | 144.2683 | 55.7218 | 96.89% | 3667.4429 | 98.6% | 98.91% | 85.01% |  |  | 98.54% | 1.0396
2019-12-31 | 194.4419 | 171.9931 | 171.9931 | 160.3341 | 148.0442 | 13.8852 | 13.8852 | 3471.9785 | 1160.0595 | 104.9598 | 612.9181 | 51.5079 | 19.0355 | 60.4658 | 318.0051 | 9517.6351 | 407.5834 |  |  | 23.6686 | 1.0525 | 41.9162 | 4084.8966 | 2206.9593 | 1877.9373 | 717.8778 | 22.4488 | 11.6591 | 12.2617 | 14.5514 | 12.4292 | 2.2491 | 3670.8066 | 9504.9609 | 11078.1906 | 2435.7099 | 5689.8155 | 10251.4466 | 0.097399 | 0.10539 | 0.026119 | 22.4893 | 12.6785 | 14.2786 | 19.7942 | 71.6043 | 146.0367 | 157.249 | 124.1317 | 90.6367 | 99.22% | 98.94% | 96.9% | 99.19% | 98.74% | 98.58% | 123.2047 | 113.8631 | 459.4433 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 134.1034 | 17 | 54 | 284 | 46 | 96.97% | 0.088551 | 0.097914 | 46.3695 | 49.4464 | 146.2301 | 55.1042 | 96.97% | 3759.2475 | 98.63% | 98.95% | 85% |  |  | 98.56% | 1.0525
2019-12-30 | 192.797 | 170.3453 | 170.3453 | 158.6332 | 146.1865 | 13.7624 | 13.7624 | 3475.2811 | 1161.1629 | 105.0596 | 612.2993 | 51.1923 | 18.9189 | 60.0953 | 316.0567 | 9233.8759 | 404.7704 |  |  | 23.6992 | 1.0513 | 41.6594 | 4087.5804 | 2209.0585 | 1878.5219 | 717.359 | 22.4517 | 11.7122 | 12.3651 | 14.5652 | 12.441 | 2.2513 | 3579.7635 | 9276.9228 | 10814.4471 | 2374.9976 | 5550.6419 | 10006.4184 | 0.098138 | 0.1061 | 0.02624 | 22.4737 | 12.7357 | 14.4175 | 20.1712 | 72.9331 | 148.6616 | 156.0283 | 123.2741 | 90.1956 | 99.2% | 98.92% | 96.84% | 99.15% | 98.69% | 98.51% | 122.2767 | 113.1027 | 457.3131 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 132.3651 | 17 | 54 | 284 | 46 | 96.91% | 0.089182 | 0.098624 | 46.5289 | 49.6269 | 145.2239 | 56.1351 | 96.91% | 3666.7477 | 98.6% | 98.9% | 85.02% |  |  | 98.53% | 1.0513
2019-12-29 | 192.2294 | 169.7764 | 169.7764 | 158.0451 | 145.691 | 13.7728 | 13.7728 | 3474.812 | 1161.0062 | 105.0454 | 612.8562 | 51.315 | 18.9642 | 60.2393 | 316.8141 | 9279.2506 | 404.3373 |  |  | 23.7486 | 1.0493 | 41.7592 | 4087.6682 | 2208.7604 | 1878.9078 | 717.9016 | 22.453 | 11.7312 | 12.2656 | 14.5633 | 12.4394 | 2.251 | 3597.1168 | 9317.0328 | 10859.698 | 2386.735 | 5576.3223 | 10049.0031 | 0.098339 | 0.1065 | 0.02641 | 22.4723 | 12.7496 | 14.2839 | 20.079 | 72.6226 | 148.0833 | 155.3912 | 122.5576 | 89.4344 | 99.21% | 98.92% | 96.85% | 99.16% | 98.7% | 98.53% | 122.0266 | 112.6753 | 454.3813 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 131.9076 | 17 | 54 | 284 | 46 | 96.92% | 0.089442 | 0.098892 | 46.4498 | 49.5058 | 144.5614 | 55.8906 | 96.92% | 3684.0763 | 98.61% | 98.91% | 85.01% |  |  | 98.54% | 1.0493
2019-12-28 | 194.0189 | 171.5798 | 171.5798 | 159.9479 | 147.5496 | 13.8378 | 13.8378 | 3474.5667 | 1160.9243 | 105.038 | 612.6621 | 52.4685 | 19.3906 | 61.5935 | 323.9363 | 9595.6546 | 407.9821 |  |  | 23.5223 | 1.0585 | 42.698 | 4087.2288 | 2208.6044 | 1878.6244 | 717.7002 | 22.4391 | 11.6319 | 12.316 | 14.5622 | 12.4385 | 2.2508 | 3707.3726 | 9604.6451 | 11195.7786 | 2459.7641 | 5747.7567 | 10359.5929 | 0.09833 | 0.10661 | 0.026551 | 22.4625 | 12.6452 | 14.3489 | 20.0944 | 72.6682 | 148.1527 | 156.7597 | 123.4952 | 89.7326 | 99.21% | 98.93% | 96.87% | 99.18% | 98.74% | 98.57% | 122.0378 | 112.5565 | 451.9583 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 133.7607 | 17 | 54 | 284 | 46 | 96.94% | 0.089496 | 0.098928 | 46.387 | 49.4566 | 145.6191 | 55.9282 | 96.94% | 3797.1662 | 98.62% | 98.94% | 85.01% |  |  | 98.54% | 1.0585
2019-12-27 | 195.0051 | 172.2923 | 172.2923 | 160.5138 | 148.0277 | 13.7171 | 13.7171 | 3472.631 | 1160.2775 | 104.9795 | 612.7909 | 47.1629 | 17.4298 | 55.3651 | 291.1794 | 9048.3458 | 410.6511 |  |  | 22.909 | 1.084 | 38.3803 | 4085.4219 | 2207.374 | 1878.0479 | 717.7704 | 22.7128 | 11.7785 | 12.4362 | 14.5541 | 12.4315 | 2.2496 | 3510.2419 | 9095.0578 | 10603.2831 | 2328.7413 | 5442.4153 | 9810.6322 | 0.099612 | 0.10716 | 0.026232 | 22.7501 | 12.8083 | 14.4857 | 19.5267 | 70.6043 | 143.9247 | 158.375 | 125.7507 | 92.9564 | 99.25% | 98.98% | 97.03% | 99.16% | 98.7% | 98.53% | 120.4669 | 111.983 | 457.4548 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 134.2878 | 17 | 54 | 284 | 46 | 97.09% | 0.090287 | 0.099916 | 46.9275 | 50.0441 | 147.8208 | 54.3425 | 97.09% | 3595.2655 | 98.69% | 98.91% | 85% |  |  | 98.58% | 1.084
2019-12-26 | 193.9426 | 171.1544 | 171.1544 | 159.0486 | 146.3067 | 13.7154 | 13.7154 | 3470.8792 | 1159.6922 | 104.9265 | 613.2641 | 41.5461 | 15.354 | 48.7716 | 256.5023 | 7822.5866 | 407.4654 |  |  | 22.3344 | 1.1085 | 33.8095 | 4084.1433 | 2206.2604 | 1877.8829 | 718.1907 | 22.7882 | 12.1058 | 12.4814 | 14.5468 | 12.4253 | 2.2484 | 3067.7992 | 7942.7479 | 9257.8276 | 2035.5273 | 4754.9356 | 8566.7334 | 0.10158 | 0.10772 | 0.025585 | 22.8339 | 13.1623 | 14.5238 | 20.1137 | 72.7608 | 148.4009 | 158.7322 | 127.8553 | 97.411 | 99.25% | 98.97% | 97.01% | 99.01% | 98.47% | 98.27% | 118.1291 | 111.3964 | 469.0165 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 132.5904 | 17 | 54 | 284 | 46 | 97.07% | 0.091389 | 0.10134 | 47.3755 | 50.52 | 149.3897 | 55.9941 | 97.07% | 3141.5795 | 98.68% | 98.72% | 84.98% |  |  | 98.53% | 1.1085
2019-12-25 | 186.7515 | 164.5964 | 164.5964 | 153.035 | 140.9279 | 13.612 | 13.612 | 3445.8401 | 1152.3799 | 103.3314 | 608.6023 | 52.2446 | 19.3376 | 61.5115 | 322.971 | 8957.2483 | 387.939 |  |  | 23.9762 | 1.0401 | 42.5468 | 4054.4425 | 2190.1288 | 1864.3137 | 711.9337 | 22.1551 | 11.5613 | 12.1806 | 14.4404 | 12.3469 | 2.2142 | 3497.2384 | 9058.5181 | 10541.6813 | 2321.3278 | 5421.5353 | 9762.646 | 0.099764 | 0.10846 | 0.026727 | 22.4435 | 12.7157 | 14.3499 | 20.6912 | 75.0451 | 151.5177 | 150.552 | 118.4036 | 86.1711 | 99.17% | 98.87% | 96.69% | 99.11% | 98.62% | 98.45% | 120.2834 | 110.6381 | 448.9881 |  |  |  | 32.0863 | 27.4346 | 4.92 | 2502.7275 | 1316.86 | 118.08 | 3937.6675 | 127.2548 | 17.0417 | 54.2083 | 284.625 | 46.0417 | 96.77% | 0.090861 | 0.10048 | 45.8971 | 49.509 | 139.996 | 57.5413 | 96.77% | 3581.264 | 98.54% | 98.85% | 84.99% |  |  | 98.49% | 1.0401
2019-12-24 | 189.3694 | 166.9254 | 166.9254 | 155.1275 | 142.8035 | 13.7279 | 13.7279 | 3469.7364 | 1184.788 | 84.6277 | 612.8849 | 49.5581 | 18.9797 | 62.2112 | 315.2738 | 8866.9443 | 397.4071 |  |  | 23.7596 | 1.0488 | 40.9684 | 4082.6213 | 2200.3206 | 1882.3007 | 697.5126 | 22.444 | 11.7979 | 12.3188 | 14.5076 | 12.6942 | 1.8135 | 3451.5686 | 9208.6975 | 10436.7096 | 2294.3836 | 5417.7536 | 9797.0963 | 0.099425 | 0.11047 | 0.021656 | 22.4727 | 12.949 | 14.6815 | 20.8155 | 78.743 | 121.7215 | 153.0425 | 120.5208 | 87.8284 | 99.17% | 98.85% | 96.78% | 99.09% | 98.55% | 98.76% | 120.6941 | 108.6245 | 554.1141 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 129.0478 | 18 | 59 | 299 | 47 | 96.91% | 0.090517 | 0.1013 | 46.5608 | 50.1032 | 142.5599 | 56.0066 | 96.91% | 3543.8932 | 98.6% | 98.86% | 84.99% |  |  | 98.53% | 1.0488
2019-12-23 | 187.3755 | 164.9302 | 164.9302 | 153.0267 | 140.5644 | 13.7903 | 13.7903 | 3469.4045 | 1184.6747 | 84.6196 | 613.1551 | 48.3273 | 18.5083 | 60.6662 | 307.4438 | 8426.6857 | 394.4869 |  |  | 23.7328 | 1.0499 | 39.9509 | 4082.5596 | 2200.1102 | 1882.4495 | 697.7747 | 22.4453 | 11.9036 | 12.3516 | 14.5062 | 12.6929 | 1.8133 | 3286.1317 | 8762.2936 | 9929.121 | 2184.7168 | 5156.8357 | 9321.4083 | 0.10051 | 0.11133 | 0.02165 | 22.4735 | 13.0618 | 14.7115 | 21.3375 | 80.7481 | 124.8728 | 151.5315 | 119.7073 | 87.9354 | 99.15% | 98.82% | 96.7% | 99.02% | 98.43% | 98.66% | 119.3906 | 107.7903 | 554.2692 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 126.7871 | 18 | 59 | 299 | 47 | 96.83% | 0.091354 | 0.10228 | 46.7004 | 50.2468 | 141.4946 | 57.4254 | 96.83% | 3373.6523 | 98.57% | 98.78% | 84.98% |  |  | 98.5% | 1.0499
2019-12-22 | 184.6496 | 162.4329 | 162.4329 | 150.7654 | 138.186 | 13.7451 | 13.7451 | 3468.5369 | 1184.3784 | 84.5985 | 612.5458 | 54.7351 | 20.9624 | 68.71 | 348.2082 | 8918.1751 | 386.5626 |  |  | 24.4975 | 1.0195 | 45.248 | 4081.0826 | 2199.56 | 1881.5227 | 697.1442 | 22.2166 | 11.6676 | 12.3029 | 14.5026 | 12.6898 | 1.8128 | 3469.9088 | 9248.2061 | 10477.3815 | 2307.3466 | 5444.2148 | 9837.2424 | 0.099652 | 0.11155 | 0.02219 | 22.258 | 12.8145 | 14.6743 | 22.2127 | 84.0921 | 130.092 | 148.3642 | 115.9765 | 83.2854 | 99.09% | 98.74% | 96.46% | 99.04% | 98.46% | 98.68% | 120.4189 | 107.579 | 540.7848 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 124.5186 | 18 | 59 | 299 | 47 | 96.6% | 0.091064 | 0.10182 | 46.1871 | 49.7467 | 137.7882 | 59.7957 | 96.6% | 3562.1283 | 98.46% | 98.79% | 84.99% |  |  | 98.44% | 1.0195
2019-12-21 | 179.7562 | 158.6411 | 158.6411 | 147.638 | 134.6312 | 12.7205 | 12.7205 | 3361.2368 | 1147.7394 | 81.9814 | 591.8808 | 65.8901 | 25.2345 | 82.7131 | 419.173 | 9441.1041 | 357.4673 |  |  | 24.6151 | 1.0149 | 54.4696 | 3953.1176 | 2131.516 | 1821.6016 | 673.8622 | 21.1151 | 11.003 | 11.7723 | 14.054 | 12.2972 | 1.7567 | 3602.9879 | 9598.8102 | 10870.2813 | 2396.6715 | 5652.0037 | 10208.1989 | 0.098622 | 0.11086 | 0.022435 | 22.1952 | 12.694 | 14.7791 | 24.8342 | 94.0662 | 145.5863 | 144.6209 | 112.5726 | 79.4689 | 98.95% | 98.54% | 95.89% | 98.96% | 98.34% | 98.57% | 121.6761 | 108.2428 | 534.8865 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 122.3258 | 18 | 59 | 299 | 47 | 96.06% | 0.090349 | 0.10094 | 43.8905 | 49.6683 | 133.6331 | 66.8755 | 96.06% | 3698.7734 | 98.22% | 98.7% | 85.03% |  |  | 98.25% | 1.0149
2019-12-20
2019-12-19 | 186.4683 | 164.7151 | 164.7151 | 153.4927 | 141.4298 | 13.5835 | 13.5835 | 3447.4008 | 1177.1613 | 84.0829 | 607.4394 | 47.4836 | 18.1852 | 59.6071 | 302.0766 | 9404.484 | 387.6485 |  |  | 24.4869 | 1.0199 | 39.2534 | 4054.8403 | 2186.1566 | 1868.6836 | 691.5224 | 21.7532 | 11.2225 | 12.2026 | 14.4142 | 12.6124 | 1.8018 | 3700.9354 | 9899.4774 | 11227.9683 | 2458.6117 | 5815.4535 | 10535.8557 | 0.098131 | 0.11018 | 0.022218 | 22.0097 | 12.4592 | 14.7353 | 17.9814 | 67.9059 | 104.7743 | 149.8061 | 116.7412 | 82.7089 | 99.26% | 98.98% | 97.13% | 99.27% | 98.83% | 99.01% | 122.2849 | 108.9079 | 540.1141 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 127.712 | 18 | 59 | 299 | 47 | 97.23% | 0.089842 | 0.1004 | 45.1782 | 49.2042 | 138.6083 | 48.3263 | 97.23% | 3801.8563 | 98.75% | 99.09% | 85.02% |  |  | 98.74% | 1.0199
2019-12-18 | 187.6634 | 165.7097 | 165.7097 | 154.3243 | 141.866 | 13.8532 | 13.8532 | 3464.8323 | 1183.1135 | 84.5081 | 611.7488 | 53.4353 | 20.4646 | 67.0783 | 339.9392 | 9435.3161 | 393.7366 |  |  | 24.4553 | 1.0211 | 44.1735 | 4076.5812 | 2197.2107 | 1879.3704 | 696.2569 | 21.9537 | 11.3855 | 12.2347 | 14.4871 | 12.6762 | 1.8109 | 3689.0892 | 9843.7854 | 11156.6642 | 2452.2443 | 5790.9204 | 10472.8444 | 0.098178 | 0.11012 | 0.022125 | 22.0314 | 12.5268 | 14.6211 | 20.4151 | 77.2228 | 119.3609 | 150.6745 | 117.5446 | 83.5774 | 99.17% | 98.84% | 96.75% | 99.17% | 98.67% | 98.86% | 122.2264 | 108.9733 | 542.3807 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 128.1134 | 18 | 59 | 299 | 47 | 96.88% | 0.089831 | 0.1004 | 45.5738 | 49.1794 | 139.4973 | 54.9266 | 96.88% | 3787.9045 | 98.59% | 98.96% | 84.99% |  |  | 98.56% | 1.0211
2019-12-17 | 187.1856 | 165.1891 | 165.1891 | 153.6498 | 141.3435 | 13.7312 | 13.7312 | 3471.5606 | 1185.4109 | 84.6722 | 613.1903 | 50.0401 | 19.1643 | 62.8163 | 318.3401 | 9245.5079 | 393.5734 |  |  | 24.416 | 1.0227 | 41.3668 | 4084.7509 | 2201.4774 | 1883.2735 | 697.8626 | 21.9965 | 11.5394 | 12.2818 | 14.5152 | 12.7008 | 1.8144 | 3615.3528 | 9649.8012 | 10938.3333 | 2402.939 | 5675.8569 | 10267.1647 | 0.098607 | 0.11043 | 0.022084 | 22.0074 | 12.6555 | 14.6263 | 19.5776 | 74.037 | 114.4098 | 150.5373 | 117.6231 | 84.0214 | 99.2% | 98.89% | 96.9% | 99.19% | 98.7% | 98.89% | 121.6949 | 108.6708 | 543.3855 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 127.5524 | 18 | 59 | 299 | 47 | 97.02% | 0.090145 | 0.10078 | 45.8176 | 49.2892 | 139.5462 | 52.665 | 97.02% | 3712.3311 | 98.65% | 98.98% | 84.99% |  |  | 98.62% | 1.0227
2019-12-16 | 184.7965 | 162.713 | 162.713 | 151.0548 | 138.7598 | 13.6588 | 13.6588 | 3472.6364 | 1185.7783 | 84.6984 | 611.9694 | 52.0232 | 19.9238 | 65.3058 | 330.9563 | 8740.8246 | 389.2257 |  |  | 24.5662 | 1.0168 | 43.0062 | 4084.6057 | 2202.1596 | 1882.4461 | 696.6678 | 22.0835 | 11.6582 | 12.2331 | 14.5197 | 12.7048 | 1.815 | 3437.0179 | 9175.9121 | 10400.0813 | 2284.6371 | 5396.4033 | 9762.4592 | 0.099234 | 0.11082 | 0.021945 | 22.0999 | 12.8008 | 14.6087 | 21.2909 | 80.5165 | 124.4124 | 148.7723 | 116.5696 | 84.091 | 99.13% | 98.79% | 96.61% | 99.07% | 98.51% | 98.73% | 120.9263 | 108.2869 | 546.8118 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 125.1679 | 18 | 59 | 299 | 47 | 96.74% | 0.090574 | 0.1013 | 45.9748 | 49.5095 | 138.2793 | 57.2737 | 96.74% | 3529.5773 | 98.53% | 98.83% | 85.02% |  |  | 98.5% | 1.0168
2019-12-15 | 183.5806 | 161.6709 | 161.6709 | 150.2139 | 137.92 | 13.7329 | 13.7329 | 3468.5361 | 1184.3782 | 84.5984 | 611.628 | 53.6941 | 20.5637 | 67.4032 | 341.5857 | 8957.0688 | 383.5004 |  |  | 24.9367 | 1.0024 | 44.3875 | 4080.1641 | 2199.5595 | 1880.6046 | 696.2265 | 21.9097 | 11.4571 | 12.2044 | 14.5026 | 12.6898 | 1.8128 | 3515.1387 | 9380.217 | 10630.4117 | 2336.7887 | 5518.0092 | 9979.258 | 0.098687 | 0.11066 | 0.022122 | 21.9606 | 12.5968 | 14.5876 | 21.1562 | 80.0297 | 123.6997 | 147.3118 | 114.9565 | 82.1457 | 99.12% | 98.78% | 96.58% | 99.09% | 98.55% | 98.76% | 121.5965 | 108.4448 | 542.448 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 124.2013 | 18 | 59 | 299 | 47 | 96.71% | 0.090266 | 0.10091 | 45.5712 | 49.1449 | 136.605 | 56.922 | 96.71% | 3609.4608 | 98.51% | 98.87% | 85.01% |  |  | 98.51% | 1.0024
2019-12-14 | 181.6506 | 160.212 | 160.212 | 149.0659 | 136.8647 | 13.657 | 13.657 | 3431.9916 | 1171.8996 | 83.7071 | 606.0724 | 57.661 | 22.0829 | 72.383 | 366.8222 | 9334.6211 | 375.3311 |  |  | 25.1138 | 0.99566 | 47.6668 | 4038.064 | 2176.3849 | 1861.6791 | 689.7796 | 21.4387 | 11.1461 | 11.9524 | 14.3498 | 12.5561 | 1.7937 | 3641.712 | 9705.8163 | 10995.6625 | 2421.6171 | 5713.6988 | 10323.9297 | 0.098347 | 0.11085 | 0.022458 | 21.8227 | 12.438 | 14.4852 | 21.5458 | 81.5697 | 126.1928 | 145.2766 | 112.7754 | 79.5227 | 99.09% | 98.73% | 96.45% | 99.11% | 98.57% | 98.78% | 122.0175 | 108.2512 | 534.3279 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 123.3249 | 18 | 59 | 299 | 47 | 96.59% | 0.090207 | 0.10077 | 44.5371 | 48.746 | 134.2212 | 58.0016 | 96.59% | 3738.4819 | 98.46% | 98.88% | 84.99% |  |  | 98.48% | 0.99566
2019-12-13 | 182.934 | 161.1856 | 161.1856 | 149.8307 | 137.6119 | 13.7064 | 13.7064 | 3462.9142 | 1182.4585 | 84.4613 | 612.6879 | 58.2548 | 22.3103 | 73.1283 | 370.5996 | 9387.068 | 383.6448 |  |  | 25.2254 | 0.99141 | 48.1577 | 4075.6021 | 2195.9944 | 1879.6077 | 697.1492 | 21.7484 | 11.3549 | 12.2093 | 14.4791 | 12.6692 | 1.8099 | 3660.9471 | 9746.3687 | 11038.8536 | 2434.9041 | 5741.2307 | 10365.8002 | 0.098125 | 0.1107 | 0.022418 | 21.8295 | 12.4849 | 14.5603 | 21.7509 | 82.4009 | 127.5756 | 146.2904 | 113.4613 | 80.0389 | 99.08% | 98.73% | 96.42% | 99.11% | 98.56% | 98.77% | 122.2928 | 108.3988 | 535.274 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 123.8836 | 18 | 59 | 299 | 47 | 96.57% | 0.090037 | 0.10057 | 45.3126 | 48.8747 | 135.1463 | 58.5796 | 96.57% | 3757.3301 | 98.45% | 98.88% | 84.97% |  |  | 98.47% | 0.99141
2019-12-12 | 183.7574 | 161.84 | 161.84 | 150.496 | 138.1843 | 13.7402 | 13.7402 | 3472.191 | 1185.6262 | 84.6876 | 612.5243 | 56.4757 | 21.629 | 70.895 | 359.2817 | 9434.4671 | 386.095 |  |  | 25.2047 | 0.9922 | 46.687 | 4084.7153 | 2201.8772 | 1882.8381 | 697.2119 | 21.9174 | 11.344 | 11.9827 | 14.5179 | 12.7031 | 1.8147 | 3680.0962 | 9817.6328 | 11125.344 | 2446.5906 | 5776.2717 | 10444.2487 | 0.098035 | 0.11066 | 0.022458 | 21.9309 | 12.4491 | 14.2916 | 21.0588 | 79.6754 | 123.1767 | 146.9337 | 113.9009 | 80.1751 | 99.12% | 98.77% | 96.56% | 99.14% | 98.62% | 98.82% | 122.4056 | 108.4424 | 534.3302 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 124.4948 | 18 | 59 | 299 | 47 | 96.69% | 0.089982 | 0.1005 | 45.2441 | 48.6716 | 135.8314 | 56.6667 | 96.69% | 3778.6197 | 98.51% | 98.92% | 85% |  |  | 98.52% | 0.9922
2019-12-11 | 183.0548 | 161.3678 | 161.3678 | 150.0823 | 137.8727 | 13.6973 | 13.6973 | 3456.4446 | 1180.2494 | 84.3035 | 610.5679 | 57.0691 | 21.8562 | 71.6399 | 363.0565 | 9456.6667 | 382.2001 |  |  | 25.1025 | 0.99609 | 47.1775 | 4067.0125 | 2191.8917 | 1875.1208 | 694.8714 | 21.687 | 11.2855 | 12.1529 | 14.452 | 12.6455 | 1.8065 | 3693.0333 | 9844.0235 | 11153.0981 | 2455.5797 | 5794.5723 | 10471.3347 | 0.098366 | 0.11106 | 0.022567 | 21.8397 | 12.4577 | 14.5663 | 21.1887 | 80.2074 | 124.0701 | 146.3454 | 113.4131 | 79.7388 | 99.11% | 98.76% | 96.53% | 99.14% | 98.62% | 98.82% | 121.993 | 108.0466 | 531.7598 |  |  |  | 32 | 28 | 4 | 2496 | 1344 | 96 | 3936 | 124.2357 | 18 | 59 | 299 | 47 | 96.67% | 0.090301 | 0.10085 | 45.1254 | 48.8637 | 135.1237 | 57.0354 | 96.67% | 3791.2297 | 98.49% | 98.92% | 84.99% |  |  | 98.51% | 0.99609
2019-12-10 | 182.0168 | 160.0538 | 160.0538 | 148.581 | 136.5472 | 13.6934 | 13.6934 | 3469.8502 | 1181.2256 | 94.9199 | 612.8017 | 51.2446 | 17.556 | 56.9384 | 293.7073 | 9120.0328 | 383.8568 |  |  | 25.0928 | 0.99646 | 38.5171 | 4082.6518 | 2193.7047 | 1888.9472 | 707.7216 | 21.963 | 11.4728 | 12.1819 | 14.464 | 12.656 | 2.034 | 3568.3247 | 9429.0184 | 10844.0324 | 2375.7495 | 5578.432 | 10103.5716 | 0.099022 | 0.11159 | 0.025392 | 21.9542 | 12.4697 | 14.3516 | 17.6128 | 66.2971 | 117.1677 | 145.5509 | 113.0165 | 79.8214 | 99.26% | 98.98% | 97.09% | 99.26% | 98.81% | 98.84% | 121.1854 | 107.5398 | 472.5979 |  |  |  | 32 | 28 | 4.5 | 2496 | 1344 | 108 | 3948 | 122.6102 | 18.5 | 60 | 309.5 | 54 | 96.91% | 0.091262 | 0.10129 | 45.6176 | 48.7755 | 134.6888 | 53.0237 | 96.91% | 3677.4238 | 98.61% | 99.05% | 84.99% |  |  | 98.61% | 0.99646
2019-12-09 | 179.6905 | 157.7233 | 157.7233 | 146.2078 | 134.0012 | 13.6692 | 13.6692 | 3472.6367 | 1178.5918 | 105.2314 | 613.1951 | 52.1674 | 16.2489 | 52.1674 | 273.6653 | 8651.5348 | 378.2908 |  |  | 25.2335 | 0.99111 | 36.2399 | 4085.8318 | 2188.8134 | 1897.0184 | 718.4265 | 21.9672 | 11.5155 | 12.176 | 14.4317 | 12.6278 | 2.255 | 3392.4979 | 8872.371 | 10348.0088 | 2262.885 | 5280.5829 | 9572.3814 | 0.099464 | 0.11159 | 0.027957 | 21.8965 | 12.3816 | 14.1657 | 16.9847 | 63.6813 | 127.0628 | 143.8045 | 112.1542 | 79.9417 | 99.28% | 99.01% | 97.14% | 99.25% | 98.79% | 98.67% | 120.6464 | 107.5349 | 429.2352 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 120.2611 | 19 | 61 | 320 | 61 | 96.71% | 0.091904 | 0.10141 | 45.6587 | 48.4438 | 133.4009 | 56.3179 | 96.71% | 3508.5732 | 98.51% | 99.01% | 84.99% |  |  | 98.53% | 0.99111
2019-12-08 | 179.2135 | 157.4473 | 157.4473 | 146.1601 | 133.8002 | 13.7273 | 13.7273 | 3466.7243 | 1176.5852 | 105.0523 | 611.2318 | 54.7163 | 17.0428 | 54.7163 | 287.0362 | 8943.5748 | 376.6701 |  |  | 25.3759 | 0.98573 | 38.0105 | 4077.9561 | 2185.0868 | 1892.8693 | 716.2841 | 21.7662 | 11.2871 | 12.0736 | 14.4072 | 12.6063 | 2.2511 | 3491.3605 | 9136.4737 | 10657.4242 | 2328.6295 | 5435.8573 | 9857.9465 | 0.09928 | 0.11178 | 0.028304 | 21.7617 | 12.18 | 14.1118 | 17.1883 | 64.4227 | 128.4888 | 143.0451 | 111.1707 | 78.3983 | 99.27% | 98.99% | 97.09% | 99.26% | 98.81% | 98.7% | 120.87 | 107.3564 | 423.9671 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 120.0989 | 19 | 61 | 320 | 61 | 96.64% | 0.091923 | 0.10137 | 45.1269 | 48.0535 | 132.3744 | 56.9795 | 96.64% | 3611.3649 | 98.48% | 99.03% | 85.01% |  |  | 98.51% | 0.98573
2019-12-07 | 180.1628 | 158.3228 | 158.3228 | 146.902 | 134.7554 | 13.7797 | 13.7797 | 3465.6079 | 1176.2063 | 105.0184 | 612.543 | 56.6764 | 17.6533 | 56.6764 | 297.3186 | 9241.1894 | 380.2619 |  |  | 25.3136 | 0.98808 | 39.3722 | 4078.1509 | 2184.3832 | 1893.7677 | 717.5614 | 21.84 | 11.4208 | 12.1748 | 14.4025 | 12.6022 | 2.2504 | 3590.6665 | 9383.483 | 10941.2752 | 2395.487 | 5587.2475 | 10122.5332 | 0.099118 | 0.112 | 0.028535 | 21.8295 | 12.3089 | 14.1885 | 17.3428 | 65.0562 | 129.88 | 143.574 | 111.1799 | 77.9229 | 99.26% | 98.99% | 97.06% | 99.28% | 98.84% | 98.72% | 121.0674 | 107.1444 | 420.5297 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 120.849 | 19 | 61 | 320 | 61 | 96.62% | 0.091947 | 0.10135 | 45.4356 | 48.3268 | 132.5794 | 57.5249 | 96.62% | 3712.9041 | 98.47% | 99.05% | 84.98% |  |  | 98.49% | 0.98808
2019-12-06 | 181.1831 | 159.1154 | 159.1154 | 147.6363 | 135.3652 | 13.8542 | 13.8542 | 3474.0213 | 1179.0618 | 105.2734 | 613.0367 | 62.5262 | 19.4754 | 62.5262 | 328.0062 | 9562.0879 | 383.3335 |  |  | 25.1946 | 0.99258 | 43.436 | 4087.058 | 2189.6861 | 1897.3718 | 718.31 | 22.0677 | 11.4791 | 12.3855 | 14.4375 | 12.6328 | 2.2559 | 3610.9013 | 9435.341 | 10999.2928 | 2409.3525 | 5618.4776 | 10177.3714 | 0.099278 | 0.11221 | 0.02856 | 21.9879 | 12.3409 | 14.4138 | 19.1559 | 71.8716 | 143.5108 | 144.3457 | 111.7419 | 78.3997 | 99.19% | 98.89% | 96.78% | 99.2% | 98.72% | 98.59% | 120.8722 | 106.9376 | 420.1622 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 121.5447 | 19 | 61 | 320 | 61 | 96.29% | 0.092103 | 0.10153 | 45.9323 | 48.7426 | 133.2575 | 63.5471 | 96.29% | 3733.9046 | 98.33% | 98.95% | 85% |  |  | 98.34% | 0.99258
2019-12-05
2019-12-04 | 183.3695 | 161.5954 | 161.5954 | 150.2217 | 137.6389 | 14.0112 | 14.0112 | 3470.2907 | 1177.7956 | 105.1603 | 612.6152 | 53.7303 | 16.7357 | 53.7303 | 281.8637 | 9305.0327 | 390.8548 |  |  | 25.1206 | 0.9954 | 37.3256 | 4082.9059 | 2187.3347 | 1895.5711 | 717.7755 | 21.7741 | 11.3737 | 12.1654 | 14.422 | 12.6192 | 2.2534 | 3569.1827 | 9337.6777 | 10892.181 | 2380.5213 | 5556.409 | 10075.0651 | 0.097889 | 0.10982 | 0.027708 | 21.7278 | 12.2439 | 14.173 | 16.6897 | 62.5605 | 124.7933 | 146.6523 | 114.3839 | 80.9531 | 99.3% | 99.03% | 97.2% | 99.3% | 98.87% | 98.76% | 122.5884 | 109.2742 | 433.0859 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 123.906 | 19 | 61 | 320 | 61 | 96.77% | 0.090476 | 0.09981 | 45.3132 | 48.1447 | 135.7217 | 55.3308 | 96.77% | 3691.5664 | 98.54% | 99.08% | 85% |  |  | 98.55% | 0.9954
2019-12-03 | 182.9307 | 161.0174 | 161.0174 | 149.4681 | 137.2438 | 13.8141 | 13.8141 | 3467.383 | 1176.8088 | 105.0722 | 612.4612 | 54.2779 | 16.9062 | 54.2779 | 284.7363 | 9177.7084 | 391.5937 |  |  | 25.2925 | 0.98887 | 37.706 | 4079.8442 | 2185.502 | 1894.3422 | 717.5334 | 21.9133 | 11.5494 | 12.2001 | 14.4099 | 12.6087 | 2.2515 | 3551.7723 | 9287.9264 | 10832.4898 | 2369.152 | 5528.252 | 10020.6381 | 0.097334 | 0.10932 | 0.027534 | 21.8903 | 12.4435 | 14.2198 | 16.8156 | 63.051 | 125.814 | 146.3987 | 114.0588 | 80.8623 | 99.29% | 99.02% | 97.16% | 99.29% | 98.86% | 98.74% | 123.2868 | 109.7741 | 435.8181 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 123.5417 | 19 | 61 | 320 | 61 | 96.73% | 0.09 | 0.099285 | 45.6628 | 48.5536 | 135.5013 | 55.7595 | 96.73% | 3673.1946 | 98.52% | 99.07% | 84.99% |  |  | 98.54% | 0.98887
2019-12-02 | 181.0887 | 159.2309 | 159.2309 | 147.6327 | 135.4819 | 13.7919 | 13.7919 | 3463.0273 | 1175.3305 | 104.9402 | 610.7747 | 51.4685 | 16.0312 | 51.4685 | 269.9984 | 8692.0227 | 387.6662 |  |  | 25.2114 | 0.99194 | 35.7543 | 4073.8019 | 2182.7566 | 1891.0454 | 715.7149 | 21.8578 | 11.5982 | 12.1849 | 14.3918 | 12.5928 | 2.2487 | 3381.6102 | 8850.2919 | 10324.5145 | 2255.2936 | 5265.238 | 9549.5774 | 0.098338 | 0.10999 | 0.027414 | 21.8862 | 12.5329 | 14.2584 | 16.7811 | 62.8898 | 125.4176 | 145.1716 | 113.571 | 81.3675 | 99.29% | 99.02% | 97.17% | 99.26% | 98.81% | 98.69% | 122.0285 | 109.1036 | 437.734 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 121.7453 | 19 | 61 | 320 | 61 | 96.74% | 0.090718 | 0.10014 | 45.641 | 48.6775 | 134.747 | 55.6256 | 96.74% | 3497.8894 | 98.53% | 99.02% | 85.01% |  |  | 98.54% | 0.99194
2019-12-01 | 181.4628 | 159.873 | 159.873 | 148.5371 | 136.3152 | 13.7347 | 13.7347 | 3448.3637 | 1170.3538 | 104.4959 | 608.2582 | 52.7493 | 16.4301 | 52.7493 | 276.7178 | 8941.3185 | 384.8356 |  |  | 25.0779 | 0.99702 | 36.6441 | 4056.6219 | 2173.5141 | 1883.1078 | 712.7541 | 21.5898 | 11.3359 | 11.9925 | 14.3309 | 12.5395 | 2.2392 | 3465.7579 | 9069.9734 | 10580.6129 | 2311.4398 | 5396.1204 | 9786.5371 | 0.098229 | 0.10991 | 0.027514 | 21.755 | 12.3267 | 14.1206 | 16.7955 | 62.9461 | 125.5353 | 145.4581 | 113.7535 | 81.1423 | 99.29% | 99.02% | 97.17% | 99.27% | 98.83% | 98.72% | 122.1634 | 109.1842 | 436.1446 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 122.6051 | 19 | 61 | 320 | 61 | 96.74% | 0.090651 | 0.10005 | 44.9181 | 48.2023 | 134.8332 | 55.6748 | 96.74% | 3584.8798 | 98.53% | 99.04% | 85.01% |  |  | 98.54% | 0.99702
2019-11-30 | 191.4824 | 169.1122 | 169.1122 | 157.4405 | 145.116 | 13.814 | 13.814 | 3463.8422 | 1157.341 | 104.7138 | 612.3592 | 50.7315 | 18.7486 | 59.5544 | 313.2118 | 9060.1204 | 400.788 |  |  | 23.9139 | 1.0426 | 41.2844 | 4076.2015 | 2201.7874 | 1874.4141 | 717.0731 | 22.3702 | 11.6717 | 12.2804 | 14.5173 | 12.4001 | 2.2439 | 3519.2432 | 9103.1089 | 10606.1868 | 2335.6894 | 5452.5139 | 9816.3939 | 0.097715 | 0.10554 | 0.026009 | 22.4796 | 12.724 | 14.3224 | 20.0919 | 72.7299 | 148.4457 | 154.8986 | 122.4976 | 89.9484 | 99.2% | 98.91% | 96.81% | 99.14% | 98.67% | 98.49% | 122.8058 | 113.6997 | 461.3735 |  |  |  | 32.09 | 27.41 | 4.96 | 2503.02 | 1315.68 | 119.04 | 3937.74 | 131.2041 | 17 | 54 | 284 | 46 | 96.88% | 0.088747 | 0.098162 | 46.3223 | 49.526 | 144.2925 | 55.9585 | 96.88% | 3603.2303 | 98.59% | 98.88% | 84.98% |  |  | 98.54% | 1.0426
2019-11-30 | 183.6293 | 161.7883 | 161.7883 | 150.2198 | 138.1187 | 13.7708 | 13.7708 | 3456.343 | 1173.0619 | 104.7377 | 610.037 | 53.4073 | 16.6351 | 53.4073 | 280.1696 | 8914.3399 | 390.0772 |  |  | 24.5716 | 1.0166 | 37.1013 | 4066.38 | 2178.5435 | 1887.8366 | 714.7747 | 21.8409 | 11.5685 | 12.1595 | 14.364 | 12.5685 | 2.2444 | 3451.3787 | 9028.0042 | 10529.9258 | 2302.1026 | 5372.6453 | 9740.4736 | 0.098989 | 0.11049 | 0.027457 | 21.9278 | 12.5307 | 14.2557 | 17.4489 | 65.4151 | 130.5061 | 147.5107 | 115.6371 | 83.0969 | 99.28% | 99.01% | 97.12% | 99.24% | 98.78% | 98.66% | 121.2256 | 108.6076 | 437.0548 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 124.2553 | 19 | 61 | 320 | 61 | 96.69% | 0.091224 | 0.10072 | 45.5689 | 48.7143 | 136.8905 | 57.853 | 96.69% | 3569.6314 | 98.5% | 99% | 85% |  |  | 98.49% | 1.0166
2019-11-29 | 183.573 | 161.5943 | 161.5943 | 149.7952 | 137.2252 | 13.6209 | 13.6209 | 3449.7085 | 1170.8102 | 104.5366 | 608.656 | 45.2578 | 14.0967 | 45.2578 | 237.418 | 8202.3016 | 390.9585 |  |  | 23.9582 | 1.0408 | 31.4399 | 4058.3645 | 2174.3617 | 1884.0028 | 713.1926 | 21.9787 | 11.7991 | 12.2259 | 14.3365 | 12.5444 | 2.2401 | 3165.5575 | 8287.9866 | 9670.6711 | 2110.8867 | 4929.6269 | 8943.8012 | 0.1005 | 0.11098 | 0.026999 | 22.1322 | 12.8205 | 14.3818 | 16.4791 | 61.739 | 123.0824 | 148.4788 | 117.652 | 86.3574 | 99.33% | 99.08% | 97.35% | 99.22% | 98.75% | 98.62% | 119.4045 | 108.1303 | 444.4632 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 123.93 | 19 | 61 | 320 | 61 | 96.94% | 0.092092 | 0.10183 | 46.0037 | 49.3345 | 138.6697 | 54.6131 | 96.94% | 3274.6081 | 98.62% | 98.97% | 85% |  |  | 98.57% | 1.0408
2019-11-28 | 182.4404 | 160.7914 | 160.7914 | 149.4058 | 137.0674 | 13.7281 | 13.7281 | 3455.33 | 1172.718 | 104.707 | 609.465 | 51.652 | 16.0883 | 51.652 | 270.9613 | 9040.4523 | 389.3401 |  |  | 24.6246 | 1.0145 | 35.8819 | 4064.7949 | 2177.9049 | 1886.89 | 714.172 | 21.649 | 11.3855 | 12.0718 | 14.3598 | 12.5648 | 2.2437 | 3486.8277 | 9127.6157 | 10649.2018 | 2325.2936 | 5429.5524 | 9849.3399 | 0.099548 | 0.11135 | 0.027889 | 21.749 | 12.3436 | 14.1717 | 16.6682 | 62.4565 | 124.5314 | 146.3417 | 114.481 | 81.6166 | 99.31% | 99.05% | 97.25% | 99.28% | 98.85% | 98.74% | 120.5453 | 107.7723 | 430.2695 |  |  |  | 32 | 28 | 5 | 2496 | 1344 | 120 | 3960 | 123.3715 | 19 | 61 | 320 | 61 | 96.83% | 0.091858 | 0.10138 | 45.1064 | 48.2643 | 135.6417 | 55.2453 | 96.83% | 3606.8616 | 98.57% | 99.06% | 85.01% |  |  | 98.55% | 1.0145
Note on CL1: Dawn Vickers: not used for A-E calculations
Note on CM1: Dawn Vickers: not used for A-E calculations
Note on CR1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Additional Calculation

## Abbreviation list
Abbreviation list
Conc: Concentrate
AFBC: Average feed-brine concentration (log-mean feed brine average)
NPC: Normalized permeate concentration
Net Drv Psi: Net driving pressure
dp, DP: differential pressure
Press: Pressure
TCF: Temperature correction factor
Stage 1-2 Feed Flow: flow rate from RO stage 1 to stage 2 (stage 1 brine flow)
NdeltaP: Normalized differential pressure
Calc: Calculated
Est: Estimated
IBP: Interstage booster pump (between stage 1 and 2)
EC (Cond): electrical conductivity
KVA: "Kilovolt-amperes"
Notes:
the system pressures (psi) and flow rates (gpm) are listed in columns B-L. The grey data are directly from the sensors and green are calculated values.

## Installation date
D01 | Installation date
Dupont/Filmtec BW30XFRLE | 2020-10-01